| DOCKET NO. 225D - Kleen Energy Systems, LLC Certificate of Environmental Compatibility and Public Need for the construction, maintenance and operation of a Electric Generating Facility and Switchyard on River Road, Middletown, Connecticut. Reopening of this docket pursuant to Connecticut General Statutes § 4-181a(b) limited to Council consideration of changed conditions and of the attachment of conditions to the certificate consistent with the findings and recommendations in the Executive Report issued by the Thomas Commission. | } } } | Connecticut Siting Council February 8, 2011 |
| --- | --- | --- |

# Opinion

# On November 21, 2002, the Connecticut Siting Council (Council) granted a Certificate of Environmental Compatibility and Public Need (Certificate) to Kleen Energy Systems, LLC (Kleen) for the construction, maintenance and operation of a 620-megawatt natural-gas fired combined cycle electric generating facility off of River Road in Middletown.  On February 7, 2010, during construction of the facility, there was an explosion caused by the release and combustion of natural gas being used to clean natural gas piping at the facility, a procedure otherwise known as a “gas blow”.  The project was estimated at 97 percent complete at the time of the explosion.

As a result of the explosion, Governor M. Jodi Rell established a commission, the Kleen Energy Plan Investigation Review Panel, chaired by Judge Alan Nevas (the “Nevas Commission”), to identify the cause and origin of the explosion and to provide information necessary for a second Commission (Thomas Commission) to provide recommendations for any necessary legislative and regulatory changes that could prevent such an event from occurring in the future.  On September 21, 2010, the Thomas Commission issued its Executive Report, which included recommendations for regulatory changes that could be accomplished by executive order, state legislation and/or the adoption of regulations.

On October 7, 2010, the Council, on its own motion, reopened the Docket 225 record for the limited purpose of consideration of changed conditions and of the attachment of conditions to the Certificate consistent with the recommendations of the Thomas Commission.  The specific findings of the Thomas Commission are as follows:

a.	“The use of flammable gases to conduct ‘gas blows’ should be banned in Connecticut; at least until such time as there are accepted national standards published and in place”;

b.	“Requirement of special inspectors, development of safety plans and payment of cost by power plant applicant”;

c.	Assembly of a “Coordinating Council” for future power plant applications;

d.	Attachment of conditions to certificates issued by the Siting Council that include a ban on flammable gas blows and compliance with certain code recommendations;

e.	Review of existing power plants that received certificates from the Council to determine if such certificates warrant re-opening for consideration of the Nevas and Thomas Commission recommendations;

f. Adoption of the following codes and regulations by the Department of Public Safety:

- Amend the Flammable & Combustible Liquids Code, Connecticut General Statute §29-320 to adopt the 2010 Edition of National Fire Protection Association (NFPA 37), “Standard for the Installation and Use of Stationary Combustion Engines and Gas Turbines”;

- Amend the Gas Equipment and Piping Code, C.G.S. §29-329 to adopt the 2009 Edition of NFPA 54, “National Fuel Gas Code” including Temporary Interim Amendment 09-3 (August 25, 2010) and by Connecticut amendment remove the exception regarding fuel gas piping at electric utility power plants and to adopt American Society of Mechanical Engineers (ASME) Standard B31, “Code for Pressure Piping” including mandatory compliance with Appendices IV and V of ASME B31.1 for newly constructed electric utility power plants;

- Amend the Connecticut Fire Prevention Code adopted pursuant to C.G.S. §29-291a to add new sections in the Hazardous Materials Chapter regarding “Gas Piping Cleaning Operations”;

- Amend the Fire Prevention Code adopted pursuant to C.G.S. §29-291a to delete and revise sections 29-291a-2(a) and (b) regarding “Relationship to State Fire Safety and Building Codes” and to adopt the requirements of the 2010 Edition of NFPA 850 “Fire Protection for Electric Generating Plants and High Voltage Current Converter Stations”; and

g. Adoption of legislation to provide for payment into a code training fund by any power

plant applicant who is required to obtain Siting Council approval.

In its review of the Thomas Commission findings and recommendations, the Council must first consider the limits of its jurisdiction.  Jurisdiction over electric generating facilities is conferred upon the Council pursuant to the Public Utility Environmental Standards Act (PUESA).  PUESA does not charge the Council with any authority to impose or enforce occupational safety and hazard standards and regulations.  The Council recognizes that the tragic accident that occurred at the Kleen facility is an isolated incident with unique circumstances and that the Council’s decision in this reopened docket should not be considered precedent for any possible future Council actions regarding any gas-related incidents at other electric generating facilities under the Council’s jurisdiction.   In the event of a future incident, the Council will consider the adoption of any specific findings and recommendations of any Commissions that may be appointed by the Governor in response to such an incident.

Notwithstanding its statutory jurisdictional limitations, the Council has considered changed conditions in this docket.  Upon review of the Thomas Commission findings and recommendations for further examination of potential changes to the regulatory process concerning gas blows, the Council finds changed conditions in industry practices specifically pertaining to the gas pipe cleaning process used for the construction of the Kleen facility.  The Thomas Commission urges the Council to attach conditions to Kleen’s Certificate consistent with the Commission’s findings and recommendations relative to gas blow procedures and compliance with code recommendations.

The Council is cognizant that these are only recommendations: they will require further action by other state agencies or by enabling legislation to become mandatory.  Notwithstanding this issue, the Council has examined each of these recommendations based on the changed conditions concerning Kleen’s Certificate, hereby adopts the Thomas Commission recommendations, and will attach said recommendation to Kleen’s Certificate.  The Council is aware that an item in the recommended code requirements includes the imposition of Temporary Interim Amendment 09-3 (August 25, 2010).  A portion of this standard, Section 8.3.2.1(5) states that the piping shall be purged by the gas supplier in accordance with written procedures.  Although the Council finds that this requirement could be problematic given that the gas supplier did not construct or does not own the gas distribution system at the facility, the Council also notes that the imposition of this item would have no effect on the Kleen facility because the gas lines have already been cleaned and the gas supply system is currently operational.

One area of concern to the Council not specifically addressed by the Thomas Commission is the apparent lack of a local notification system during facility emergencies or for routine facility construction and maintenance activities that could cause neighborhood alarm.  The Council understands that such a system can be established using different forms of contact and that, given the options, no system can be 100 percent assured of reaching every intended recipient.  Still, such a system is valuable to disseminate information and allay neighborhood concerns.  The Council will require Kleen to create a local response system that will include notification to local emergency responders, City of Middletown and Town of Portland officials, representatives of the NRG facility on River Road, and local residents who wish to participate, specifically on Bow Lane (east of Cedar Lane) and River Road (east of Silvermine Road) in Middletown, and Wellwyn Drive, Lyman Road, and Payne Road in Portland.

In addition, to ensure adequate provisions are in place to respond to emergencies when the facility is operational the Council will direct Kleen to incorporate an Emergency Response Plan (ERP) into the Operations Plan that is required by the Council’s November 21, 2002 Decision and Order.  The ERP shall be reviewed and approved by the Council prior to facility operation.  The Council shall consult with and solicit comment regarding the ERP from appropriate state agencies and local emergency responders as part of the Council’s ERP review process.