##### Instructions

This application is provided to assist a Public Water System (PWS) seeking approval from the Department of Public Health (DPH) for a water treatment plant (WTP) which will achieve 4 log inactivation of viruses using chlorine as a disinfectant. This application excludes groundwater sources which have been determined to be under the direct influence of surface water or surface WTPs.  In order to achieve 4 log inactivation of viruses a system has to maintain a CT value as established in US Environmental Protection Agency Table which is based on water temperature. The State of Connecticut is requiring that a CT value of at least 6.0 mg-min/L be achieved and maintained corresponding to a groundwater temperature of 50o F (10o C) and pH of 6.0-9.0. CT is equal to a measured residual disinfection concentration level (mg/L) at a compliance sampling location multiplied by a determined contact time (min) which is calculated based on specific flows as well as the configuration of the pipes, tanks or other physical components at a PWS’s water treatment plant (WTP) up to the sampling location, tap or sampling line tapped into a WTP’s discharge/effluent pipe prior to a first consumer.

CT [mg-min/L] = contact time (T) [min] x residual disinfection concentration (C) [mg/L]

Since CT is a fixed value of 6.0 mg-min/L the main goal of this application is to identify the operational conditions and components used to determine contact time (T), and then determine the minimum residual disinfectant concentration (CMIN) that a specific WTP must at least achieve and maintain for compliance. The residual disinfection concentration for system using chlorine as a disinfectant is commonly referred to as free chlorine residual.

This application form must be submitted to the DPH along with a General Application form. Separate forms need to be completed for each WTP. Additional supporting information as identified in this application must be provided in order for the DPH to start its review. If a new or replacement chlorination system is being installed at an existing or proposed PWS, and/or with a project which has other new components (i.e. wells, tanks, pipes, pumps, other treatment, etc.) additional applications need to be submitted.

A document entitled “TECHNICAL GUIDELINES FOR DETERMINING DISINFECTION “CT” WHEN USING CHLORINE FOR DISINFECTION OF GROUNDWATER SOURCES OF SUPPLY” (CT Guideline) should be used as a reference in completing this application form; and it identifies applicable Regulations of Connecticut State Agencies (RCSA) or Connecticut General Statutes (CGS). Applications, forms and CT Guideline are available on the DPH’s website http://www.ct.gov/dph/publicdrinkingwater.

Check off and complete all items that apply. If the space provided in this application is not adequate, please provide the additional information in an attachment with reference to the specific application section and question. Footnotes are provided to assist a PWS in completing specific components of the application. Two figures are also provided at the end of the application to help a PWS understand the basic terms in this application.

| Section A. General Information |
| --- |
| PWS Name: | PWSID #: CT | Town: |
| Contact information of the primary person who can answer technical questions regarding this project: |
| Name: | Title: |
| Company: |
| Address: |
| Address: |
| Email: |
| Phone: | Business: | Cell: |

| Section B. Plans |
| --- |
| A plan sheet or drawing/schematic of an existing and/or proposed WTP must be submitted showing: pipes; point of chlorine injection; tank(s) showing inlet, outlet and baffling configuration; booster pump(s); compliance sample location; sample line; sample tap and/or continuous chlorine analyzer used for taking compliance chlorine residual measurements; and, location of first consumer (i.e. service line, tee/split in plumbing, WTP, etc.). Pipe diameter(s) and corresponding lengths of pipe(s) used to determine contact time also needs to be identified. |
| Section C. Identification of WTP and Well(s) Treated at WTP |
| Name of existing or proposed WTP: Does the existing WTP currently use chlorination?: Yes No If Yes, is a backup chemical metering pump or inventory of spare parts provided or readily available in order to avoid or allow for a minimal interruption (required for 4 log disinfection system)? Yes No If No or if a new WTP is being proposed to provide chlorination, additionally submit “Chemical Feed System Project Application” and “Water Treatment Plant Classification Form” to the DPH. Identify Wells (numbers and/or names) supplying WTP: |
| Section D. Water pH Range |
| pH range of untreated well or blended well raw water which supplies WTP: Does PWS adjust pH at this WTP? Yes No If yes, pH range of the treated water: Is pH in the range of 6.0 – 9.0? Yes Noa Footnote a: If the pH is above 9.0 the DPH must be contacted to determine an applicable CT value for the WTP in order to achieve 4 log inactivation of viruses. The CT required will be substantially higher. |
| Section E. Maximum Flowb (Q) |
| Maximum flow rate of well(s) (QW) [gallons per minute (gpm)]: Maximum flow rate of booster pump(s) (QB) (gpm)c: Method used for determining maximum flow rate: Meter readings; Other (describe): Footnote b: If more than one well is used during any normal operation, the total gpm flow of the wells used must be identified and used in calculations as applicable. A PWS needs to assess what system components (pipes, tanks or other) are to be used to achieve CT in order to determine applicable maximum flow rate(s). Figures 1 and 2 are provided in this document to assist a PWS in making the determination of flow rates, and will also assist in the calculations within the following application sections. Figure 1 illustrates a WTP with only a well(s) which supplies water directly to a distribution system with or without pressure storage. Where a tank and corresponding discharge pipe supply the distribution system with gravity flow the maximum flow (gpm) can be estimated as follows: historic average day demand [(ADD) gallons/day] divided by 3 to determine a peak hour demand, and then divided by the conversion of 60 min/hr to determine the maximum flow (gpm). Footnote c: If more than one booster pump is used during any normal operation, the individual booster pump capacities and total gpm for the booster pumps used normal operation must be identified and used in calculations as applicable. Figure 2 illustrates a WTP with well(s), atmospheric storage tank(s) and with or without booster pump(s) to supply water directly to a distribution system. |
| Section F. Contact Time (T) Information/Calculations |
| 1. Pipe(s)d Includes all contact times from the point of chlorine injection up to compliance sample location before a first consumer. | TP = contact time (min.) in a specific pipe segment TP = [(0.785 x D2) x L x 7.48]/Q Q = QW or QB (from Section E) |
| D = diameter of the pipe (feet – NOT inches) | L = length of pipe (feet) | Q = maximum flow (gpm) | TP = (min) |
| Total contact time in pipe segment(s) = TTP |  |
| Footnote d: A PWS may install additional pipe and/or a larger diameter pipe in series with existing pipes to increase contact time. |

| Section F. Contact Time (T) Information/Calculations (continued) |
| --- |
| 2. Tank(s) Includes all contact times for pressure, hydropneumatic and/or atmospheric storage tanks, as well as filter vessels. | TT = contact time (min) in a specific tank TT = V/Q x BF Q = QW or QB (from Section E) |
| V = minimum volume of water in tank (gallons)e and f | Q = maximum flow (gpm)f | Baffle Factor (BF)f | TT = (min) |
|  | Total contact time in tank(s) = TTT |  |
| Footnote e: Volume of water in tank at lowest normal operating level - NOT the total/gross volume. Calculations supporting how the volume was determined should be provided. Note, since many tanks are horizontal cylinders and the calculation for determining the volume of a partially filled tank is very complicated, websites on the internet (search “volume of partially filled horizontal cylinder”) can be found to easily determine the volume by just knowing diameter or radius of tank, length of tank and normal lowest height of water in tank. For an Atmospheric Tank: Volume of water in tank at which level well(s) come on to re-fill tank (i.e. float switch, level probe, pressure sensor, etc.) For a Pressure or Hydropneumatic Tank: Volume of water in tank at which level well(s) or booster pump come on to re-fill tank (i.e. pressure switch, level probe, etc.) No contact time (T) is given for a tank with a common inlet/outlet pipe. Footnote f: Refer to DPH’s CT Guideline to determine appropriate volume, flow and BF. |
| 3. Total Contact Time to Sample Location = TTS (min) TTS = TTP (from Section F.1. Pipe(s)) + TTT (from Section F.2. Tank(s)) TTS = |
| Section G. Determining Minimum Compliance Residual Disinfectant Concentration (Free Chlorine Residual) Necessary to Achieve CT |
| CT (mg-min/L) = Residual Disinfectant Concentration [C (mg/L)] x Contact Time [T (min)] or C = CT/T CT = at least 6.0 mg-min/L Minimum Residual Disinfectant Concentration (mg/L) = CMIN CMIN = 6.0 mg-min/L /(divided by) TTS (min) (from Section F.3) To achieve 4 log inactivation of viruses a PWS must maintain a minimum CT value of at least 6.0 mg-min/L, which corresponds to a minimum residual disinfectant concentration of no less than 0.20 mg/L after 30 minutes of contact time or equivalent at the compliance sampling location. A CT value of 6.0 mg-min/L is based on a water temperature of no less than 50oF (10oC) and pH range of 6.0 - 9.0. Use of a lower CT will not be acceptable. |
| CT (mg-min/L) | TTS [from Section F.3 (min)] | CMIN (mg/L)g | CTARGET (mg/L)h |
| 6.0 |  |  |  |
| Footnote g: A PWS must use a CMIN of no less than 0.20 mg/L to achieve 4 log inactivation. The calculated CMIN needs to be rounded up to the nearest 0.05 mg/L increment. The CMIN identified will be the value which will be used to determine compliance at a system’s approved sampling location for treatment providing 4 log inactivation. Footnote h: A free chlorine residual of greater than the calculated CMIN should be maintained by a system since the residual may fluctuate based on the operation of the water treatment feed system components and water quality, and to avoid non-compliance. A system may also want to maintain a higher residual at the WTP in order to maintain a detectable chlorine level within its distribution/plumbing system. CTARGET is the level a PWS plans to maintain as a target level and should be at least 0.2 mg/L higher than the calculated CMIN (asked only for informational purpose). |
| Is the calculated CMIN equal or greater than 0.20 mg/L? Yes No If no, a CMIN of at least 0.20 mg/L must be maintained and will be used for the DPH for compliance. If calculated CMIN is elevated such that it may result in taste and odor concerns (i.e. approaching 2.0 mg/L) TTS should be increased to lower CMIN. Please refer to DPH’s CT Guideline. |

| Section H. Identification of Compliance Sampling Location |
| --- |
| A PWS must provide and identify a compliance sampling location where the residual disinfectant concentration CMIN is proposed to be monitored. A PWS will be required to maintain a residual disinfectant concentration (i.e. free chlorine residual) at this sampling location equal or greater than the identified minimum residual chlorine concentration per Section G to achieve the required CT value. A sample line to a sample tap or continuous chlorine analyzer with a sample tap must be provided off of the water pipe or main carrying the chlorinated water after the point at which CT is achieved. The use of sample lines to achieve an equivalent CT is not an option (see DPH CT Guideline). 1. What will be the WTP’s compliance sampling location for monitoring residual chlorine concentration? Sample tap Continuous chlorine analyzeri Footnote i: A PWS serving greater than 3,300 people must continuously monitor the residual disinfectant concentration of the treated water (use continuous analyzer) at a location approved by the DPH. A PWS serving 3,300 or fewer people must conduct a daily test for residual disinfectant concentration or can use a continuous analyzer but will be subject to the monitoring and reporting requirements of system serving greater than 3,300 people. Additionally, a sample tap needs to be installed right at the analyzer to allow for calibration of the analyzer and to allow for grab sampling every 4 hours in the event there is problem with the analyzer. |
| Section I. Compliance Testing for Residual Chlorine Concentration (Free Chlorine Residual) and Associated Components |
| Are tests for residual chlorine to be conducted by a State Certified Laboratory?: Yes No If yes, CT approved Lab: PH - The DPH may grant an exemption from the use of a laboratory when the analysis for the parameter is conducted by a DPH certified treatment operator using a test kit or continuous chlorine analyzer conforming to a test methodology approved by the DPHj. A list of methodologies approved by the DPH can be obtained upon request. Is a test kit or analyzer to be used for compliance residual chlorine concentration monitoring?: Yes No Footnote j: An analytical methods specified in 40 CFR 141.74(a)(2), as amended from time to time, must be used. |
| Test kit - Manufacturer/Model No.: | Testing Methodology: |
| Analyzer - Manufacturer/Model No.: | Testing Methodology: |
| DPH certified treatment plant operator who will use and maintain test kit and/or analyzer: |
| Name: | DPH Certification #: |
| A treatment plant operator must be identified and documentation from the manufacturer of test kit or analyzer as to its testing methodology must be provided to DPH before an exemption can be considered. Receipt of a project approval from the DPH will be recognized as the exemption. |
| Method to retain test results from analyzerk: Written log Chart recorder SCADA Other: Footnote k: A system must retain continuous readings for a least every 4 hours, and the lowest reading for each day is required to be reported to the DPH monthly on a form located on the DPH’s website. |
| If a continuous chlorine analyzer is to be provided, check all applicable alarms and alarm type(s) to be provided.l Alarms: low level (alarm-set point above CMIN) mg/L low-low level (initiates action) mg/L high level (alarm) mg/L high-high level (initiates action) mg/L Alarm Type: audio visual dialer SCADA Other: Footnote l: If a continuous chlorine analyzer is to be used for compliance monitoring: at least a low and high alarm with a means to alert the system’s operator must be provided; a low-low alarm (recommended at just below CMIN) must also be provided to alert an operator to take action and which automatically shuts down WTP only if other PWS facilities are available to maintain adequate system pressure; and a high-high alarm (recommended less than 4.0 mg/L MRDL) which alerts an operator and automatically shuts down of the WTP only if other PWS facilities are available to maintain adequate system pressure is strongly recommended. |

| Section J. Certification |
| --- |
| This application must be signed by the PWS administrative official, his/her authorized representative, or certified operator of the PWS. I hereby certify that I have examined the information contained in this application as submitted to the DPH and have determined it to be accurate to the best of my knowledge: |
| Signature: | Date Signed: |
| Name (Print): | Telephone #: |
| Title and Relationship to PWS: |

Figures

# Text boxes

Well(s)

Pressure Tank

BF = 0 therefore no T

Chlorine Injection

Sample Location

(tap or sample line to tap or analyzer)

Chlorine Residual

(C) [mg/L]

Time

TTP = TTS (min)

Flow Well(s)

(QW) [gpm]

1. Flow (Q) and Pipe Contact Time (T) for PWS with Plumbing System

First Consumer:

First Tee or Split in Plumbing

Flow Well(s)

(QW) [gpm]

TTP = Total Contact Time in Pipe Segments

TTS = Total Contact Time to Sample Location = TTP

Flow Well(s)

(QW) [gpm]

Atmospheric Tank

Chlorine Injection

Sample Location

(tap or sample line to tap or analyzer)

Chlorine Residual

(C) [mg/L]

TP2

Flow Booster(s)

(QB) [gpm]

TT1

TP3

First Consumer:

Service

Line

2. Flow (Q) and Pipe and Tank Contact Time (T) for PWS with Distribution

Distribution System

(Total Contact Time to Sampling Location) TTS = TTP (pipes) + TTT (tank)

TTS = TP1 + TT1 + TP2 + TP3

No T is given for a service line.  All T are in minutes.

These figures are for illustration only.

TP1

Flow Booster(s)

(QB) [gpm]

Flow

Booster(s)

(QB)

[gpm]