Petition No. 1008

UTC Power Corporation

UConn, Storrs, Connecticut

Staff Report

November 3, 2011

On September 28, 2011, the Connecticut Siting Council (Council) received a petition from UTC Power Corporation (UTC Power) for a declaratory ruling that no Certificate of Environmental Compatibility and Public Need is required for the installation of a 400 kW fuel cell in the Storrs section of Mansfield.  On October 26, 2011, Council member Brian Golembiewski and Christina Walsh of the Council staff met with UTC Power representative Kim Lingard to conduct a field review of the proposed installation.

UTC Power proposes to install a fuel cell at The University of Connecticut (UConn) Center for Clean Energy Engineering at 44 Weaver Road, Storrs.  The proposed fuel cell is 9 feet wide by 29 feet long by 10 feet tall and would be located on the east side of the building.  The equipment would be completely enclosed.

The proposed installation is a natural gas-fueled, phosphoric acid fuel cell system.  The fuel cell is a distributed generation resource and combined heat and power application that would provide electric power while using waste heat for heating and cooling.  The proposed fuel cell would be paired with an absorption chiller to make chilled water.  The overall efficiency of the fuel cell, when all heat is used, would be 90 percent, including electric and thermal output.

The proposed fuel cell would operate in water balance, meaning that water would not be added or discharged after initial start-up of the facility under normal operating circumstances.  If any water overflow from the unit occurs, it would consist of de-ionized water and flow directly into a sanitary drain.  The unit would meet all Connecticut Department of Environmental Protection air and water quality standards.

Safety features on the fuel cell include a combustible gas sensor and thermal fuses that detect any over-temperature.  If an over-temperature is detected the fuel cell is designed to shutdown and UTC Power would receive a system alarm notification.  An emergency stop button is located on the outside of the enclosure and a gas shut-off valve and electrical disconnect switch would be easily accessible to emergency personnel.

The nearest residential area consists of dormitory buildings for graduate students located approximately 500 feet from the proposed site.  The Longley School building is a laboratory building located approximately 400 feet from the proposed site.  At full power, the fuel cell would emit a noise level below 45 dBA at 400 feet.  The proposed fuel cell would comply with Connecticut noise regulations.