Petition No. 475

Voicestream Wireless

Fairfield, Connecticut

Staff Report

August 31, 2000

On August 22, 2000, Connecticut Siting Council (Council) member Edward S. Wilensky met Voicestream Wireless (Voicestream) representatives J. Brendan Sharkey, Esq., Haider Syed, Brian Raggazine, and David Wicanpole for inspection of a Connecticut Light & Power Company (CL&P) electric transmission line structure (no. 876) located off Morehouse Drive, Fairfield. Voicestream, with the agreement of CL&P, proposes to modify the transmission structure for telecommunications use and is petitioning the Council for a declaratory ruling that no Certificate of Environmental Compatibility and Public Need (Certificate) is required for the modification.

This site consists of an existing Fort Worth Powermount( installed within the 84-foot high CL&P transmission line support structure by Sprint Spectrum L.P. approved by the Council on December 18, 1997 (Petition No. 383). Sprint’s antennas are mounted to a platform with a centerline height of 104 feet above ground level. At that time Sprint contended a distance of about 10 feet would be necessary between the antenna support platform and the top of the tower as a minimum to maintain electric safety clearances.  Also, the Council’s approval in Petition 383 required Sprint to install landscaping; however, this landscaping appears to have little or no upkeep uncharacteristic to the neighborhood.  Staff recommends that landscaping be restored.

Voicestream proposes to attach a platform, similar to Sprint, with three antennas at a centerline height of 95 feet attached to the platform on the Powermount( structure.  The distance between the bottom of Voicestream’s antenna and CL&P’s shield wire would be four feet. While CL&P approves of this design it would be two feet less than their minimum separation.  A structural analysis concludes that one x-brace at the top conductor level would be overstressed one percent and the south foundations of the structure would be overstressed two percent; however these calculations are considered acceptable with no additional reinforcement necessary.  Also, Voicestream would place associated equipment cabinets on a 9-foot by 10-foot steel platform supported by concrete piers within the structure’s footprint and within an existing wood fence compound. Electric telephone utilities would be placed underground from an existing distribution pole. No clearing or grading is proposed.

The proposed site is within an R-3 Residential District zone. There are three homes approximately 150 feet; one each located north, east, and south, of the transmission structure.

The worst case power density for the telecommunications operations at the site has been calculated to be less than 4.5% of the applicable standard for uncontrolled environments.

Voicestream contends that the proposed installation will not cause a substantial adverse environmental effect, and for this reason would not require a Certificate.