Petition No. 476

Connecticut Light and Power Company

New Milford, Connecticut

Staff Report

August 31, 2000

On August 25, 2000, Connecticut Siting Council (Council) member Brian Emerick and staff members Fred Cunliffe and Christina Lepage met Luis Gonzales of Connecticut Light and Power Company (CL&P) for inspection of a CL&P switching station located on Long Mountain Drive, New Milford.  CL&P proposes to modify the switching station to increase the reliability of the power provided to Southwestern Connecticut and is petitioning the Council for a declaratory ruling that no Certificate of Environmental Compatibility and Public Need (Certificate) is required for the modification.

CL&P proposes the installation of two 345-kV circuit breakers, two 345-kV disconnect switches, six 345-kV coupling capacitor voltage transformers and three 345-kV surge arresters within an existing fence line.  The new structures would be placed within the space of the existing structures.  The existing site contains three 345-Kv circuit breakers and three associated 345-Kv transmission lines.  Currently, if any of the three circuit breakers fails existing autransformers may overload, which may cause power failures throughout southwestern Connecticut.  The installation of the proposed equipment would eliminate the possibility of the loss of major transmission paths from the 345-Kv system to the 115-Kv system in southwestern Connecticut.  The proposed equipment would be at the same relative height as the existing equipment thereby causing virtually no additional visual impact.

The proposed site is within the existing CL&P switching station fenced area along Long Mountain Drive, New Milford.  An existing access road will continue to be used to access the site.  The existing switching station is located within a residential area with the closest residential dwelling approximately four hundred feet east of the site.  Wetlands and waterways do exist on the property however they are not within the fenced area and are about five hundred feet west of the site.

CL&P contends that the installation of the proposed structures would have no visual impact to the surrounding area; noise levels at the property lines would remain below state limits; there would be no interference to television or radio; the project is not within a 100-year flood zone or stream channel encroachment lines; and the wetlands and waterways on the site would not be affected this addition; therefore, there would be no substantial adverse environmental impact.