| PETITION NO. 663 - South Norwalk Electric and Water (SNEW) petition for a declaratory ruling that no Certificate of Environmental Compatibility and Public Need is required for the proposed repowering of an existing SNEW Generating Station located at One State Street, Norwalk, Connecticut. | } } } } | Connecticut Siting Council October 7, 2004 |
| --- | --- | --- |

- Findings of Fact

Introduction

- On February 27, 2004, South Norwalk Electric and Water (SNEW) submitted a petition to the Connecticut Siting Council (Council) for a declaratory ruling pursuant to Connecticut General Statutes (CGS) section 16-50k(a) that no Certificate of Environmental Compatibility and Public Need would be required for the proposed repowering of the existing SNEW facility at One State Street in South Norwalk, Connecticut. (SNEW1, p.1, p.5)

- Pursuant to Sections 16-50j-21 and 16-50j-40 of the Regulations of Connecticut State Agencies, the Council, after giving due notice thereof, held a public hearing on July 20, 2004, beginning at 7:00 p.m. in the Norwalk Town Hall Council Chambers, 125 East Avenue, Norwalk, Connecticut.  The Council and its staff made an inspection of the proposed site on July 20, 2004. (Council hearing notice dated May 26, 2004; Transcript, July 20, 2004, p.2)

- Notice of the Norwalk Zoning Commission hearing of April 14, 2004 on the proposed project was provided to all abutting property owners by Certified mail by SNEW on April 2, 2004.  Pursuant to CGS §§ 16-50x(d), applications for location approval were submitted by SNEW to the Norwalk Zoning Commission, the Norwalk Zoning Board of Appeals, and the Norwalk Conservation Commission.  The Norwalk Zoning Commission approved the project on April 21, 2004. The Norwalk Zoning Board of Appeals determined it had no jurisdiction for this project under CGS §§ 16-50x(d) on March 17, 2004.  The Norwalk Conservation Commission determined on March 24, 2004, that no regulated activities regarding wetlands and watercourses would take place and that a full application by SNEW was not necessary. (SNEW 4f, 4g, 4h; SNEW 5, PHQ 1)

- Pursuant to CGS §§ 16-50j(h), the Council solicited the following State agencies for comments on this petition on May 26, 2004: the Department of Environmental Protection (DEP); the Department of Public Health (DPH); the Council on Environmental Quality (CEQ); the Department of Public Utility Control (DPUC); the Office of Policy and Management (OPM); the Department of Economic and Community Development (DECD); and the Department of Transportation (DOT). (Record)

- The following State agency offered comments on the application: the DPH.  The DPH stated the project is not located within any areas of possible drinking water concerns. (DPH letter of June 22, 2004)

- The following State agencies did not offer comments on the proposed project: the DEP, CEQ, DPUC, OPM, DECD, and the DOT. (Record)

Public Need and Benefit

- Southwestern Connecticut is experiencing serious electric reliability problems.  Electric transmission constraints in Southwestern Connecticut result in substantial congestion costs to all Connecticut electric consumers.  Independent System Operator of New England (ISO-New England) submitted an Emergency Capability Request for Proposals (RFP) on December 1, 2003.  The SNEW Repowering Project was proposed in response to this RFP.  (SNEW 1, p. 1, p. 9)

- The addition of 50 MW of fast response power would improve system reliability in the region by decreasing the likelihood of the loss of load.  The project is expected to displace more polluting and less efficient fossil-fueled generation. (SNEW 1, p. 7; ISO-NE 2003 Regional Transmission Expansion Plan, pp. 25-26; SNEW 4, pp.6-7)

Existing Site

- The existing SNEW electric generating station contains five slow speed reciprocating engines installed between the 1930’s and early 1970’s, and one high speed engine installed in 1990, with a combined total output of 17.3 MW.  The site has been used for generation since 1892.  Three of the engines are damaged and all have been rendered inoperable and have been deactivated through ISO-NE since October 2002. (SNEW 1, pp. 2-3; SNEW 2, Overview, p. 1; Tr., pp.58-59)

- SNEW is a municipal electric and water utility established in 1892 which provides service to approximately 6000 customers in the South Norwalk area. SNEW is owned by the Second Taxing District of the City of Norwalk, an entity governed by an elected board of commissioners.  The Second Taxing District is one of the owners and members of the Connecticut Municipal Energy Cooperative (CMEEC).  CMEEC provides all of the power requirements of its member municipal utilities.  (SNEW 1, p. 4)

- The existing SNEW facility consists of a powerhouse building with a dispatch control center, a substation, a garage and warehouse, parking and storage areas, and underground fuel storage. Utility easements on the west side of the site include sewer, water, cable and electric. The existing engines employed Number 2 fuel oil stored in two 40,000-gallon underground fuel storage tanks and was interconnected to the Connecticut Light and Power Company (CL&P) system at 27.6kV.  (SNEW 2, p. 1-1)

The Proposed Project

- The proposed Repowering Project is subject to a declaratory ruling by the Council under CGS § 16-50k(a) as a Brownfield site which would be used solely for the purpose of generating electricity, would use a fuel other than nuclear materials or coal, and would be constructed at a site where an electric generating facility operated prior to July 1, 1998.  (SNEW 1, p. 3)

- The existing SNEW site is 1.6 acres in size and is within the Industrial Zone No. 1 zone. Other uses in the immediate vicinity of the site are the South Norwalk Railroad Station and parking garage to the east, an inactive industrial site to the south, a senior citizens’ housing complex to the north and residential housing to the west across a four-lane divided roadway.  (SNEW 1, p.5)

- The existing SNEW station has five metal stacks, each approximately 98 feet in height.  The five stacks would be removed and replaced by three new stacks approximately 130 feet in height. An existing 90-foot tall brick stack would remain and serve as the stack for the project’s black start generator.  (SNEW 1, p.8)

- The project would include three Wartsila 18V50 DF dual fuel generator sets. Each generator set is nominally rated at 17 MW, 13.8 kV 3 phase 60 Hertz.  Each generator would fire natural gas as the primary fuel and low sulfur distillate oil as an alternate fuel.  (SNEW 2, p.1-1)

- Each engine generator set would produce 16,368kW of power at the generator terminals at a peak efficiency of 47 percent on natural gas.  Each engine generator would be 60 feet in length, 17 feet in width and 20 feet in height with a weight of 400 tons.  (SNEW 5, PHQ. 6)

- The generator sets would be housed in a new 6700 square foot building which would be constructed on the same location as an old structure which would be demolished.  No below grade demolition would be needed.  The engines would connect to an existing switchyard located adjacent to an existing powerhouse building and would inject electricity into the existing 27.6 kV CL&P distribution system. (SNEW 4, p.5)

- Modifications to the existing SNEW site would include a new fuel truck unloading station, a fuel transfer pump station, exterior foundations for the new selective catalytic reduction (SCR) stacks, transformers and reactors, site grading and site drainage and surfacing. (SNEW 2, p. 1-2)

- Modifications to the existing SNEW powerhouse would include a new engine-generator room, 15 kV switchgear area, new control room, renovations for new compressed air stations and an emergency black start generator.  (SNEW 2, p.1-2)

- SNEW would install a new lube oil storage/transfer system, waste oil collection system and new service/instrument air systems.  (SNEW 2, p.1-2)

- SNEW would install 13.8 kV paralleling switchgear to interconnect the new electric generators to the existing 13.8 kV electric distribution system, a 13.8 kV/4160/480/120 volts station service power system to provide station service power to the new equipment, and one emergency power system for black start of the power generation system and to serve emergency electric loads to maintain the electric generation system.  (SNEW 2, p. 1-2)

- The SNEW plant is interconnected to the existing Norwalk 9S Substation which is owned and operated by CL&P.  (Tr., p.19; SNEW 4, p.4)

- A supply of natural gas via a 16-inch diameter natural gas line installed in 2003 is already available on the SNEW site, and therefore no new infrastructure construction for natural gas would be required.  The generating units would run on low pressure gas, so no compression of gas would be required. (Tr., pp. 19-20; SNEW 4, p.4)

- The units would be delivered to a barge facility in Norwalk in three parts; a generator, the engine block, and the frame to the engine block.  SNEW has identified a route from the Norwalk harbor to the site.  Some relocation of overhead wires would be needed to allow the units to pass through the streets.  (Tr. p. 23)

- The turbine units would be installed on the site prior to putting up the structural steel for the powerhouse building.  (Tr., p.23)

- Removal of existing equipment and building demolition would take approximately ten weeks to complete.  The Number 2 fuel oil storage tanks would remain and be used for alternate fuel storage of low sulfur distillate oil.  (SNEW 5, PHQ. 7)

Environmental Considerations

- The proposed repowering site is almost entirely developed, consisting of concrete, pavement, gravel and graded or disturbed soil.  No significant wildlife habitat exists on the SNEW site.  There are no known existing populations of Federal or State Endangered, Threatened or Special Concern species at the proposed site.  (SNEW 2, p. 4-3; SNEW 2, App. B)

- The area surrounding the proposed site within one mile is highly developed with commercial, industrial, and residential uses.  (SNEW 2, p. 4-7)

- The project would employ state-of-the-art technology for the control of air emissions, including selective catalytic reduction for the control of nitrogen oxides, and an oxidation catalyst to control carbon monoxide and volatile organic compounds.  (SNEW 1, p. 6; SNEW 4, p.10)

- Air emissions from the project would not exceed the major source thresholds and would not be subject to the Prevention of Significant Deterioration review.  The project’s NOx emissions would be subject to Lowest Achievable Emission Rate (LAER) and emission offset requirements.  The volatile organic carbon emissions (VOC’s) would not be subject to LAER or offsets.  Emissions of VOC’s, carbon monoxide and particulate matter with a diameter of less than or equal to 10 microns are subject to Best Available Control Technology Requirements.  The project would be subject to Connecticut’s NOx Budget Plan, which requires stack testing and continuous emissions monitoring.  (SNEW 1, p. 6; SNEW 4, pp.10-11)

- The Repowering Project would comply with all ambient air quality standards and Hazardous Air Pollutants requirements.  (SNEW 1, p. 6; SNEW 4, p.11)

- The project must obtain NOx emission reductions (offsets) to offset new emissions at a ratio of at least 1.3 to 1.  The project would therefore be required to obtain 93 tons of offsets. The offsets must be obtained from the same area in which the source operates or an area that contributes to ozone in the area, such as Fairfield County or the Metropolitan New York City area.  (Tr., pp.48-49, SNEW 2, p. 5-8)

- The potential emissions of the project are shown in the table below.

| Potential Emissions of the Proposed Project |  |  |
| --- | --- | --- |
| Pollutant | Net Maximum Potential Emissions (TPY) |  |
| PM10 | 21.4 |  |
| SO2 | 8.8 |  |
| NOx | 70.8 |  |
| CO | 39.7 |  |
| VOCs | 23.6 |  |

(SNEW 2, p. 5-5)

- SNEW submitted an air permit application to the DEP on February 27, 2004.  A dispersion modeling report demonstrating compliance with ambient air quality standards was submitted to the DEP on April 2, 2004.  Both of the documents are currently under review by the DEP.  (SNEW 4, Pre-filed Testimony, p.11)

- A continuous emissions monitoring system (CEM) would be installed on the project, with a CEM system report provided quarterly to the DEP.  (SNEW 5, Q. 9)

- The project would require water for cooling, sanitary, and maintenance purposes.  Peak water supply demand would be approximately 250 gallons per minute (gpm) during summer operating conditions at full load.  Average water use would be 0.15 million gallons per day (MGD), assuming 10 hours per day during the summer.  The project would be supplied with water by SNEW, which has an available yield of 10.0 MGD, and maximum daily demands of 8.0 MGD.  (SNEW 1, p. 7)

- Water discharge from the proposed project is estimated to be less than 100,000 gallons per day, which would be discharged to the Norwalk Wastewater Treatment Plant.  Water discharges would be minimized through the recirculation and pretreatment of cooling tower makeup water.  All wastewater discharges would be monitored under a DEP discharge permit.  The Norwalk Wastewater Treatment Plant has the capacity to treat 30 MGD.  (SNEW 1, p.7)

- There are no inland wetlands or watercourses on the proposed site.  Storm water runoff would continue to be collected and discharged to the existing storm drainage system serving the area. (SNEW 1, p. 9)

- Both the City of Norwalk and State of Connecticut have noise standards requiring that noise from this project may not exceed 51 dBA at night and 61 dBA during the daytime at the boundary of a residential noise zone.  The project has been designed to meet this limit at any residential area. (SNEW 1, p. 7)

- SNEW conducted a noise modeling program which concluded that noise control measures would be required on the project to achieve compliance with noise regulations.  With the inclusion of noise control measures, the 51 dBA night time noise standard would be achieved in all residential locations including the upper floor residences of nearby apartments.  (SNEW 1, p. 7, Tr., pp. 24-25)

- SNEW considered noise vibration from the turbines, including noise coming through the exhaust.  Noise control measures have been designed to control all low-frequency noise from the project.  (Tr., pp. 41-42)

- The noise level from the proposed repowering project is expected to be much less than that of the previous SNEW generating plant.  (Tr., p. 28)

- The project is typically planned to operate Mondays through Fridays, during the hours of 8:00 a.m. to 8:00 p.m.  (Tr., pp. 45-46)

- An existing noise barrier along Martin Luther King Drive was installed for a temporary generating unit installed in 2003.  The sound barrier will be removed because it is no longer necessary, and its removal would have no effect on sound levels from the site.  (Tr., pp. 30-31)

- The repowering project would include three new stacks approximately 130 feet in height clustered together on the east side of the power house.  The stacks were originally planned to be enclosed, but for aesthetic purposes, the enclosure was removed from the design.  (SNEW 1, p. 8, Tr., p. 15, pp. 21-22)

- The framework surrounding the three stacks would be painted a color to match the sky, such as a light blue or a light gray.  (Tr., p.22; SNEW 8)

- The proposed stacks would be obscured from view on the west side of Dr. Martin Luther King Drive when leaves are on the trees.  During the winter months, the stacks would be visible through the branches of the trees.  The stacks would be visible throughout the year from the Leroy Downs Apartments to the north.  (Tr., pp.36-37, SNEW 2, Section 2, Viewpoint 1, Viewpoint 8)

- The proposed stacks would be visible from the Side by Side community school at a distance of approximately 1030 feet, from the Columbus School at a distance of approximately 800 feet, from the Harbor View Heights Condominium at a distance of approximately 525 feet, and from the Copper Apartments at a distance of approximately 700 feet.  The top of the stacks may be visible from Veteran’s Memorial Park at a distance of approximately 2500 feet.  (SNEW 2, pp. 2-7 to 2-24)

- The proposed project would connect to CL&P’s existing 27.6 kV underground distribution lines at the State Street Substation and interconnect to the Wilson Avenue Substation.  All of the circuits entering and leaving the project area are currently and projected to be underground circuits which shield electric fields from the circuits.  No changes to the underground interconnecting circuits are planned.  (SNEW 2, pp. 7-5 to 7-6)

- SNEW took magnetic field measurements in January 2004 in the area of the proposed project with the results shown in the table below.

Magnetic Field Measurements

| Location | Range in mG |
| --- | --- |
| State Street (South side) | 3.0-10.5 |
| State Street (North side) | 2.0-4.0 |
| Bates Court (North side) | 0.8-10.0 |
| Bates Court (South side) | 2.7-10.3 |
| SNEW driveway (State Street) | 2.4 |
| SNEW driveway (manhole in sidewalk) | 26.8 |

(SNEW 2, p. 7-5 to 7-6)

- SNEW performed no magnetic field calculations due to a lack of load flow data with the proposed generation in service.  However, SNEW estimates the maximum magnetic fields would range between two to three times the measured values, depending on the level of generation produced and the distribution served from the site. (SNEW 2, p. 7-6)

- The project would use drift eliminators to reduce the impacts of fogging, icing, and visible condensed water vapor plumes from the cooling towers.  Ground fog would be expected to occur a maximum of one hour per year, with elevated visible plumes expected no more than 35 hours per year.  (SNEW 4, p.13; SNEW 5, PHQ 16)

Project Cost

- The cost of the proposed project, including the costs of equipment and labor, is estimated as $40,000,000.  (Tr., p. 24)