CONNECTICUT DISTRIBUTED GENERATION TECHNICAL WORKING GROUP

MEETING MINUTES

Tuesday, April 20, 2021

9:00 AM – 11:15 PM

Attendees:

- Andy Mayshar, Con Ed Clean Energy Business

- Jean-Paul LaMarche, Clean Focus (Greenskies)

- Carl Nowiszewski, Eversource

- David A Ferrante, Eversource

- Joseph Debs, Eversource

- Mark Kirschbaum, UI

- Joseph Folz, UI

- Elder Romero, UI

- Joseph Marranca, UI

- Brad Marszalkowski, ISO NE

- JR Viglione, OCC

- Ion Balan, UI

Facilitators:

- Zak Alexander, PURA, Zachary.Alexander@ct.gov

- Lauren Bergman, PURA, Lauren.Bergman@ct.gov

Not in Attendance

- Amanda De Vito Trinsey, CIEC/Couch White, LLP

.Meeting Schedule and Minute Keeping

- Monday, May 24, 2021

- Jean-Paul LaMarche or designee to take minutes

- Tuesday, June 22, 2021

- David Ferrante or designee to take minutes

- Tuesday, July 20, 2021

- Joseph Folz or designee to take minutes

- Tuesday, August 24, 2021

- Amanda De Vito Trinsey or designee to take minutes

- Previous Meeting Minutes Reviewed & Approved

- Eversource Presentation on Hosting Capacity Maps

Presented by Joseph Debs

- Eversource’s current & future Hosting Maps.

- Cautioned that hosting maps may not always reflect current queue and should only be used for preliminary guidance

- Provide ability to establish reasonable expectation of connection at a particular site, i.e. what interconnection will look like before you apply

- Quick, easy way to evaluate sites for interconnection

- Disclaimer spells out limitations of capacity maps

- Gather all information about all interconnections and run scenario of hosting capacity maps monthly

- Estimate maximum hosting capacity without significant upgrades

- Hosting capacity maps updated once a month

- One-month lag between new generation added and what’s shown on map

- For informational purposes, does not provide detailed explanation of upgrades

- Information provided:

- Circuit, voltage, substation, hosting capacity

- Limitations

- Does not secure queue position

- Does not include all voltage and thermal scenarios

- Does not include protection and control limitations

- Do not all support reverse flow – can change if aware of issue

- Does not consider temporary overvoltage of risk of islanding

- Does not provide equipment upgrade information

- Impact study needed to provide information on equipment upgrade

- Hosting capacity is dependent on load in an area

- Even if within the capacity limits, may still need small upgrades

- Need to consider the availability of overhead lines – additional challenges when lines are underground

- Constraints can occur in circuit or substation, or both

- Working on user manual and log in to help users employ the maps and track usage

- Other upgrades include more granular data, information on queue, measuring tool

- UI Presentation on Hosting Capacity Maps

Presented by Elder Romero

- UI has two hosting capacity maps – one for residential PV (secondary lines) and a beta version of a map for primary lines (covering only a single substation)

- Demonstrated the secondary map and the ability to search on a Residential Account to determine if an upgrade might be required

- Presented info on Avangrid hosting maps in New York

- Cautioned that hosting maps may not always reflect current que and should only be used for preliminary guidance

- Over 95% of interconnection applications are for residential rooftop PV

- Use ESRI mapping

- Testing ESRI, kevala, and EPRI for new mapping capabilities

- Public facing map has legend for whether interconnections are possible at a specific location

- Provides enough granularity to search by address

- Includes measurement tool, can draw on map

- Eligibility form to allow developer to input details of proposed system, obtain more detailed response on what is allowed

- Provides basic information before proceeding with application

- Circuit models were updated once a year, DG updated more regularly

- DER data updated quarterly

- Primary hosting capacity maps are still a work in progress but UI is hoping to leverage work done by sister utilities in New York to increase the speed of deployment

- ISO-NE Presentation on IEEE-1547

Presented by Brad Marszalkowski

- Currently inverter manufacturers products don’t meet this standard – implementation timelines may change based on when manufacturers can meet these requirements

- Indicated that a common standard for all ISO New England territory was desired

- The developers agreed that a common standard was desirable

- IEEE-1547 includes guidelines on connecting DERs to distribution network

- Critical to the inclusion of DERs

- Behind the meter solar is one of largest sources in ISO-NE

- PV mostly in MA, good amount in RI and CT

- Important to study system-wide

- Most recent version is 2018

- Islanding not big issue if you have shale trip set up correctly

- MA TSRG working on implementation standards for NE

- Discussion on IEEE-1547 Presentation

- Multiple developers support standardized guidelines for NE

- Connecticut could adopt the standards being developed by MA TSRG and ISO

- First item is the bulk system support implementation, ride through

- Try to stick with MA’s timeline for implementation

- Similar standards across states helps utilities who work across multiple states

- ISO NE wants NE-wide implementation of 1547

- Open Discussion

- Developer feedback on hosting map presentations positive

- Most important is keeping maps up to date

- Including queue is a positive change

- Future discussions: Implementation of IEEE-1547

- Highly detailed and technical

- Difficult challenge, big effort

- What system is needed to work through IEEE-1547 implementation

- How to leverage best practices from MA

- Worth investigating MA’s approach to IEEE-1547

- IEEE-1547 governs standards

- MA is working on process for implementing IEEE-1547

- Policy group needs to take into account shifting policies to best implement standards

- Large amount of PV interconnecting in low load areas leads to congestion

- Implementation/process/policy issues that will not be addressed by IEEE-1547