# STATE OF CONNECTICUT

# DEPARTMENT OF ENERGY & ENVIRONMENTAL PROTECTION

# OFFICE OF ENVIRONMENTAL REVIEW

# 79 ELM STREET, HARTFORD, CT 06106-5127

To:	Eric McPhee - Supervising Sanitary Engineer

DPH - Drinking Water Section, 450 Capitol Avenue, MS#51WAT, Hartford

From:	David J. Fox - Senior Environmental Analyst	Telephone:   860-424-4111

Date:	November 7, 2014	E-Mail:  david.fox@ct.gov

Subject:	Stony Brook Water Treatment Plant Upgrade, Montville

The Department of Energy & Environmental Protection (DEEP) has received the Notice of Scoping for the proposed upgrade to the Stony Brook Water Treatment Plant in Montville.  The following comments are submitted for your consideration.

The Natural Resources Conservation Service’s Soil Survey depicts a band of Scarboro muck associated with Stony Brook immediately north of the project site.  A significant portion of the proposed building addition is within the 50-foot upland review area, as depicted on the site plan provided.  The Department recommends that the runoff from the roof of the proposed addition not be discharged directly to the wetland or the upland review area.  The feasibility of infiltrating this runoff should be investigated, considering the suitability of the soils and availability of space.  Inland wetlands and watercourses, with associated upland review areas, are regulated by the local inland wetlands agency, pursuant to section 22a-42 of the CGS.  The local agency should be contacted regarding permit requirements.

In order to protect wetlands and watercourses on and adjacent to the site, strict erosion and sediment controls should be employed during construction.  The Connecticut Guidelines for Soil Erosion and Sediment Control prepared by the Connecticut Council on Soil and Water Conservation in cooperation with DEEP is a recommended source of technical assistance in the selection and design of appropriate control measures.  The 2002 revised edition of the Guidelines is available online at: Erosion Control Guidelines.

Stormwater discharges from construction sites where one or more acres are to be disturbed, regardless of project phasing, require an NPDES permit from the Permitting & Enforcement Division.  The General Permit for the Discharge of Stormwater and Dewatering Wastewaters Associated with Construction Activities (DEEP-WPED-GP-015) will cover these discharges.  The construction stormwater general permit dictates separate compliance procedures for Locally Approvable projects and Locally Exempt projects (as defined in the permit).  Locally Exempt construction projects disturbing over 1 acre must submit a registration form and Stormwater Pollution Control Plan (SWPCP) to the Department.  Locally Approvable construction projects with a total disturbed area of one to five acres are not required to register with the Department provided the development plan has been approved by a municipal land use agency and adheres to local erosion and sediment control land use regulations and the CT Guidelines for Soil Erosion and Sediment Control.  Locally Approvable construction projects with a total disturbed area of five or more acres must submit a registration form to the Department prior to the initiation of construction.  This registration shall include a certification by a Qualified Professional who designed the project and a certification by a Qualified Professional or regional Conservation District who reviewed the SWPCP and deemed it consistent with the requirements of the general permit.  The SWPCP for Locally Approvable projects is not required to be submitted to the Department unless requested.  The SWPCP must include measures such as erosion and sediment controls and post construction stormwater management.  A goal of 80 percent removal of total suspended solids from the stormwater discharge shall be used in designing and installing post-construction stormwater management measures.  The general permit also requires that post-construction control measures incorporate runoff reduction practices, such as LID techniques, to meet performance standards specified in the permit.  For further information, contact the division at 860-424-3018.  A copy of the general permit as well as registration forms may be downloaded at: Construction Stormwater GP.

If any water mains or storage tanks are to be tested and disinfected, the discharge would be covered by the General Permit for the Discharge of Hydrostatic Pressure Testing Wastewater (DEP-PERD-GP-011).  This general permit applies to all discharges of waters used to test the structural integrity of new or used tanks and pipelines that hold or transfer drinking water, sewage, or natural gas.  The general permit contains pH, chlorine, oil and grease, and suspended solids limits which will need to be complied with during the testing and verified through monitoring.  Registration is required to be submitted to the Department in order for the discharges to be authorized by this general permit.  A fact sheet, the general permit which includes the registration form, titled Notice of Coverage, and the Application Transmittal form may be downloaded at: Hydrostatic GP.

Development plans that entail soil excavation should include a protocol for sampling and analysis of potentially contaminated soil.  A soil management plan should be developed for the project to deal with soils during construction.  The Department’s Guidance for Utility Company Excavation should be used a guide in developing the plan.  The guidance is available on-line at: Utility Guidance.

The Natural Diversity Data Base, maintained by DEEP, contains no records of extant populations of Federally listed endangered or threatened species or species listed by the State, pursuant to section 26-306 of the Connecticut General Statutes, as endangered, threatened or special concern in the project area.  This information is not the result of comprehensive or site-specific field investigations.  Also, be advised that this is a preliminary review.  A more detailed review may be conducted as part of any subsequent environmental permit applications submitted to DEEP for the proposed site.  Consultation with the Natural Diversity Data Base should not be substituted for on-site surveys required for environmental assessments.  The extent of investigation by competent biologist(s) of the flora and fauna found at the site would depend on the nature of the existing habitat(s).  If field investigations reveal any Federal or State listed species, please contact the DEEP Geologic & Natural History Survey at 860-424-3540.

The NDDB includes all information regarding critical biologic resources available at the time of the request.  This information is a compilation of data collected over the years by the Department’s Natural History Survey and cooperating units, private conservation groups and the scientific community.  This information is not necessarily the result of comprehensive or site specific field investigations.  Current research projects and new contributors continue to identify additional populations of species and locations of habitats of concern as well as enhance existing data.  Such new information is incorporated into the NDDB as it becomes available.  If the project is not implemented within 12 months, then another NDDB review should be requested for up-to-date information.  Also be advised that this is a preliminary review and not a final determination.  A more detailed review may be conducted as part of any subsequent environmental permit applications submitted to DEEP for the proposed site.

Thank you for the opportunity to review this project.  If there are any questions concerning these comments, please contact me.

cc:	Robert Hannon, DEEP/OPPD

Eric Thomas, DEEP/WPSD