| Docket 187A- Milford Power Company, LLC Certificate of Environmental Compatibility and Public Need for the Milford Power Project located off of Oronoque Road in Milford, Connecticut. Reopening of this docket pursuant to Connecticut General Statutes § 4-181a(b) to Modify the Decision and Order in Docket 187 to Allow Milford Power Company, LLC to Suspend its Backup Fuel System Based on Changed Conditions the attachment of conditions to the certificate consistent with the findings and recommendations contained in the Final Report issued by the Kleen Energy Plant Investigation Review Panel and the recommendations of the Thomas Commission. | } } } | Connecticut Siting Council December 2, 2010 |
| --- | --- | --- |

- Opinion

- Introduction

- On January 8, 1999, the Connecticut Siting Council (Council) granted a Certificate of Environmental Compatibility and Public Need (Certificate) to PDC-El Paso Milford LLC for the construction, maintenance and operation of a two-unit 544-megawatt (MW) natural-gas fired combined cycle electric generating facility in Milford.  On December 9, 2003, the Council granted a transfer of the Certificate from PDC-El Paso Milford LLC to Milford Power Company, LLC (Milford Power).

- Condition (1e) of the Council’s Decision and Order (D&O) in this docket required the project to run on natural gas, except during the curtailment of natural gas, when the project may run on low sulfur distillate fuel oil as permitted by the Connecticut Department of Environmental Protection (DEP).  On August 27, 2004, the Council modified the Condition to allow the project to run on natural gas but also to run on distillate fuel oil as permitted by the DEP.

- On July 29, 2010, Milford Power requested that the Council modify its D&O to allow the suspension of the low sulfur (0.05%) distillate fuel oil system at Milford Power, which will eliminate its ability to immediately operate on fuel oil.

- On August 17, 2010, the Council voted to reopen the proceeding on changed conditions under Connecticut General Statutes (C.G.S.) § 4-181a(b) specifically limited to suspension of the backup fuel system at Milford Power and the attachment of conditions to the Certificate consistent with the findings and recommendations contained in the Final Report issued by the Kleen Energy Plant Investigation Review Panel and the Executive Report issued by Thomas Commission.

- Suspension of Backup Fuel Oil System

- Since the Certificate was issued in this docket, natural gas supply has increased and improvements have been made to pipeline infrastructure in New England; improvements have been made to the electric transmission grid in Connecticut; and new power generation facilities have been constructed.  Therefore, the ability to operate the power plant on fuel oil is no longer needed for reliability or economic reasons.

- Since commencement of commercial operation in 2004, Milford Power has never used fuel oil commercially and has only used it in short-term testing and commissioning.  Fuel oil would be more expensive to use than natural gas and the possibility of natural gas pipeline curtailment has been greatly reduced.  Since 2004, there has been one interruption of natural gas service to the plant, which lasted approximately ten hours and was due to a failed valve on a gas pipeline leading to the plant.

- The backup fuel system has caused Milford Power to trip ten times in the past six years.  The trips were typically due to instrumentation incorrectly reading the position of the valve, which causes the unit to shut down as a protective measure.

- Milford Power would recommission and make available the backup fuel oil system within 120 days after the occurrence of a second natural gas delivery disruption to the power plant of five or more consecutive dates within any five-year period.  The backup fuel oil system may also be recommissioned at the plant if future conditions warrant it.

- All existing buildings and equipment associated with the backup fuel system would be maintained for the potential future recommissioning of the system.  The existing 1.2 million gallon oil tank would be emptied but remain in place for potential future use.

- The current maintenance of the fuel oil system costs Milford Power approximately one million dollars per year.  Most of the cost is spent burning oil in testing the reliability of the backup fuel system.  The remainder of the cost is spent in the maintenance and repair of the system.

- The Council finds that the above factors regarding an increase in natural gas supply, improvements to the electrical transmission grid in Connecticut and construction of generation facilities within New England have resulted in changed conditions that reduce the need for the backup fuel oil system currently in place at Milford Power.  The Council will approve the request of Milford Power to suspend the low sulfur (0.05%) distillate fuel oil system at the Milford Power Plant.

- Kleen Energy Plant Investigation Review Panel (Nevas Commission) and the Thomas Commission

- On February 7, 2010, there was an explosion at the Kleen Energy Systems, LLC power plant facility in Middletown, Connecticut that was caused by the release and combustion of natural gas that was being used to clean natural gas piping at the facility, a procedure known as a “gas blow.”

After the explosion, Governor M. Jodi Rell established a commission, the Kleen Energy Plant Investigation Review Panel, chaired by Judge Alan Nevas (the “Nevas Commission”), to identify the cause and origin of the explosion and to provide information necessary for a second Commission, the Thomas Commission, to provide recommendations for legislative and regulatory changes.  On June 3, 2010, the Nevas Commission issued its Final Report that included an analysis of existing regulations concerning the “cleaning” or “blowing” of natural gas pipelines and recommended changes to regulatory criteria for consideration by the Thomas Commission to prevent the recurrence of such an explosion.

The specific findings of the Nevas Commission are as follows:

- “The Commission finds that the February 7, 2010 explosion was the product of a process used to clean a natural gas pipeline using large quantities of natural gas that came into contact with an ignition source known as a gas blow”;

- “The Commission finds that, although the Kleen Energy construction project was heavily regulated by a variety of agencies, no agency regulated the process used – or any process that might be used such as gas purging – to clean the natural gas pipeline that was the source of the explosion”; and

- “The Commission finds, and recommends to the Thomas Panel, that there are significant regulatory steps that should be taken to ensure that the events of February 7, 2010 are not repeated.”

On September 21, 2010, the Thomas Commission issued an Executive Report that included recommendations for regulatory changes that can be accomplished by executive order, state legislation or adoption of regulations.

The Executive Report issued by the Thomas Commission contains the following Final Recommendations:

a. Use of flammable gases to conduct “gas blows” should be banned in Connecticut, at least until such time as there are accepted national standards published and in place;

b. Requirement of special inspectors, development of safety plans and payment of cost by

power plant applicant;

c. Assembly of a “Coordinating Council” for future power plant applications;

d. Attachment of conditions to certificates issued by the Siting Council that include a ban on flammable gas blows and compliance with code recommendations;

e. Review of existing power plants by the Siting Council to modify final decisions of power plants within its jurisdiction to determine whether such plants warrant further attention;

f. Adoption of the following codes and regulations by the Connecticut Department of Public Safety:

- Amend the Flammable & Combustible Liquids Code, C.G.S. §29-320 to adopt the 2010 Edition of NFPA 37, “Standard for the Installation and Use of Stationary Combustion Engines and Gas Turbines”;

- Amend the Gas Equipment and Piping Code, C.G.S. §29-329 to adopt the 2009 Edition of NFPA 54, “National Fuel Gas Code” including Temporary Interim Amendment 09-3 and by Connecticut amendment remove the exception regarding fuel gas piping at electric utility power plants and to adopt ASME Standard B31, “Code for Pressure Piping” including mandatory compliance with Appendices IV and V of ASME B31.1 for newly constructed electric utility power plants;

- Amend the Connecticut Fire Prevention Code adopted pursuant to C.G.S. §29-291a to add new sections in the Hazardous Materials Chapter regarding “Gas Piping Cleaning Operations”;

- Amend the Fire Prevention Code adopted pursuant to C.G.S. §29-291a to delete and revise sections 29-291a-2(a) and (b) regarding “Relationship to State Fire Safety and Building Codes” and to adopt the requirements of the 2010 Edition of NFPA 850 “Fire Protection for Electric Generating Plants and High Voltage Current Converter Stations”; and

g. Adoption of legislation to provide for payment into a code training fund by any power plant applicant who is required to obtain Siting Council approval.

In its review of the Nevas Commission and Thomas Commission findings and recommendations, the Council must consider its jurisdiction over these matters.  Jurisdiction over electric generating facilities is conferred upon the Council pursuant to the Public Utility Environmental Standards Act (PUESA).  PUESA does not charge the Council with any authority to impose or enforce occupational safety and hazard standards and regulations.  The Council recognizes that the tragic accident that occurred at the Kleen facility is an isolated incident with unique circumstances.  In the event of a future incident, the Council will consider the adoption of any specific findings and recommendations of any Commissions that may be appointed by the Governor in response to such an incident.

Notwithstanding its statutory jurisdictional limitations, the Council has considered changed conditions in this docket.  Upon review of the Nevas Commission findings and recommendations concerning gas blows; the Thomas Commission recommendations regarding banning gas blows, assembly of a “Coordinating Council” for future power plant applications, and adoption of certain fire codes; and a recommendation by the United States Chemical Safety Board to prohibit natural gas blows during power plant construction, the Council finds changed conditions in industry practices specifically pertaining to the gas pipe cleaning process.

Based on the changed conditions in this proceeding, the Council will attach conditions to the Decision and Order of this docket in accordance with the Nevas Commission and Thomas Commission recommendations.