Petition No. 1000

The Connecticut Light and Power Company

Statewide

Staff Report

August 11, 2011

On July 6, 2011, the Connecticut Siting Council (Council) received a Petition (Petition) from The Connecticut Light and Power Company (CL&P) for a declaratory ruling that no Certificate of Environmental Compatibility and Public Need is required for the proposed transmission remediation activities to comply with the North American Electric Reliability Corporation (NERC) facility ratings recommendation to industry.  Specifically, on October 7, 2010, NERC issued a nationwide alert to the bulk power industry of possible discrepancies between the design of transmission facilities and actual field conditions that require immediate attention.  NERC recommended that the utilities assess transmission lines to confirm that the facility ratings were being determined based on actual field conditions and that any difference between design and actual field conditions is within the tolerances defined by the facility rating methodology.

Transmission lines have a thermal rating in order to protect the line from overheating under excessive load.  As the line loading increases, the heat causes the conductors to expand in length and increase sag.  This can lead to clearance issues if obstacles are in the way of the conductors or the actual line clearance is less than predicted.  CL&P’s evaluation will determine if any height/clearance issues prevent the lines from reaching their design thermal rating.  If they do, this could be a NERC reliability issue since the line’s rating may be reduced.  CL&P would seek corrective action.

To comply with the NERC recommendation, CL&P plans to:

- Review as-build transmission line clearances on 345-kV, 115-kV and portions of the 69-kV system.  Light detection and ranging technology (LiDAR) will be employed to measure the distances to the existing ground profile and other objects within the right-of-way (ROW);

- Utilize computer modeling to graphically translate the LiDAR data;

- Identify and evaluate any clearance “points of interest” for potential impact on the transmission line thermal rating;

- Remediate all clearance issues that adversely affect a line’s ability to achieve its designed thermal rating;

- Work with customers to address encroachments or other ROW modifications that have occurred within its easements or property;

- File status reports twice per year with NERC on its findings and progress.

CL&P plans to have the field clearance assessments of the 345-kV lines completed by year-end 2011.  The assessment of the 115-kV and 69-kV lines would be completed by year-end 2012.  Remediation activities would be completed within one year of identification of a clearance issue.  The remediation activities would include taking measures to prohibit access to the area(s) of concern until the remediation is complete, clear soil or re-grade to improve clearances, increase tension on the line(s) to eliminate or reduce sag, replace an existing structure to increase the height of the conductors, and/or install an intermediate structure to reduce the conductor span sag.

The remediation activities are not expected to have a substantial adverse environmental effect.  No new ROW would be required.  Any effects to wetlands/watercourses would be temporary.  Proper erosion and sedimentation controls would be employed.  Existing access routes would be utilized.  Tree and vegetation clearing would be kept to a minimum.  Electric and magnetic fields (EMF) would decrease in areas where conductor heights above ground are increased.  Changes to EMF off of the ROW would be negligible.