Petition No. 354

Connecticut Light & Power Company

Emergency Installation of One Gas Turbine Unit at South Meadows Station

Hartford, Connecticut

Staff Report

May 21, 1996

On May 17, 1996, Connecticut Siting Council (Council) members William J. Huber, Colin C. Tait, Gerald J. Heffernan, and Joel M. Rinebold, Mark Kohler, and Fred Cunliffe of Council staff met with Daniel Bergeron, James A. Ginnetti, Robert Carberry, Al Rice, Daniel Venora, and Donald D. Biondi of Connecticut Light & Power Company (CL&P) at the proposed project site within South Meadows Station in the City of Hartford, Connecticut.

The impetus for this petition is the continued shutdown of the three nuclear units at Millstone Point Power Station and the potential for electric generation shortages in Connecticut during peak load periods this summer.  Moreover, CL&P’s ability to bring power into the State during high load periods is limited by physical constraints of the transmission system.

CL&P plans to implement measures to meet forecast power needs and avoid undesired service curtailments.

CL&P will be purchasing power from every available resource, both in and out of Connecticut;

CL&P will run all of its available generating units to their reasonable limits;

CL&P will be installing capacitors on distribution feeders in various bulk substations, which should increase the ability of the transmission system to bring power into Connecticut by at least 100 megawatts (MW);

CL&P has asked all private power producers in the State to generate to their maximum output;

CL&P will reactivate Middletown Unit No. 1, and has arranged to reactivate The United Illuminating Company’s Bridgeport Harbor Unit No. 1;

CL&P has arranged to shift load to substations outside Connecticut to help relieve the capacity shortage in the State; and

CL&P is exploring additional interruption of service with industrial and commercial customers, and use of customer-owned emergency generators.

Even with these measures, the State of Connecticut will experience a capacity deficiency this summer unless additional generating capacity is brought into the State.

CL&P’s contingency plan is to temporarily install 160 MW of generation at Devon Station, Milford, Connecticut, consistent with CL&P’s 1996 Summer Capacity Assessment without Millstone Station and Bridgeport Harbor 2.  While the proposed 40 MW of generation at South Meadow Station is not specifically outlined in the above mentioned assessment, CL&P contends the proposed generation at South Meadow Station is only for peaking capacity. The proposed South Meadow Station’s 40 MW unit is part of a plan to insure generating capacity, meeting the company’s criteria of capacity shortage to one day in ten years, in the event Connecticut Yankee Nuclear Power Station  suffers a prolonged outage.

CL&P chose South Meadow Station as a temporary installation because necessary infrastructure such as jet fuel availability, electric transmission line accessibility, and water availability exists on-site.  Other generating stations in the State may have only two of the three parameters necessary for an expedited installation of a gas turbine.

The unit will be a new General Electric LM 6000 gas turbine generator modified to burn jet fuel.  The unit will be 70 feet long by 47 feet wide by 36 feet high.  The stack height of the unit is approximately 43 feet and, if needed, an additional silencer would add 10 feet to the stack height.  The installation of this turbine unit will add approximately 40 MW of generating capacity.  The chosen capacity is arbitrary based upon inventory availability for a short-term lease arrangement.  A new 600-foot fuel line will be installed above ground from the fuel tank yard to the turbine unit.  CL&P has an existing Spill Prevention Control and Countermeasure Plan for South Meadow Station.  The turbine will be water-cooled via a tap off an existing municipal water intake at South Meadow Station.

The turbine unit will generate power at 13.8-kilovolts (kV) and be connected to 13.8-kV to 115-kV generator step-up transformer.  The interconnection to CL&P’s existing 115-kV transmission system will be via a new 800-foot long line consisting of three new structures standing between 45 to 75 feet high.  Existing transmission structures at South Meadow Station have heights of 105 and 125 feet.

The project area where the turbine and ancillary equipment will be installed is the former fly-ash handling area for South Meadow Station.  The area is relatively clear, level, and gravel covered.  The project area is approximately 1,000 feet west of the Connecticut River.  Portions of this area are below the 100-year flood contour; however, a levee is between the river and South Meadow Station.  CL&P would install a concrete foundation for the turbine.  No inland wetland or watercourse is within 50 feet of the project area.

The nearest residential area in the City of Hartford is approximately a quarter-mile east of the project area and across the highway.  Noise at 400 feet will be approximately 60 decibels.

CL&P is concurrently working with the Department of Environmental Protection for air emission permits.  CL&P also provided information to local officials in the City of Hartford.  The South Meadow Station is on land zoned industrial, and public utilities are allowed by right by Hartford’s Zoning Regulations.

In order to have the turbine unit available during peak load periods, CL&P has established an in-service date of July 1, 1996, and hopes to have the unit available earlier.  No other emergency generation is being contemplated by CL&P at this time.  CL&P proposes to operate this unit at peak load capacity.  Construction has started and will continue for approximately two months, during which time construction will take place around the clock, seven days a week.  CL&P plans to have this unit available for a six-month period.  In the unlikely event this would become a permanent installation, CL&P would seek appropriate approval from the Council including any State and local approvals that may be required.

CL&P contends the proposed temporary installation of this turbine generating unit is an emergency installation for peak loads this summer (1996).  Furthermore, CL&P submits that this project will not have a substantial adverse environmental effect and requests that the Council render an expeditious declaratory ruling that no Certificate of Environmental Compatibility and Public Need is required.

Council staff makes the following recommendations:

1.	A noise survey shall be conducted, and upon the request of the Council, additional mitigation measures be drafted for Council review and approval;

2.	Operation of the turbine shall terminate on October 31, 1996, corresponding with NEPOOL Capacity Analysis for the period April 1996, through December 1996. CL&P shall provide a report identifying days of operations, MW generated, MW delivered to the electric transmission grid, and an updated forecast of Connecticut’s capacity through 1997, by November 30, 1996.  Any future use of the turbine will require Council review and approval;

3.	CL&P shall provide a schedule and weekly progress reports for construction, testing, and operation;

4.	All changes to Petition No. 354, will require advance notice and Council approval;

5.	Council staff will make inspections on a regular basis; and

6.	Emergency approval for changes to equipment, reconfiguration of site components, and/or construction methods impacting the environment and public safety can be reviewed and approved by the Council Chairman.