Petition No. 378

Aetna Life Insurance Company

Staff Report

July 15, 1997

On Tuesday, July 15, 1997, Connecticut Siting Council (Council) member Colin C. Tait and Council staff Joel M. Rinebold, Fred Cunliffe, and Paul Aresta met Aetna Life Insurance Company (Aetna)  representatives Jimmie Woods, Joseph Todaro, and Jeff Waldron (Sherborn Consulting Group) for a site inspection of the proposed emergency generating devices at 570 Pigeon Hill Road, Windsor and 1000 Middle Street, Middletown.  Aetna is petitioning for a declaratory ruling that no Certificate of Public Safety and Necessity (Certificate) is required for the addition of emergency generating devises at both their Windsor and Middletown offices.

Aetna proposes to replace six 1.0 megawatt diesel emergency generating devices with five 2 megawatt diesel emergency generating devices at their Middletown offices and install the six 1.0 megawatt diesel emergency generating devices at their Windsor offices. On December 13, 1989, the Council acknowledged Aetna’s petition (Pet - 241) that the installation of four 1.25 megawatt generators at their Windsor office at 570 Pigeon Hill Road would not require a Certificate. Aetna has contracted with SCI-TECH INC., to prepare and submit construction and operating permits to the Department of Environmental Protection for the proposed emergency generating devices. One or more generators will operate simultaneously, dependent on the actual load during an emergency.

Facility

1000 Middle Street

Middletown

570 Pigeon Hill Road

| Windsor |
| --- |
| Quantity and Capacity | (5) Five - 2 megawatt generators | (6) Six - 1.0 megawatt generators |
| Maximum Operation | 115 hours per generator | 195 hours per generator |
| % Annual Availability | 1.3% | 2.2% |
| Maximum Fuel Consumption | 15,341 gallons / generator / yr. | 14,600 gallons / generator / yr. |
| Area of Addition/Site Area | .08 acre / 285 acres <1% | .08 acre / 110 acres <1% |
| Distance To Nearest Property | 371 feet | 125 feet |
| Unit Dimensions = L x W x H | 19.8 ft x 7.6 ft x 8.35 ft | 17 ft x 6 ft x 7 ft (approx.) |

Aetna contends that each of the proposed emergency generating devises has a capacity of less than five megawatts; the generators would be installed for the purpose of producing emergency back-up electrical power; operation will be limited to less than 500 hundred hours per year for each unit; Aetna is not an entity which is an electric or gas company. Aetna further contends that the generating devices will not have a substantial adverse environmental effect, and are emergency generating devises as defined in CGS Sec. 16-50i (f) and are therefore except from Council jurisdiction.