Petition No. 539

Northeast Utilities Service Company (NU)

Canton, Connecticut

Staff Report

January 17, 2002

On January 8, 2002, Connecticut Siting Council (Council) member Colin C. Tait and Council staff Paul M. Aresta met NU representative Robert J. Charpentier for an inspection of Connecticut Light and Power's (CL&P) Canton Substation located off Morgan Road, in Canton, Connecticut.  NU is petitioning the Council for a declaratory ruling that the proposed installation of two 115-kV capacitor banks, and associated equipment at the existing Canton Substation would not have a substantial adverse environmental effect.

NU proposes to install two 115-kV, 25.2 MVAR capacitor banks, two 115-kV circuit breakers, two 115-kV circuit switchers, one set of 115-kV current limiting reactors, three 115-kV disconnect switches, and a new 115-kV termination structure.  NU would also expand the relay and control enclosure, and the existing fence line.

The proposed 115-kV termination structure would be approximately 60 feet tall, and all other proposed equipment would be no taller than approximately 22 feet high.  The existing fence in the northwest corner of the substation would be expanded to accommodate the relocation of a mobile transformer.  The fence, located south of the existing 115-kV termination structures, would be expanded to accommodate the installation of the proposed 115-kV capacitor banks and circuit switchers.  The proposed equipment is required to improve area transmission voltage levels during contingency conditions.  The proposed work would be completed by the end of November 2002.

A storm water swale, located southeast of the substation, would be relocated to the east to accommodate expansion of the substation fence.  The Town of Canton Inland Wetlands and Watercourses Agency issued a permit authorizing the proposed work on December 1, 2001.  The proposed equipment would not be located within a 100-year flood zone, or any stream encroachment lines.  No substantial vegetation would be removed.  CL&P contends that the proposed equipment upgrades would have little visual impact; would not cause interference for television or radio; and would not adversely affect the environment, or scenic, historic, and recreational values.