# Petition No. 553

# UTC Fuel Cells, LLC

# South Windsor High School

# Town of South Windsor

# Staff Report

# April 3, 2002

On March 26, 2002, Connecticut Siting Council (Council) member Daniel P. Lynch and Council staff Paul Aresta met Brad Mondschein, a representative of the Town of South Windsor, and Patrick O'Neill, a representative for UTC Fuel Cells for a site inspection of the proposed location for the installation of a 200 kW fuel cell at the South Windsor High School.  The Town of South Windsor and UTC Fuel Cells are petitioning the Council for approval to install a 200 kW fuel cell at the South Windsor High School.

The Town of South Windsor and UTC Fuel Cells propose to add a 200 kW fuel cell to supplement the existing electricity and heat requirements of the South Windsor High School.  The proposed fuel cell would also be a source of electricity and heat during emergencies; the South Windsor High School is a disaster relief center.  The Town of South Windsor would own the proposed fuel cell following the completion of installation and testing.

The proposed fuel cell would be located on the South Windsor High School property, which is an area designated as residential zoning.  The proposed fuel cell is 10 feet wide by 18 feet long by 10 feet tall, and would be surrounded by an eight-foot tall chain link fence.  The proposed fuel cell would be fueled by natural gas, and would generate a maximum of 200kW of electricity, 800,000 BTU's of heat, and water.  There would be no clearing of vegetation for the installation of the fuel cell; however, minor clearing would be required for the extension of the gas service.  The operation of the proposed fuel cell would not require an air emissions permit from the Department of Environmental Protection because it would not trigger any of the air permit applicability thresholds stipulated in §22a-174-3(a) of the Regulations of Connecticut State Agencies.  The proposed fuel cell would generate sound levels of 60 dBA at 30 feet from the fuel cell.

The Town of South Windsor and UTC Fuel Cells contend that the proposed fuel cell power plant is clean, quiet, and highly efficient; and would serve the school and community with electricity and heat; and serve as a tool to enhance the education of fuel cell technology.