Petition No. 777

New Cingular Wireless PCS LLC

Plymouth, Connecticut

Staff Report

July 27, 2006

New Cingular Wireless PCS LLC (Cingular) is petitioning the Council for a declaratory ruling that no Certificate of Environmental Compatibility and Public Need is required for the modification of an existing monopole facility located at 126 South Street in Plymouth, Connecticut.  Cingular proposes to expand the size of the lease area and compound to accommodate shared use.  The Council approved the existing facility on March 16, 1993 (Docket 156).

The existing facility consists of a 180-foot monopole owned by Alltel Newco LLC (Alltel).  The tower supports seven antennas at 178 feet operated by Alltel, and six antennas at 169 feet operated by Verizon.  A 2,000 square foot, L-shaped compound encloses two prefabricated equipment shelters.

Cingular proposes to install six panel antennas on t-arms at a centerline height of 159 feet.  Cingular proposes to expand the lease area and compound by 306 square feet to accommodate a 12-foot by 20-foot prefabricated equipment shelter.

The compound expansion area consists of a cleared area used for parking.  No clearing appears to be necessary.  A chain-link fence would enclose the new compound area.

No modifications to the monopole or foundation are necessary.  With Cingular’s proposed installation, the monopole would be at 104% of capacity and the foundation would be at 107% of capacity.  The structural engineer determined the capacities of both structural elements are within acceptable engineering tolerances.

The worst-case power density for proposed telecommunications operations at the site has been calculated to be 15.24% of the applicable standard for uncontrolled environments.