Petition No. 839 - Revision

Northeast Utilities/CL&P

New Milford, Connecticut

Staff Report

August 28, 2008

On February 28, 2008, the Connecticut Siting Council (Council) approved a petition from Northeast Utilities Service Company, acting for Connecticut Light and Power Company for the replacement of an existing 100-kW, 208/120-Volt, three-phase emergency diesel generator with a 125-kW, 208/120-Volt, three phase emergency generator driven by a liquid propane fired engine at the Long Mountain Switching Station in New Milford.

On August 14, 2008, CL&P submitted a request to the Council to change the conditions for which Petition 839 was approved. CL&P wishes to change the location of the emergency generator and propane storage tank from the southwest corner of the substation to an area near the substation’s control house, which is located near the west side of the substation. CL&P is seeking this change because the location of the new generator and propane tank as approved by the Council would be within the horizontal clearance boundary of an energized 345-kV overhead line.

The original location of the replacement generator was chosen because the propane supplier would be able to access the propane storage tank without entering the substation. With the change of the generator to the new location for which approval is being sought, the propane supplier would need to make arrangements with CL&P personnel to be escorted inside the substation

The Long Mountain Switching Station is set in a small depression, and its perimeter is heavily wooded. There are a few homes in the vicinity, but the existing trees effectively screen the switching station even during the winter months when the leaves are down. The change in the location of the emergency generator will have little effect on the appearance or operation of the substation.

Staff recommends approval.