## Sheet2
ACCC OVERLOAD REPORT: MONITORED ELEMENTS LOADED ABOVE 100.0 % OF RATING SET B
Sort This Column for Lookup | MONITORED ELEMENT | [8 empty] | CONTINGENCY | RATE | FLOW | % | Other Case | Diff
73106-73154-2-SGTN5TSTK | 73106 |  | SOUTHGTN | 345 | 73154 | * | SGTN B | 115 | 2 | SGTN5TSTK | 585 | 690.2 | 118 | #N/A | 23
73227-73633-1-SGTN7TSTK | 73227 | * | E.MERIDN | 115 | 73633 |  | NO.WALLF | 115 | 1 | SGTN7TSTK | 112 | 120 | 105.6 | 101 | 4.6
73196-73198-1-8100-8200DCT | 73196 |  | GLEN JCT | 115 | 73198 | * | SOUTHGTN | 115 | 1 | 8100-8200DCT | 228 | 229.3 | 98.3 | #N/A | 3.3
73669-73681-1-WRIVER2TSTK | 73669 |  | GRAND AV | 115 | 73681 | * | WEST RIV | 115 | 1 | WRIVER2TSTK | 258 | 255 | 95.8 | #N/A | 0.8
73669-73681-2-WRIVER1TSTK | 73669 |  | GRAND AV | 115 | 73681 | * | WEST RIV | 115 | 2 | WRIVER1TSTK | 258 | 255 | 95.8 | #N/A | 0.8
70721-70732-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70732 |  | MCNEIL T | 34.5 | 1 | BASE CASE | 30 | 29.8 | 102.2 | 101.6 | 0.6
73170-73176-1-1165LINE | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | 1165LINE | 138 | 144.9 | 104.4 | 104.2 | 0.2
70712-70719-1-LOSSMP3 | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | LOSSMP3 | 50 | 49.6 | 98.1 | 98 | 0.1
70490-70504-1-BASE CASE | 70490 | * | VERNONRD | 115 | 70504 |  | SBRAT 69 | 69 | 1 | BASE CASE | 24 | 25 | 104.2 | 104.2 | 0
70512-70719-1-LOSSMP3 | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | LOSSMP3 | 50 | 51.2 | 102.4 | 102.4 | 0
70721-70740-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70740 |  | 10-20 | 13.8 | 1 | BASE CASE | 20 | 26.1 | 130.5 | 130.5 | 0
73107-73116-1-BASE CASE | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | BASE CASE | 436 | 428.4 | 95.1 | 95.1 | 0
73144-73167-1-1440LINE | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440LINE | 252 | 255.2 | 98.8 | 98.8 | 0
73162-73163-1-SOUTHEND6T | 73162 |  | WATERSDE | 115 | 73163 | * | COS COB | 115 | 1 | SOUTHEND6T | 239 | 298.7 | 124.7 | 124.7 | 0
73162-73168-1-SOUTHEND6T | 73162 | * | WATERSDE | 115 | 73168 |  | GLNBROOK | 115 | 1 | SOUTHEND6T | 352 | 367 | 102.4 | 102.4 | 0
70512-70719-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 50.2 | 100.4 | 100.5 | -0.1
70512-70735-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70735 |  | WILL #2 | 34.5 | 1 | BASE CASE | 50 | 48.8 | 97.5 | 97.6 | -0.1
70712-70719-1-BASE CASE | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 48.6 | 96.1 | 96.2 | -0.1
70557-70714-1-BASE CASE | 70557 | * | Q CITY | 115 | 70714 |  | Q CTY 34 | 34.5 | 1 | BASE CASE | 50 | 52.3 | 104.6 | 105.2 | -0.6
70521-70555-1-BASE CASE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | BASE CASE | 50 | 52.2 | 104.4 | 105.1 | -0.7
70521-70555-1-354LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 354LINE | 50 | 54 | 107.9 | 108.8 | -0.9
73188-73192-1-BUNKERH2T | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | BUNKERH2T | 112 | 110.7 | 103.6 | 107.2 | -3.6
73188-73192-1-1272-1721DCT | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | 1272-1721DCT | 112 | 132.1 | 126.6 | 131.6 | -5
73651-73668-1-WOODMNT2TSTK | 73651 | * | NH HARBR | 22 | 73668 |  | E.SHORE | 115 | 1 | WOODMNT2TSTK | 475 | 452.6 | 95.3 | 100.6 | -5.3

## thermal
ACCC OVERLOAD REPORT: MONITORED ELEMENTS LOADED ABOVE 100.0 % OF RATING SET B
Sort This Column for Lookup | MONITORED ELEMENT | [8 empty] | CONTINGENCY | RATE | FLOW | % | Other Case | Diff
70490-70504-1-BASE CASE | 70490 | * | VERNONRD | 115 | 70504 |  | SBRAT 69 | 69 | 1 | BASE CASE | 24 | 25 | 104.2 | 104.2 | 0
70512-70719-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 50.2 | 100.4 | 100.5 | -0.1
70512-70719-1-LOSSMP3 | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | LOSSMP3 | 50 | 51.2 | 102.4 | 102.4 | 0
70512-70735-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70735 |  | WILL #2 | 34.5 | 1 | BASE CASE | 50 | 48.8 | 97.5 | 97.6 | -0.1
70521-70555-1-354LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 354LINE | 50 | 54 | 107.9 | 108.8 | -0.9
70521-70555-1-BASE CASE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | BASE CASE | 50 | 52.2 | 104.4 | 105.1 | -0.7
70557-70714-1-BASE CASE | 70557 | * | Q CITY | 115 | 70714 |  | Q CTY 34 | 34.5 | 1 | BASE CASE | 50 | 52.3 | 104.6 | 105.2 | -0.6
70712-70719-1-BASE CASE | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 48.6 | 96.1 | 96.2 | -0.1
70712-70719-1-LOSSMP3 | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | LOSSMP3 | 50 | 49.6 | 98.1 | 98 | 0.1
70721-70732-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70732 |  | MCNEIL T | 34.5 | 1 | BASE CASE | 30 | 29.8 | 102.2 | 101.6 | 0.6
70721-70740-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70740 |  | 10-20 | 13.8 | 1 | BASE CASE | 20 | 26.1 | 130.5 | 130.5 | 0
73106-73154-2-SGTN5TSTK | 73106 |  | SOUTHGTN | 345 | 73154 | * | SGTN B | 115 | 2 | SGTN5TSTK | 585 | 690.2 | 118 | #N/A | 23
73107-73116-1-BASE CASE | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | BASE CASE | 436 | 428.4 | 95.1 | 95.1 | 0
73144-73167-1-1440LINE | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440LINE | 252 | 255.2 | 98.8 | 98.8 | 0
73162-73163-1-SOUTHEND6T | 73162 |  | WATERSDE | 115 | 73163 | * | COS COB | 115 | 1 | SOUTHEND6T | 239 | 298.7 | 124.7 | 124.7 | 0
73162-73168-1-SOUTHEND6T | 73162 | * | WATERSDE | 115 | 73168 |  | GLNBROOK | 115 | 1 | SOUTHEND6T | 352 | 367 | 102.4 | 102.4 | 0
73170-73176-1-1165LINE | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | 1165LINE | 138 | 144.9 | 104.4 | 104.2 | 0.2
73188-73192-1-1272-1721DCT | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | 1272-1721DCT | 112 | 132.1 | 126.6 | 131.6 | -5
73188-73192-1-BUNKERH2T | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | BUNKERH2T | 112 | 110.7 | 103.6 | 107.2 | -3.6
73196-73198-1-8100-8200DCT | 73196 |  | GLEN JCT | 115 | 73198 | * | SOUTHGTN | 115 | 1 | 8100-8200DCT | 228 | 229.3 | 98.3 | #N/A | 3.3
73227-73633-1-SGTN7TSTK | 73227 | * | E.MERIDN | 115 | 73633 |  | NO.WALLF | 115 | 1 | SGTN7TSTK | 112 | 120 | 105.6 | 101 | 4.6
73651-73668-1-WOODMNT2TSTK | 73651 | * | NH HARBR | 22 | 73668 |  | E.SHORE | 115 | 1 | WOODMNT2TSTK | 475 | 452.6 | 95.3 | 100.6 | -5.3
73669-73681-1-WRIVER2TSTK | 73669 |  | GRAND AV | 115 | 73681 | * | WEST RIV | 115 | 1 | WRIVER2TSTK | 258 | 255 | 95.8 | #N/A | 0.8
73669-73681-2-WRIVER1TSTK | 73669 |  | GRAND AV | 115 | 73681 | * | WEST RIV | 115 | 2 | WRIVER1TSTK | 258 | 255 | 95.8 | #N/A | 0.8

## voltage
MONITORED VOLTAGE REPORT
Sort This Column for Lookup | SYSTEM |  | CONTINGENCY | BUS |  |  | V-CONT | V-INIT | V-MAX | V-MIN | Other Case | Diff
70622-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70622 | WHITE RV | 13.8 | 1.0534 | 1.0534 | 1.05 | 0.9 | 1.0528 | 0.0006
70625-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70625 | WTRFORD | 34.5 | 1.0585 | 1.0585 | 1.05 | 0.9 | 1.0581 | 0.0004
70626-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70626 | GILMAN | 34.5 | 1.0601 | 1.0601 | 1.05 | 0.9 | 1.0595 | 0.0006
70639-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70639 | HGATE VL | 46 | 1.0554 | 1.0554 | 1.05 | 0.9 | 1.0554 | 0
70640-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70640 | MISSQ P | 48 | 1.0554 | 1.0554 | 1.05 | 0.9 | 1.0554 | 0
70693-318-362STKBR | ZONE 41 | RANGE | 318-362STKBR | 70693 | ESX-STAT | 3.2 | 1.0657 | 1.0617 | 1.05 | 0.9 | 1.067 | -0.0013
70693-330+LAKE | ZONE 41 | RANGE | 330+LAKE | 70693 | ESX-STAT | 3.2 | 1.0695 | 1.0617 | 1.05 | 0.9 | 1.0715 | -0.002
70693-347+LAKE | ZONE 41 | RANGE | 347+LAKE | 70693 | ESX-STAT | 3.2 | 1.0695 | 1.0617 | 1.05 | 0.9 | 1.0715 | -0.002
70693-384LINE | ZONE 41 | RANGE | 384LINE | 70693 | ESX-STAT | 3.2 | 1.0649 | 1.0617 | 1.05 | 0.9 | 1.0657 | -0.0008
70693-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70693 | ESX-STAT | 3.2 | 1.0617 | 1.0617 | 1.05 | 0.9 | 1.0624 | -0.0007
70693-CARD1T+LAKE | ZONE 41 | RANGE | CARD1T+LAKE | 70693 | ESX-STAT | 3.2 | 1.0698 | 1.0617 | 1.05 | 0.9 | 1.0719 | -0.0021
70693-CARD3T+LAKE | ZONE 41 | RANGE | CARD3T+LAKE | 70693 | ESX-STAT | 3.2 | 1.0697 | 1.0617 | 1.05 | 0.9 | 1.0719 | -0.0022
70693-ESHORE12TSTK | ZONE 41 | RANGE | ESHORE12TSTK | 70693 | ESX-STAT | 3.2 | 1.065 | 1.0617 | 1.05 | 0.9 | 1.0659 | -0.0009
70693-LOLAKERD | ZONE 41 | RANGE | LOLAKERD | 70693 | ESX-STAT | 3.2 | 1.0644 | 1.0617 | 1.05 | 0.9 | 1.0654 | -0.001
70693-LOSSMID4 | ZONE 41 | RANGE | LOSSMID4 | 70693 | ESX-STAT | 3.2 | 1.0649 | 1.0617 | 1.05 | 0.9 | 1.0657 | -0.0008
70693-LOSSMON6 | ZONE 41 | RANGE | LOSSMON6 | 70693 | ESX-STAT | 3.2 | 1.0652 | 1.0617 | 1.05 | 0.9 | 1.066 | -0.0008
70693-LOSSMP2 | ZONE 41 | RANGE | LOSSMP2 | 70693 | ESX-STAT | 3.2 | 1.0704 | 1.0617 | 1.05 | 0.9 | 1.071 | -0.0006
70693-LOSSMP3 | ZONE 41 | RANGE | LOSSMP3 | 70693 | ESX-STAT | 3.2 | 1.0746 | 1.0617 | 1.05 | 0.9 | 1.0748 | -0.0002
70693-LOSSNHAV | ZONE 41 | RANGE | LOSSNHAV | 70693 | ESX-STAT | 3.2 | 1.0651 | 1.0617 | 1.05 | 0.9 | 1.0659 | -0.0008
73125-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73125 | MILFORD | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73129-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73129 | E.DEVONJ | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73151-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73151 | UNCASVLA | 115 | 1.0532 | 1.0193 | 1.05 | 0.9 | 1.0533 | -0.0001
73152-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73152 | UNCASVLB | 115 | 1.0534 | 1.0195 | 1.05 | 0.9 | 1.0535 | -0.0001
73210-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73210 | MONTVLLE | 115 | 1.0537 | 1.0197 | 1.05 | 0.9 | 1.0537 | 0
73267-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73267 | DARIEN | 115 | 1.0658 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0158
73278-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73278 | MONT DSL | 115 | 1.0537 | 1.0197 | 1.05 | 0.9 | 1.0537 | 0
73286-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73286 | COMPO | 115 | 1.0559 | 1.0412 | 1.05 | 0.9 | #N/A | 0.0059
73293-1565-PLNRDCT | '345KV ' | RANGE | 1565-PLNRDCT | 73293 | NORWALK | 345 | 1.05 | 1.0189 | 1.05 | 0.95 | #N/A | 0
73293-1565-PLNRDCT | ZONE 171 | RANGE | 1565-PLNRDCT | 73293 | NORWALK | 345 | 1.05 | 1.0189 | 1.05 | 0.9 | #N/A | 0
73293-PLUMNOR | '345KV ' | RANGE | PLUMNOR | 73293 | NORWALK | 345 | 1.05 | 1.0189 | 1.05 | 0.95 | #N/A | 0
73293-PLUMNOR | ZONE 171 | RANGE | PLUMNOR | 73293 | NORWALK | 345 | 1.05 | 1.0189 | 1.05 | 0.9 | #N/A | 0
73300-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73300 | ELYTAP | 115 | 1.0615 | 1.0396 | 1.05 | 0.9 | #N/A | 0.0115
73388-1721LINE | ZONE 171 | RANGE | 1721LINE | 73388 | SO.NAUG | 13.8 | 1.0529 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0029
73388-1770-321DCT | ZONE 171 | RANGE | 1770-321DCT | 73388 | SO.NAUG | 13.8 | 1.0521 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0021
73388-1887-321DCT | ZONE 171 | RANGE | 1887-321DCT | 73388 | SO.NAUG | 13.8 | 1.053 | 1.0557 | 1.05 | 0.9 | #N/A | 0.003
73388-329-352DCT | ZONE 171 | RANGE | 329-352DCT | 73388 | SO.NAUG | 13.8 | 1.0647 | 1.0557 | 1.05 | 0.9 | 1.0559 | 0.0088
73388-352+AUTO | ZONE 171 | RANGE | 352+AUTO | 73388 | SO.NAUG | 13.8 | 1.0648 | 1.0557 | 1.05 | 0.9 | 1.056 | 0.0088
73388-398LINE | ZONE 171 | RANGE | 398LINE | 73388 | SO.NAUG | 13.8 | 1.0583 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0083
73388-398LREAC | ZONE 171 | RANGE | 398LREAC | 73388 | SO.NAUG | 13.8 | 1.0583 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0083
73388-8100-8200DCT | ZONE 171 | RANGE | 8100-8200DCT | 73388 | SO.NAUG | 13.8 | 1.0514 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0014
73388-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73388 | SO.NAUG | 13.8 | 1.0557 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0057
73388-DC1-BES-NOR | ZONE 171 | RANGE | DC1-BES-NOR | 73388 | SO.NAUG | 13.8 | 1.0519 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0019
73388-LONGMT5TSTK | ZONE 171 | RANGE | LONGMT5TSTK | 73388 | SO.NAUG | 13.8 | 1.0588 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0088
73388-LOSSBPT3 | ZONE 171 | RANGE | LOSSBPT3 | 73388 | SO.NAUG | 13.8 | 1.0521 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0021
73388-PEQUON42TSTK | ZONE 171 | RANGE | PEQUON42TSTK | 73388 | SO.NAUG | 13.8 | 1.0513 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0013
73388-SCOVRK5TSTK | ZONE 171 | RANGE | SCOVRK5TSTK | 73388 | SO.NAUG | 13.8 | 1.0523 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0023
73388-SGTN5TSTK | ZONE 171 | RANGE | SGTN5TSTK | 73388 | SO.NAUG | 13.8 | 1.0522 | 1.0557 | 1.05 | 0.9 | #N/A | 0.0022
73448-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73448 | UNCASVIL | 27.6 | 1.051 | 1.0169 | 1.05 | 0.9 | 1.051 | 0
73574-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73574 | MILFD#1 | 13.8 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73575-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73575 | MILFD#2 | 13.8 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73620-MONTVSTBKR | ZONE 178 | RANGE | MONTVSTBKR | 73620 | BUDDGTNB | 34.5 | 1.0799 | 1.0448 | 1.05 | 0.9 | 1.0798 | 0.0001
73657-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73657 | ENGLISH7 | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73657-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73657 | ENGLISH7 | 13.8 | 1.0535 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0035
73657-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73657 | ENGLISH7 | 13.8 | 1.0531 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0031
73657-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73657 | ENGLISH7 | 13.8 | 1.0539 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0039
73657-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73657 | ENGLISH7 | 13.8 | 1.0533 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0033
73657-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73657 | ENGLISH7 | 13.8 | 1.0538 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0038
73657-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73657 | ENGLISH7 | 13.8 | 1.0521 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0021
73657-318LINE | ZONE 185 | RANGE | 318LINE | 73657 | ENGLISH7 | 13.8 | 1.0521 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0021
73657-321LINE | ZONE 185 | RANGE | 321LINE | 73657 | ENGLISH7 | 13.8 | 1.0536 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0036
73657-329-352DCT | ZONE 185 | RANGE | 329-352DCT | 73657 | ENGLISH7 | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73657-329LINE | ZONE 185 | RANGE | 329LINE | 73657 | ENGLISH7 | 13.8 | 1.0517 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0017
73657-330+LAKE | ZONE 185 | RANGE | 330+LAKE | 73657 | ENGLISH7 | 13.8 | 1.0607 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0107
73657-347+LAKE | ZONE 185 | RANGE | 347+LAKE | 73657 | ENGLISH7 | 13.8 | 1.0607 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0107
73657-348LINE | ZONE 185 | RANGE | 348LINE | 73657 | ENGLISH7 | 13.8 | 1.053 | 1.0569 | 1.05 | 0.9 | #N/A | 0.003
73657-352+AUTO | ZONE 185 | RANGE | 352+AUTO | 73657 | ENGLISH7 | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73657-354LINE | ZONE 185 | RANGE | 354LINE | 73657 | ENGLISH7 | 13.8 | 1.0595 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0095
73657-84004LINE | ZONE 185 | RANGE | 84004LINE | 73657 | ENGLISH7 | 13.8 | 1.0617 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0117
73657-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73657 | ENGLISH7 | 13.8 | 1.0523 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0023
73657-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73657 | ENGLISH7 | 13.8 | 1.0522 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0022
73657-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0509 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0009
73657-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0509 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0009
73657-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73657 | ENGLISH7 | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73657-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73657 | ENGLISH7 | 13.8 | 1.0569 | 1.0569 | 1.05 | 0.9 | 1.0505 | 0.0064
73657-CARD1T+LAKE | ZONE 185 | RANGE | CARD1T+LAKE | 73657 | ENGLISH7 | 13.8 | 1.0606 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0106
73657-CARD3T+LAKE | ZONE 185 | RANGE | CARD3T+LAKE | 73657 | ENGLISH7 | 13.8 | 1.0606 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0106
73657-DC1-BES-NOR | ZONE 185 | RANGE | DC1-BES-NOR | 73657 | ENGLISH7 | 13.8 | 1.0532 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0032
73657-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73657 | ENGLISH7 | 13.8 | 1.0511 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0011
73657-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0514 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0014
73657-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73657 | ENGLISH7 | 13.8 | 1.0513 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0013
73657-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0501 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0001
73657-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73657 | ENGLISH7 | 13.8 | 1.0516 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0016
73657-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73657 | ENGLISH7 | 13.8 | 1.0517 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0017
73657-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73657 | ENGLISH7 | 13.8 | 1.0515 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0015
73657-LOSSMP2 | ZONE 185 | RANGE | LOSSMP2 | 73657 | ENGLISH7 | 13.8 | 1.0607 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0107
73657-LOSSMP3 | ZONE 185 | RANGE | LOSSMP3 | 73657 | ENGLISH7 | 13.8 | 1.0616 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0116
73657-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73657 | ENGLISH7 | 13.8 | 1.0509 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0009
73657-LUDLOWSTBKR | ZONE 185 | RANGE | LUDLOWSTBKR | 73657 | ENGLISH7 | 13.8 | 1.0594 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0094
73657-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73657 | ENGLISH7 | 13.8 | 1.0513 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0013
73657-SGTN3TSTK | ZONE 185 | RANGE | SGTN3TSTK | 73657 | ENGLISH7 | 13.8 | 1.052 | 1.0569 | 1.05 | 0.9 | #N/A | 0.002
73657-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0517 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0017
73657-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73657 | ENGLISH7 | 13.8 | 1.0516 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0016
73657-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73657 | ENGLISH7 | 13.8 | 1.0536 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0036
73657-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0511 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0011
73657-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0511 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0011
73658-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73658 | ENGLISH8 | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73658-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73658 | ENGLISH8 | 13.8 | 1.0535 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0035
73658-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73658 | ENGLISH8 | 13.8 | 1.0531 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0031
73658-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73658 | ENGLISH8 | 13.8 | 1.0539 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0039
73658-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73658 | ENGLISH8 | 13.8 | 1.0533 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0033
73658-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73658 | ENGLISH8 | 13.8 | 1.0538 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0038
73658-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73658 | ENGLISH8 | 13.8 | 1.0521 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0021
73658-318LINE | ZONE 185 | RANGE | 318LINE | 73658 | ENGLISH8 | 13.8 | 1.0521 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0021
73658-321LINE | ZONE 185 | RANGE | 321LINE | 73658 | ENGLISH8 | 13.8 | 1.0536 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0036
73658-329-352DCT | ZONE 185 | RANGE | 329-352DCT | 73658 | ENGLISH8 | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73658-329LINE | ZONE 185 | RANGE | 329LINE | 73658 | ENGLISH8 | 13.8 | 1.0517 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0017
73658-330+LAKE | ZONE 185 | RANGE | 330+LAKE | 73658 | ENGLISH8 | 13.8 | 1.0607 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0107
73658-347+LAKE | ZONE 185 | RANGE | 347+LAKE | 73658 | ENGLISH8 | 13.8 | 1.0607 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0107
73658-348LINE | ZONE 185 | RANGE | 348LINE | 73658 | ENGLISH8 | 13.8 | 1.053 | 1.0569 | 1.05 | 0.9 | #N/A | 0.003
73658-352+AUTO | ZONE 185 | RANGE | 352+AUTO | 73658 | ENGLISH8 | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73658-354LINE | ZONE 185 | RANGE | 354LINE | 73658 | ENGLISH8 | 13.8 | 1.0595 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0095
73658-84004LINE | ZONE 185 | RANGE | 84004LINE | 73658 | ENGLISH8 | 13.8 | 1.0617 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0117
73658-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73658 | ENGLISH8 | 13.8 | 1.0523 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0023
73658-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73658 | ENGLISH8 | 13.8 | 1.0522 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0022
73658-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0509 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0009
73658-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0509 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0009
73658-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73658 | ENGLISH8 | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73658-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73658 | ENGLISH8 | 13.8 | 1.0569 | 1.0569 | 1.05 | 0.9 | 1.0505 | 0.0064
73658-CARD1T+LAKE | ZONE 185 | RANGE | CARD1T+LAKE | 73658 | ENGLISH8 | 13.8 | 1.0606 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0106
73658-CARD3T+LAKE | ZONE 185 | RANGE | CARD3T+LAKE | 73658 | ENGLISH8 | 13.8 | 1.0606 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0106
73658-DC1-BES-NOR | ZONE 185 | RANGE | DC1-BES-NOR | 73658 | ENGLISH8 | 13.8 | 1.0532 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0032
73658-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73658 | ENGLISH8 | 13.8 | 1.0511 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0011
73658-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0514 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0014
73658-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73658 | ENGLISH8 | 13.8 | 1.0513 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0013
73658-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0501 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0001
73658-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73658 | ENGLISH8 | 13.8 | 1.0516 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0016
73658-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73658 | ENGLISH8 | 13.8 | 1.0517 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0017
73658-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73658 | ENGLISH8 | 13.8 | 1.0515 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0015
73658-LOSSMP2 | ZONE 185 | RANGE | LOSSMP2 | 73658 | ENGLISH8 | 13.8 | 1.0607 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0107
73658-LOSSMP3 | ZONE 185 | RANGE | LOSSMP3 | 73658 | ENGLISH8 | 13.8 | 1.0616 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0116
73658-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73658 | ENGLISH8 | 13.8 | 1.0509 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0009
73658-LUDLOWSTBKR | ZONE 185 | RANGE | LUDLOWSTBKR | 73658 | ENGLISH8 | 13.8 | 1.0594 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0094
73658-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73658 | ENGLISH8 | 13.8 | 1.0513 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0013
73658-SGTN3TSTK | ZONE 185 | RANGE | SGTN3TSTK | 73658 | ENGLISH8 | 13.8 | 1.052 | 1.0569 | 1.05 | 0.9 | #N/A | 0.002
73658-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0517 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0017
73658-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73658 | ENGLISH8 | 13.8 | 1.0516 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0016
73658-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73658 | ENGLISH8 | 13.8 | 1.0536 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0036
73658-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0511 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0011
73658-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0511 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0011
73665-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73665 | NHHHVDCL | 192 | 1.0533 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0033
73665-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73665 | NHHHVDCL | 192 | 1.0559 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0059
73665-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73665 | NHHHVDCL | 192 | 1.0548 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0048
73665-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73665 | NHHHVDCL | 192 | 1.0556 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0056
73665-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73665 | NHHHVDCL | 192 | 1.055 | 1.0587 | 1.05 | 0.9 | #N/A | 0.005
73665-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73665 | NHHHVDCL | 192 | 1.0539 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0039
73665-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73665 | NHHHVDCL | 192 | 1.0515 | 1.0587 | 1.05 | 0.9 | 1.0534 | -0.0019
73665-318LINE | ZONE 185 | RANGE | 318LINE | 73665 | NHHHVDCL | 192 | 1.0521 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0021
73665-321LINE | ZONE 185 | RANGE | 321LINE | 73665 | NHHHVDCL | 192 | 1.0552 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0052
73665-329-352DCT | ZONE 185 | RANGE | 329-352DCT | 73665 | NHHHVDCL | 192 | 1.0536 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0036
73665-329LINE | ZONE 185 | RANGE | 329LINE | 73665 | NHHHVDCL | 192 | 1.0534 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0034
73665-330+LAKE | ZONE 185 | RANGE | 330+LAKE | 73665 | NHHHVDCL | 192 | 1.0627 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0127
73665-347+LAKE | ZONE 185 | RANGE | 347+LAKE | 73665 | NHHHVDCL | 192 | 1.0627 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0127
73665-348LINE | ZONE 185 | RANGE | 348LINE | 73665 | NHHHVDCL | 192 | 1.0533 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0033
73665-352+AUTO | ZONE 185 | RANGE | 352+AUTO | 73665 | NHHHVDCL | 192 | 1.0536 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0036
73665-354LINE | ZONE 185 | RANGE | 354LINE | 73665 | NHHHVDCL | 192 | 1.0615 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0115
73665-384LINE | ZONE 185 | RANGE | 384LINE | 73665 | NHHHVDCL | 192 | 1.0555 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0055
73665-84004LINE | ZONE 185 | RANGE | 84004LINE | 73665 | NHHHVDCL | 192 | 1.0622 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0122
73665-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73665 | NHHHVDCL | 192 | 1.0558 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0058
73665-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73665 | NHHHVDCL | 192 | 1.0558 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0058
73665-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73665 | NHHHVDCL | 192 | 1.0558 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0058
73665-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73665 | NHHHVDCL | 192 | 1.0587 | 1.0587 | 1.05 | 0.9 | 1.0566 | 0.0021
73665-CARD1T+LAKE | ZONE 185 | RANGE | CARD1T+LAKE | 73665 | NHHHVDCL | 192 | 1.0627 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0127
73665-CARD3T+LAKE | ZONE 185 | RANGE | CARD3T+LAKE | 73665 | NHHHVDCL | 192 | 1.0627 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0127
73665-DC1-BES-NOR | ZONE 185 | RANGE | DC1-BES-NOR | 73665 | NHHHVDCL | 192 | 1.0548 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0048
73665-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73665 | NHHHVDCL | 192 | 1.0522 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0022
73665-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73665 | NHHHVDCL | 192 | 1.0538 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0038
73665-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73665 | NHHHVDCL | 192 | 1.0536 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0036
73665-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73665 | NHHHVDCL | 192 | 1.0536 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0036
73665-LOSSMID4 | ZONE 185 | RANGE | LOSSMID4 | 73665 | NHHHVDCL | 192 | 1.0556 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0056
73665-LOSSMP2 | ZONE 185 | RANGE | LOSSMP2 | 73665 | NHHHVDCL | 192 | 1.0627 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0127
73665-LOSSMP3 | ZONE 185 | RANGE | LOSSMP3 | 73665 | NHHHVDCL | 192 | 1.0636 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0136
73665-LUDLOWSTBKR | ZONE 185 | RANGE | LUDLOWSTBKR | 73665 | NHHHVDCL | 192 | 1.0613 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0113
73665-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73665 | NHHHVDCL | 192 | 1.0537 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0037
73665-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73665 | NHHHVDCL | 192 | 1.056 | 1.0587 | 1.05 | 0.9 | #N/A | 0.006
73665-SGTN3TSTK | ZONE 185 | RANGE | SGTN3TSTK | 73665 | NHHHVDCL | 192 | 1.0518 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0018
73665-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73665 | NHHHVDCL | 192 | 1.0505 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0005
73665-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73665 | NHHHVDCL | 192 | 1.0528 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0028
73665-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73665 | NHHHVDCL | 192 | 1.0531 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0031
73665-SOTHNGTN12T | ZONE 185 | RANGE | SOTHNGTN12T | 73665 | NHHHVDCL | 192 | 1.0557 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0057
73665-WOODMNT2TSTK | ZONE 185 | RANGE | WOODMNT2TSTK | 73665 | NHHHVDCL | 192 | 1.0558 | 1.0587 | 1.05 | 0.9 | #N/A | 0.0058
73665-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73665 | NHHHVDCL | 192 | 1.056 | 1.0587 | 1.05 | 0.9 | #N/A | 0.006
73665-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73665 | NHHHVDCL | 192 | 1.056 | 1.0587 | 1.05 | 0.9 | #N/A | 0.006
73672-84004LINE | ZONE 185 | RANGE | 84004LINE | 73672 | SACKETT | 115 | 1.0519 | 1.0406 | 1.05 | 0.9 | #N/A | 0.0019
73700-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73700 | PEQUONIC | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73702-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73702 | CRRA XFO | 115 | 1.0501 | 1.0501 | 1.05 | 0.9 | #N/A | 0.0001
73716-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73716 | PEQBETAP | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73729-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73729 | ENGLISH | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73729-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73729 | ENGLISH | 13.8 | 1.0535 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0035
73729-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73729 | ENGLISH | 13.8 | 1.0531 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0031
73729-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73729 | ENGLISH | 13.8 | 1.0539 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0039
73729-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73729 | ENGLISH | 13.8 | 1.0533 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0033
73729-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73729 | ENGLISH | 13.8 | 1.0538 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0038
73729-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73729 | ENGLISH | 13.8 | 1.0521 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0021
73729-318LINE | ZONE 185 | RANGE | 318LINE | 73729 | ENGLISH | 13.8 | 1.0521 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0021
73729-321LINE | ZONE 185 | RANGE | 321LINE | 73729 | ENGLISH | 13.8 | 1.0536 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0036
73729-329-352DCT | ZONE 185 | RANGE | 329-352DCT | 73729 | ENGLISH | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73729-329LINE | ZONE 185 | RANGE | 329LINE | 73729 | ENGLISH | 13.8 | 1.0517 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0017
73729-330+LAKE | ZONE 185 | RANGE | 330+LAKE | 73729 | ENGLISH | 13.8 | 1.0607 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0107
73729-347+LAKE | ZONE 185 | RANGE | 347+LAKE | 73729 | ENGLISH | 13.8 | 1.0607 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0107
73729-348LINE | ZONE 185 | RANGE | 348LINE | 73729 | ENGLISH | 13.8 | 1.053 | 1.0569 | 1.05 | 0.9 | #N/A | 0.003
73729-352+AUTO | ZONE 185 | RANGE | 352+AUTO | 73729 | ENGLISH | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73729-354LINE | ZONE 185 | RANGE | 354LINE | 73729 | ENGLISH | 13.8 | 1.0595 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0095
73729-84004LINE | ZONE 185 | RANGE | 84004LINE | 73729 | ENGLISH | 13.8 | 1.0617 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0117
73729-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73729 | ENGLISH | 13.8 | 1.0523 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0023
73729-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73729 | ENGLISH | 13.8 | 1.0522 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0022
73729-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73729 | ENGLISH | 13.8 | 1.0509 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0009
73729-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73729 | ENGLISH | 13.8 | 1.0509 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0009
73729-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73729 | ENGLISH | 13.8 | 1.0518 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0018
73729-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73729 | ENGLISH | 13.8 | 1.0569 | 1.0569 | 1.05 | 0.9 | 1.0505 | 0.0064
73729-CARD1T+LAKE | ZONE 185 | RANGE | CARD1T+LAKE | 73729 | ENGLISH | 13.8 | 1.0606 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0106
73729-CARD3T+LAKE | ZONE 185 | RANGE | CARD3T+LAKE | 73729 | ENGLISH | 13.8 | 1.0606 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0106
73729-DC1-BES-NOR | ZONE 185 | RANGE | DC1-BES-NOR | 73729 | ENGLISH | 13.8 | 1.0532 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0032
73729-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73729 | ENGLISH | 13.8 | 1.0511 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0011
73729-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73729 | ENGLISH | 13.8 | 1.0514 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0014
73729-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73729 | ENGLISH | 13.8 | 1.0513 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0013
73729-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73729 | ENGLISH | 13.8 | 1.0501 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0001
73729-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73729 | ENGLISH | 13.8 | 1.0516 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0016
73729-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73729 | ENGLISH | 13.8 | 1.0517 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0017
73729-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73729 | ENGLISH | 13.8 | 1.0515 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0015
73729-LOSSMP2 | ZONE 185 | RANGE | LOSSMP2 | 73729 | ENGLISH | 13.8 | 1.0607 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0107
73729-LOSSMP3 | ZONE 185 | RANGE | LOSSMP3 | 73729 | ENGLISH | 13.8 | 1.0616 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0116
73729-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73729 | ENGLISH | 13.8 | 1.0509 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0009
73729-LUDLOWSTBKR | ZONE 185 | RANGE | LUDLOWSTBKR | 73729 | ENGLISH | 13.8 | 1.0594 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0094
73729-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73729 | ENGLISH | 13.8 | 1.0513 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0013
73729-SGTN3TSTK | ZONE 185 | RANGE | SGTN3TSTK | 73729 | ENGLISH | 13.8 | 1.052 | 1.0569 | 1.05 | 0.9 | #N/A | 0.002
73729-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73729 | ENGLISH | 13.8 | 1.0517 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0017
73729-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73729 | ENGLISH | 13.8 | 1.0516 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0016
73729-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73729 | ENGLISH | 13.8 | 1.0536 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0036
73729-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73729 | ENGLISH | 13.8 | 1.0511 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0011
73729-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73729 | ENGLISH | 13.8 | 1.0511 | 1.0569 | 1.05 | 0.9 | #N/A | 0.0011
73746-WOODMNT2TSTK | ZONE 186 | RANGE | WOODMNT2TSTK | 73746 | WOODMONT | 13.8 | 0.4284 | 1.0304 | 1.05 | 0.9 | 0.4265 | 0.0019

## contingencies
CONTINGENCY LEGEND
LABEL EVENTS
689LINE : OPEN LINE FROM BUS 73346 [TORRGTN 69.000] TO BUS 73336 [FALLS V 69.000] CKT 1
693LINE : OPEN LINE FROM BUS 73346 [TORRGTN 69.000] TO BUS 73336 [FALLS V 69.000] CKT 2
1100LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
1130LINE : OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1165LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
1191LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
1200LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
1206LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73600 [CONN YAN115.00] CKT 1
1222LINE : OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 1
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 2
1270LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
1310LINE : OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73221 [S.WNDSRB115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73283 [SWINDT13115.00] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73221 [S.WNDSRB115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
ONE1385 : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
1385LN+AUTO : OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 2
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 3
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1389LINE : OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1394LINE : OPEN LINE FROM BUS 73266 [SCITICO 115.00] TO BUS 72978 [FRANCONA115.00] CKT 1
1416LINE : OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1430LINE : OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
1440LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
1450LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
1466LINE : OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
1515LINE : OPEN LINE FROM BUS 72972 [LUDLOW 115.00] TO BUS 73266 [SCITICO 115.00] CKT 1
1594LINE : OPEN LINE FROM BUS 73705 [IND.WELL115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
1618LINE : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
1620NLINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73241 [MIDDLTWN115.00] CKT 1
1637LINE : OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
1640LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1655LINE : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
1668LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1710LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
1721LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1730ALINE : OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1730BLINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1730CLINE : OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1740LINE : OPEN LINE FROM BUS 73162 [WATERSDE115.00] TO BUS 73163 [COS COB 115.00] CKT 1
1753LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
1756LINE : OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
1767LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73259 [HOPEWELL115.00] CKT 1
1772LINE : OPEN LINE FROM BUS 73600 [CONN YAN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1779LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1780LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
1785LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73254 [NEWINGTN115.00] CKT 1
1788LINE : OPEN LINE FROM BUS 73245 [TORR TER115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
1790LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
1792LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
1825LINE : OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1830LINE : OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1867LINE : OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
1900LINE : OPEN LINE FROM BUS 73203 [CAMPV PH115.00] TO BUS 73245 [TORR TER115.00] CKT 1
1910LINE : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
1921LINE : OPEN LINE FROM BUS 73203 [CAMPV PH115.00] TO BUS 73240 [THOMASTN115.00] CKT 1
1975LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
8500LINE : OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
8600LINE : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
8700LINE : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
8809ALINE-2 : OPEN LINE FROM BUS 73694 [BAIRD A 115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
8909BLINE-2 : OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
9500LINE : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
84004LINE : OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
88003ALINE : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
88003ALINE-1: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
89003BLINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
89003BLINE-1: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
91001LINE : OPEN LINE FROM BUS 73701 [CRRA JCT115.00] TO BUS 73702 [CRRA XFO115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
318LINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
321LINE : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
329LINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
330LINE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
330+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73566 [LAKERD#221.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73567 [LAKERD#321.000] CKT 1
347+LAKE : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73566 [LAKERD#221.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73567 [LAKERD#321.000] CKT 1
348LINE : OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
352+AUTO : OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73105 [LONG MTN345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73202 [FROST BR115.00] CKT 1
354LINE : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
364+AUTO : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
371+AUTO : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
384LINE : OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
395LINE : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
395+AUTO : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
398LINE : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
398LREAC : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
PLUMNOR : OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73133 [PLUMUG 345.00] CKT 2
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73134 [NORUG 345.00] CKT 3
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 2
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 3
OPEN LINE FROM BUS 73135 [NOROH 345.00] TO BUS 73293 [NORWALK 345.00] CKT 3
1000-1090DCT: OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
OPEN LINE FROM BUS 73611 [DUDLEY T115.00] TO BUS 73612 [BEAN HLL115.00] CKT 1
OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
113091001DCT: OPEN LINE FROM BUS 73701 [CRRA JCT115.00] TO BUS 73702 [CRRA XFO115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1261-1620SDC: OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
1272-1721DCT: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1545-1570DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
1710-1730ADC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1710-1730BDC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1710-1730CDC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1720-1730ADC: OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1867-1880DCT: OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
1867-1890DCT: OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
1880-1890DCT: OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
8100-8200DCT: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
1565-PLNRDCT: OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73133 [PLUMUG 345.00] CKT 2
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73134 [NORUG 345.00] CKT 3
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 2
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 3
OPEN LINE FROM BUS 73135 [NOROH 345.00] TO BUS 73293 [NORWALK 345.00] CKT 3
1618-321DCT : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
1751-395DCT : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
1770-321DCT : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
1779-395DCT : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
1887-321DCT : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
1975-348DCT : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
310-348WDCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
329-352DCT : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73106 [SOUTHGTN345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73202 [FROST BR115.00] CKT 1
362W-376DCT : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
NORAUT : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73293 [NORWALK 345.00] CKT 1
SOUTH1XAUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOUTH2XAUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
LOSSBPT3 : OPEN LINE FROM BUS 73648 [BPTHBR#322.000] TO BUS 73700 [PEQUONIC115.00] CKT 1
LOSSDEV7 : OPEN LINE FROM BUS 73553 [DEVON#7 13.800] TO BUS 73195 [DEVON 115.00] CKT 1
LOLAKERD : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
LOSSMID4 : OPEN LINE FROM BUS 73557 [MIDDTN#422.000] TO BUS 73116 [MIDDLTWN345.00] CKT 1
LOSSMP2 : OPEN LINE FROM BUS 73562 [MILL#2 24.000] TO BUS 73110 [MILLSTNE345.00] CKT 1
LOSSMP3 : OPEN LINE FROM BUS 73563 [MILL#3 24.000] TO BUS 73110 [MILLSTNE345.00] CKT 1
LOSSMON6 : OPEN LINE FROM BUS 73559 [MONTV#6 22.000] TO BUS 73210 [MONTVLLE115.00] CKT 1
LOSSNHAV : OPEN LINE FROM BUS 73651 [NH HARBR22.000] TO BUS 73668 [E.SHORE 115.00] CKT 1
LOSSNOR1 : OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
LOSSNOR2 : OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
ALLINGS1TSTK: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
ALLINGS2TSTK: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73685 [ALLINGSB115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
BAIRDBSTK : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73697 [CONGRESS115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73755 [CONGRES213.800] CKT 1
BUNKERH2T : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
DEVON1TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
DEVON2TSTK : OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73125 [MILFORD 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
DEVON3TSTK : OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73125 [MILFORD 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73570 [DEVGAS1113.800] CKT 1
DEVON6TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
DEVON8TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73573 [DEVGAS1413.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
DEVON10TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73571 [DEVGAS1213.800] CKT 1
DEVON12TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73570 [DEVGAS1113.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73572 [DEVGAS1313.800] CKT 1
DEVON23TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73553 [DEVON#7 13.800] CKT 1
DEVON25TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73554 [DEVON#8 13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
ESHORE12TSTK: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73651 [NH HARBR22.000] CKT 1
GRNDAV4TSTK : OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
GRNDAV5TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
GRNDAV6TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
GRNDAV7TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
NORWLKHAR1T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR2T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR3T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR4T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR7T : OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
PEQUON22TSTK: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73696 [CONGRESS115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
PEQUON32TSTK: OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73647 [BPTHBR#220.000] CKT 1
PEQUON42TSTK: OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73697 [CONGRESS115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73648 [BPTHBR#322.000] CKT 1
SOUTHEND6T : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
SOTHNGTN12T : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
WALLING3TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73595 [WALL LV213.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73596 [WALL LV313.800] CKT 1
WATERST2TSTK: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
WRIVER1TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
WRIVER2TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
WOODMNT2TSTK: OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73746 [WOODMONT13.800] CKT 1
OPEN LINE FROM BUS 73685 [ALLINGSB115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
318-362STKBR: OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73588 [MERIDEN121.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73589 [MERIDEN221.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73590 [MERIDEN321.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73106 [SOUTHGTN345.00] CKT 1
CARD1TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
CARD1T+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73565 [LAKERD#121.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73566 [LAKERD#221.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73567 [LAKERD#321.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
CARD2TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
CARD3TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
CARD3T+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73565 [LAKERD#121.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73566 [LAKERD#221.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73567 [LAKERD#321.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
HADNKSTBKR : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73109 [MONTVILE345.00] CKT 1
LONGMT5TSTK : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
LUDLOWSTBKR : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72929 [BELCH301345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
OPEN LINE FROM BUS 72929 [BELCH301345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
OPEN LINE FROM BUS 71797 [MILLBURY345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
MANCH21TSTK : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
MONTVSTBKR : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 2
SCOVRK5TSTK : OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73664 [NHHHVDCL345.00] TO BUS 73665 [NHHHVDCL191.50] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK8TSTK : OPEN LINE FROM BUS 73107 [SCOVL RK345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SGTN3TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SGTN4TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
SGTN5TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
SGTN6TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
SGTN7TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
NORGLENLINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
NHBRGLENLINE: OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR1T : OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
NORWLKHAR2T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR3T : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 2
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 3
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR4T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR7T : OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHARBT : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 2
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 3
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
GLNBRKA4STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
GLNBRKBSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
GLNBRKB3STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
GLNBRKB4STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
GLNBRKESTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
DC1-BES-NOR : REMOVE MACHINE 1 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 1 FROM BUS 73293 [NORWALK 345.00]
DC3-BES-DEV : REMOVE MACHINE 3 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 3 FROM BUS 73129 [E.DEVONJ115.00]
DC4-SIN-NOR : REMOVE MACHINE 4 FROM BUS 73700 [PEQUONIC115.00]
REMOVE MACHINE 4 FROM BUS 73293 [NORWALK 345.00]

## nonconverged
ACCC NON-CONVERGED NETWORK REPORT:
BUS MISMATCH TOLERANCE= 2.5000 MVA
SYSTEM MISMATCH TOLERANCE= 20.0000 MVA
DISTRIBUTION FACTOR FILE: C:\Projects\10934 NE Utilities DC\DC Light\PSSE Files\Case 3.dfx
SUBSYSTEM DESCRIPTION FILE: C:\Projects\10934 NE Utilities DC\DC Light\PSSE Files\swctnew.sub
MONITORED ELEMENT FILE: C:\Projects\10934 NE Utilities DC\DC Light\PSSE Files\swct0802.mon
CONTINGENCY DESCRIPTION FILE: C:\Projects\10934 NE Utilities DC\DC Light\PSSE Files\contigphase2-091503-kleen-newDC.con
X--MISMATCH (MVA)--X
CONTINGENCY BUS SYSTEM TERMINATION CONDITION
100LINE 2.3249 21.434 MET CONVERGENCE TOLERANCE
100+400LINES 2.1383 50.361 MET CONVERGENCE TOLERANCE
400LINE 2.1456 31.045 MET CONVERGENCE TOLERANCE
500LINE 1.6494 58.638 MET CONVERGENCE TOLERANCE
667-690LINE 2.3028 28.686 MET CONVERGENCE TOLERANCE
694LINE 2.2990 37.764 MET CONVERGENCE TOLERANCE
1000LINE 2.3167 28.571 MET CONVERGENCE TOLERANCE
1050LINE 2.3267 35.915 MET CONVERGENCE TOLERANCE
1050+1766LNS 2.2999 26.271 MET CONVERGENCE TOLERANCE
1060LINE 2.3233 24.870 MET CONVERGENCE TOLERANCE
1070LINE 2.1525 26.339 MET CONVERGENCE TOLERANCE
1070+1490LNS 2.1406 50.046 MET CONVERGENCE TOLERANCE
1080LINE 2.3346 35.211 MET CONVERGENCE TOLERANCE
1090LINE 2.1525 25.850 MET CONVERGENCE TOLERANCE
1130+1416LNS 2.1362 59.347 MET CONVERGENCE TOLERANCE
1163LINE 2.3072 23.647 MET CONVERGENCE TOLERANCE
1163+1910LNS 2.2859 50.233 MET CONVERGENCE TOLERANCE
1207LINE 2.2721 34.126 MET CONVERGENCE TOLERANCE
1208LINE 2.2713 35.143 MET CONVERGENCE TOLERANCE
1235LINE 2.1406 44.807 MET CONVERGENCE TOLERANCE
1238LINE 2.2713 25.024 MET CONVERGENCE TOLERANCE
1238+1813LNS 2.1465 30.765 MET CONVERGENCE TOLERANCE
1250LINE 2.1456 32.100 MET CONVERGENCE TOLERANCE
1261LINE 2.2714 22.047 MET CONVERGENCE TOLERANCE
1272LINE 2.2713 21.275 MET CONVERGENCE TOLERANCE
1272+1445LNS 2.2575 51.611 MET CONVERGENCE TOLERANCE
1280LINE 2.3305 32.856 MET CONVERGENCE TOLERANCE
1300LINE 2.2868 60.569 MET CONVERGENCE TOLERANCE
1337LINE 2.3233 24.961 MET CONVERGENCE TOLERANCE
1342LINE 2.3001 39.985 MET CONVERGENCE TOLERANCE
1355LINE 2.2609 82.718 MET CONVERGENCE TOLERANCE
1410LINE 2.1527 22.429 MET CONVERGENCE TOLERANCE
1443LINE 2.3250 31.755 MET CONVERGENCE TOLERANCE
1443+1759LNS 2.2554 66.012 MET CONVERGENCE TOLERANCE
1445LINE 2.2715 24.940 MET CONVERGENCE TOLERANCE
1460LINE 2.3001 23.753 MET CONVERGENCE TOLERANCE
1470LINE 2.3258 20.950 MET CONVERGENCE TOLERANCE
1490LINE 2.1525 21.550 MET CONVERGENCE TOLERANCE
1500LINE 2.2546 33.002 MET CONVERGENCE TOLERANCE
1505LINE 2.2964 23.090 MET CONVERGENCE TOLERANCE
1508LINE 2.2999 32.747 MET CONVERGENCE TOLERANCE
1537LINE 2.3003 22.608 MET CONVERGENCE TOLERANCE
1545LINE 2.3261 26.684 MET CONVERGENCE TOLERANCE
1545+SPS 2.3274 26.506 MET CONVERGENCE TOLERANCE
1550LINE 2.3000 24.494 MET CONVERGENCE TOLERANCE
1550+1950LNS 2.2960 42.144 MET CONVERGENCE TOLERANCE
1560LINE 2.2711 26.879 MET CONVERGENCE TOLERANCE
1565LINE 2.3073 27.519 MET CONVERGENCE TOLERANCE
1570LINE 2.3002 27.726 MET CONVERGENCE TOLERANCE
1572LINE 2.1527 20.309 MET CONVERGENCE TOLERANCE
1572+1772LNS 2.1480 24.853 MET CONVERGENCE TOLERANCE
1575LINE 2.2589 48.136 MET CONVERGENCE TOLERANCE
1580LINE 2.2710 20.532 MET CONVERGENCE TOLERANCE
1585LINE 2.2167 26.831 MET CONVERGENCE TOLERANCE
1588LINE 2.3982 24.565 MET CONVERGENCE TOLERANCE
1605LINE 2.2547 32.959 MET CONVERGENCE TOLERANCE
1607LINE 2.3168 21.657 MET CONVERGENCE TOLERANCE
1610LINE 2.2709 33.440 MET CONVERGENCE TOLERANCE
1620SLINE 2.2715 22.464 MET CONVERGENCE TOLERANCE
1622LINE 2.2844 56.050 MET CONVERGENCE TOLERANCE
1625LINE 2.4751 26.952 MET CONVERGENCE TOLERANCE
1630LINE 2.3000 22.052 MET CONVERGENCE TOLERANCE
1670LINE 2.3001 23.484 MET CONVERGENCE TOLERANCE
1675LINE 2.3258 23.477 MET CONVERGENCE TOLERANCE
1685LINE 2.2709 22.926 MET CONVERGENCE TOLERANCE
1690LINE 2.1306 72.434 MET CONVERGENCE TOLERANCE
1704LINE 2.2711 27.139 MET CONVERGENCE TOLERANCE
1720LINE 2.3001 22.308 MET CONVERGENCE TOLERANCE
1722LINE 2.3456 33.483 MET CONVERGENCE TOLERANCE
1726LINE 2.3155 27.783 MET CONVERGENCE TOLERANCE
1732LINE 2.1523 32.021 MET CONVERGENCE TOLERANCE
1750LINE 2.1380 52.357 MET CONVERGENCE TOLERANCE
1751LINE 2.1528 20.767 MET CONVERGENCE TOLERANCE
1752LINE 2.3154 25.258 MET CONVERGENCE TOLERANCE
1759LINE 2.2838 20.416 MET CONVERGENCE TOLERANCE
1760LINE 2.2713 20.960 MET CONVERGENCE TOLERANCE
1760+1876LNS 2.1317 71.501 MET CONVERGENCE TOLERANCE
1763LINE 2.4825 30.705 MET CONVERGENCE TOLERANCE
1765LINE 2.2710 23.367 MET CONVERGENCE TOLERANCE
1766LINE 2.4084 48.877 MET CONVERGENCE TOLERANCE
1769LINE 2.3002 22.933 MET CONVERGENCE TOLERANCE
1770LINE 2.3082 39.071 MET CONVERGENCE TOLERANCE
1771LINE 2.2712 24.644 MET CONVERGENCE TOLERANCE
1773LINE 2.3008 41.039 MET CONVERGENCE TOLERANCE
1775LINE 2.2717 30.096 MET CONVERGENCE TOLERANCE
1777LINE 2.2714 30.520 MET CONVERGENCE TOLERANCE
1783LINE 2.3003 26.626 MET CONVERGENCE TOLERANCE
1784LINE 2.3045 25.173 MET CONVERGENCE TOLERANCE
1786LINE 2.1527 24.077 MET CONVERGENCE TOLERANCE
1800-1860LNS 2.3216 24.940 MET CONVERGENCE TOLERANCE
1810LINE 2.3217 22.436 MET CONVERGENCE TOLERANCE
1813LINE 2.1017 36.912 MET CONVERGENCE TOLERANCE
1820LINE 2.1351 64.455 MET CONVERGENCE TOLERANCE
1821LINE 2.1524 27.850 MET CONVERGENCE TOLERANCE
1835LINE 2.1018 27.412 MET CONVERGENCE TOLERANCE
1836LINE 2.1524 27.850 MET CONVERGENCE TOLERANCE
1870LINE 2.3243 22.196 MET CONVERGENCE TOLERANCE
1876LINE 2.1479 27.980 MET CONVERGENCE TOLERANCE
1880LINE 1.9641 25.262 MET CONVERGENCE TOLERANCE
1887LINE 2.2712 20.477 MET CONVERGENCE TOLERANCE
1890LINE 2.2714 25.356 MET CONVERGENCE TOLERANCE
1950LINE 2.2710 21.209 MET CONVERGENCE TOLERANCE
1977LINENEW 2.3002 24.775 MET CONVERGENCE TOLERANCE
1990LINE 2.1401 49.415 MET CONVERGENCE TOLERANCE
8100LINE 2.1526 22.846 MET CONVERGENCE TOLERANCE
8200LINE 2.1526 22.887 MET CONVERGENCE TOLERANCE
8300LINE 2.3075 25.233 MET CONVERGENCE TOLERANCE
8400LINE 2.3009 32.082 MET CONVERGENCE TOLERANCE
8804ALINE 2.2711 23.085 MET CONVERGENCE TOLERANCE
8809ALINE-1 2.1525 21.105 MET CONVERGENCE TOLERANCE
8904BLINE 2.2711 22.935 MET CONVERGENCE TOLERANCE
8909BLINE-1 2.1523 21.159 MET CONVERGENCE TOLERANCE
9502LINE 2.4968 21.724 MET CONVERGENCE TOLERANCE
88003ALINE-2 2.1527 30.037 MET CONVERGENCE TOLERANCE
88003ALINE-3 2.2712 25.535 MET CONVERGENCE TOLERANCE
88005ALINE 2.2711 30.125 MET CONVERGENCE TOLERANCE
88005ALINE-1 2.1524 22.880 MET CONVERGENCE TOLERANCE
88005ALINE-2 2.2710 24.970 MET CONVERGENCE TOLERANCE
88006ALINE 2.2712 23.029 MET CONVERGENCE TOLERANCE
89003BLINE-2 2.1528 30.024 MET CONVERGENCE TOLERANCE
89003BLINE-3 2.2713 25.453 MET CONVERGENCE TOLERANCE
89005BLINE 2.2710 27.618 MET CONVERGENCE TOLERANCE
89005BLINE-1 2.1524 22.932 MET CONVERGENCE TOLERANCE
89005BLINE-2 2.2711 25.001 MET CONVERGENCE TOLERANCE
89006BLINE 2.3000 31.230 MET CONVERGENCE TOLERANCE
89006BLINE-1 2.2713 23.228 MET CONVERGENCE TOLERANCE
EDEVDEV1 2.3141 23.363 MET CONVERGENCE TOLERANCE
EDEVDEV2 2.3144 25.975 MET CONVERGENCE TOLERANCE
301-302LNS 2.3251 24.168 MET CONVERGENCE TOLERANCE
310LINE 2.3151 23.704 MET CONVERGENCE TOLERANCE
312LINE 2.3312 44.460 MET CONVERGENCE TOLERANCE
312+393LNS 2.3312 44.460 MET CONVERGENCE TOLERANCE
312+393REAC 2.3313 44.040 MET CONVERGENCE TOLERANCE
347LINE 2.3163 23.598 MET CONVERGENCE TOLERANCE
347LREAC 2.3163 23.565 MET CONVERGENCE TOLERANCE
348NLINE 2.3159 36.608 MET CONVERGENCE TOLERANCE
348N+AUTO 2.2861 36.982 MET CONVERGENCE TOLERANCE
352LINE 2.3231 33.523 MET CONVERGENCE TOLERANCE
362ELINE 2.2840 22.450 MET CONVERGENCE TOLERANCE
362WLINE 2.3145 24.006 MET CONVERGENCE TOLERANCE
368LINE 2.3169 32.836 MET CONVERGENCE TOLERANCE
371LINE 2.2875 43.597 MET CONVERGENCE TOLERANCE
376LINE 2.1529 35.930 MET CONVERGENCE TOLERANCE
381LINE 2.2847 25.640 MET CONVERGENCE TOLERANCE
381LREAC 2.2847 25.612 MET CONVERGENCE TOLERANCE
383LINE 2.3136 25.082 MET CONVERGENCE TOLERANCE
387+AUTOS 2.1829 31.727 MET CONVERGENCE TOLERANCE
393LINE 2.3216 27.266 MET CONVERGENCE TOLERANCE
1060-1165DCT 2.3099 33.403 MET CONVERGENCE TOLERANCE
1060-1270DCT 2.2713 21.119 MET CONVERGENCE TOLERANCE
1070-1080DCT 2.3221 35.055 MET CONVERGENCE TOLERANCE
1080-1280DCT 2.3383 45.510 MET CONVERGENCE TOLERANCE
1080-1490DCT 2.3346 35.224 MET CONVERGENCE TOLERANCE
1100-1200DCT 2.2434 91.390 MET CONVERGENCE TOLERANCE
1100-1300DCT 2.1385 55.547 MET CONVERGENCE TOLERANCE
1130-1430DCT 2.1364 60.323 MET CONVERGENCE TOLERANCE
1163-1550D-2 2.2632 26.451 MET CONVERGENCE TOLERANCE
1207-1775DCT 2.3328 23.554 MET CONVERGENCE TOLERANCE
1208-1640DCT 2.3000 37.746 MET CONVERGENCE TOLERANCE
1222-1730ADC 2.2710 22.791 MET CONVERGENCE TOLERANCE
1280-1870DCT 2.2969 22.429 MET CONVERGENCE TOLERANCE
1310-1763DCT 2.2397 32.131 MET CONVERGENCE TOLERANCE
1355-1610DCT 2.2491 72.628 MET CONVERGENCE TOLERANCE
1389-1880DCT 2.2790 23.935 MET CONVERGENCE TOLERANCE
1394-1515DCT 2.1221 90.827 MET CONVERGENCE TOLERANCE
1416-1867DCT 2.1365 58.114 MET CONVERGENCE TOLERANCE
1416-1880DCT 2.1365 58.467 MET CONVERGENCE TOLERANCE
1416-1890DCT 2.1366 57.265 MET CONVERGENCE TOLERANCE
1440-1450DCT 2.3168 24.357 MET CONVERGENCE TOLERANCE
1470-1565DCT 2.2764 32.961 MET CONVERGENCE TOLERANCE
1470-1637DCT 2.3243 24.520 MET CONVERGENCE TOLERANCE
1470-1720DCT 2.3243 25.577 MET CONVERGENCE TOLERANCE
1505-1607DCT 2.2749 25.737 MET CONVERGENCE TOLERANCE
1560-1570DCT 2.2718 42.429 MET CONVERGENCE TOLERANCE
1570-1575DCT 2.2353 111.20 MET CONVERGENCE TOLERANCE
1570-1580DCT 2.3139 24.200 MET CONVERGENCE TOLERANCE
1575-1585DCT 2.2591 46.716 MET CONVERGENCE TOLERANCE
1575-1990DCT 2.2581 33.184 MET CONVERGENCE TOLERANCE
1580-1585DCT 2.1365 54.407 MET CONVERGENCE TOLERANCE
1580-1730BDC 2.1523 21.233 MET CONVERGENCE TOLERANCE
1620N-1975DC 2.3010 38.558 MET CONVERGENCE TOLERANCE
1622-1887DCT 2.3132 58.722 MET CONVERGENCE TOLERANCE
1637-1720DCT 2.1530 27.446 MET CONVERGENCE TOLERANCE
1640-1690DCT 2.1305 69.008 MET CONVERGENCE TOLERANCE
1668-1721DCT 2.1384 51.067 MET CONVERGENCE TOLERANCE
1670-1771DCT 2.3175 36.868 MET CONVERGENCE TOLERANCE
1670-1830DCT 2.1324 74.415 MET CONVERGENCE TOLERANCE
1732-1788DCT 2.2864 77.887 MET CONVERGENCE TOLERANCE
1751-1777DCT 2.3162 31.466 MET CONVERGENCE TOLERANCE
1770-1887DCT 2.2411 87.949 MET CONVERGENCE TOLERANCE
1777-1779DCT 2.2716 32.562 MET CONVERGENCE TOLERANCE
1800-1810DCT 2.2696 47.991 MET CONVERGENCE TOLERANCE
1800-1825DCT 2.2494 38.099 MET CONVERGENCE TOLERANCE
1810-1825DCT 2.2832 60.389 MET CONVERGENCE TOLERANCE
1867-1977DCT 2.3006 28.705 MET CONVERGENCE TOLERANCE
1880-1977DCT 2.3004 27.867 MET CONVERGENCE TOLERANCE
1890-1977DCT 2.4749 39.670 MET CONVERGENCE TOLERANCE
1466-362EDCT 2.2845 23.657 MET CONVERGENCE TOLERANCE
1460-387DCT 2.1828 30.459 MET CONVERGENCE TOLERANCE
1610-BSKDVDC 2.2709 33.440 MET CONVERGENCE TOLERANCE
1975-362WDCT 2.3158 30.571 MET CONVERGENCE TOLERANCE
310-368DCT 2.3356 36.844 MET CONVERGENCE TOLERANCE
310-383DCT 2.3287 25.880 MET CONVERGENCE TOLERANCE
371-383DCT 2.3184 46.078 MET CONVERGENCE TOLERANCE
MANCHAUTO1 2.2719 39.698 MET CONVERGENCE TOLERANCE
PLUMAUT 2.3140 22.665 MET CONVERGENCE TOLERANCE
ASHCREEKBKR 2.2394 42.579 MET CONVERGENCE TOLERANCE
BAIRDASTK 2.3258 24.384 MET CONVERGENCE TOLERANCE
BATESROCK1T 2.1401 43.971 MET CONVERGENCE TOLERANCE
BECONFLSTK 2.1289 77.869 MET CONVERGENCE TOLERANCE
BOKUM2T 2.3004 39.926 MET CONVERGENCE TOLERANCE
BOKUM3T 2.3004 39.876 MET CONVERGENCE TOLERANCE
BRANFORD1T 2.2997 32.881 MET CONVERGENCE TOLERANCE
BRANFORD2T 2.3276 27.792 MET CONVERGENCE TOLERANCE
BRANFORD4T 2.3002 35.803 MET CONVERGENCE TOLERANCE
BRANFRDRR1T 2.2982 24.196 MET CONVERGENCE TOLERANCE
BROADWYST1 2.1328 67.781 MET CONVERGENCE TOLERANCE
BUNKERH1T 2.2589 48.043 MET CONVERGENCE TOLERANCE
BUNKERH3T 2.2575 49.443 MET CONVERGENCE TOLERANCE
COLONY1T 2.2474 38.793 MET CONVERGENCE TOLERANCE
DARIEN1T 2.2632 115.75 MET CONVERGENCE TOLERANCE
DEVON7TSTK 2.3002 27.726 MET CONVERGENCE TOLERANCE
DEVON11TSTK 2.2710 20.532 MET CONVERGENCE TOLERANCE
DEVON24TSTK 2.2711 24.501 MET CONVERGENCE TOLERANCE
DEVON26TSTK 2.2709 22.926 MET CONVERGENCE TOLERANCE
DEVON27TSTK 2.2709 28.164 MET CONVERGENCE TOLERANCE
DEVSWST1TSTK 2.3072 30.766 MET CONVERGENCE TOLERANCE
DEVSWST2TSTK 2.3070 28.502 MET CONVERGENCE TOLERANCE
DEVSWST3TSTK 2.3072 30.730 MET CONVERGENCE TOLERANCE
DEVSWST4TSTK 2.2711 30.125 MET CONVERGENCE TOLERANCE
EMERIDEN1T 2.1326 61.805 MET CONVERGENCE TOLERANCE
FLAXHILL2T 2.1326 66.648 MET CONVERGENCE TOLERANCE
FROSTBR15T 2.2995 25.348 MET CONVERGENCE TOLERANCE
FROSTBR21T 2.2900 58.834 MET CONVERGENCE TOLERANCE
FROSTBR27T 2.2589 49.799 MET CONVERGENCE TOLERANCE
GLENBROOK3T 2.2716 21.187 MET CONVERGENCE TOLERANCE
GLENBROOK8T 2.2715 25.802 MET CONVERGENCE TOLERANCE
GRNDAV1TSTK 2.1526 25.587 MET CONVERGENCE TOLERANCE
GRNDAV2TSTK 2.2716 29.464 MET CONVERGENCE TOLERANCE
GRNDAV3TSTK 2.2716 28.188 MET CONVERGENCE TOLERANCE
GREENHLL2T 2.2681 97.314 MET CONVERGENCE TOLERANCE
HADDAM1T 2.3709 40.029 MET CONVERGENCE TOLERANCE
HAWTHORNST 2.1267 84.718 MET CONVERGENCE TOLERANCE
JUNEST1 2.1297 67.513 MET CONVERGENCE TOLERANCE
MLLRVR1TSTK 2.3094 20.170 MET CONVERGENCE TOLERANCE
MLLRVR2TSTK 2.2492 74.367 MET CONVERGENCE TOLERANCE
MIXAVE1 2.2595 123.01 MET CONVERGENCE TOLERANCE
NOHAVN1TSTK 2.2506 72.072 MET CONVERGENCE TOLERANCE
NOHAVN2TSTK 2.2711 21.639 MET CONVERGENCE TOLERANCE
NWALLING1T 2.1415 40.025 MET CONVERGENCE TOLERANCE
NORWALKST1 2.3243 26.165 MET CONVERGENCE TOLERANCE
NORWALKST2 2.2715 22.852 MET CONVERGENCE TOLERANCE
OLDTOWNST 2.2663 108.23 MET CONVERGENCE TOLERANCE
PEACEABLE1T 2.2764 32.961 MET CONVERGENCE TOLERANCE
PLUMTREE25T 2.3461 41.349 MET CONVERGENCE TOLERANCE
PLUMTREE28T 2.1317 70.462 MET CONVERGENCE TOLERANCE
PLUMTREE31T 2.3076 28.151 MET CONVERGENCE TOLERANCE
QUINIPACST1 2.2370 113.11 MET CONVERGENCE TOLERANCE
ROCKRIVER1T 2.2656 32.814 MET CONVERGENCE TOLERANCE
SACKETST1 2.2905 30.097 MET CONVERGENCE TOLERANCE
SASCOCR1T 2.1475 29.858 MET CONVERGENCE TOLERANCE
SHEPAUG13A 2.3132 58.722 MET CONVERGENCE TOLERANCE
SOUTHEND5T 2.2859 54.453 MET CONVERGENCE TOLERANCE
SNAUGA1T 2.1365 54.407 MET CONVERGENCE TOLERANCE
SOTHNGTN13T 2.2491 72.628 MET CONVERGENCE TOLERANCE
SOTHNGTN14T 2.2714 33.738 MET CONVERGENCE TOLERANCE
SOTHNGTN15T 2.3175 36.868 MET CONVERGENCE TOLERANCE
SOTHNGTN16T 2.1324 74.415 MET CONVERGENCE TOLERANCE
SOTHNGTN20T 2.2922 29.179 MET CONVERGENCE TOLERANCE
SOTHNGTN22T 2.2654 26.854 MET CONVERGENCE TOLERANCE
SOTHNGTN23T 2.2962 26.372 MET CONVERGENCE TOLERANCE
SOTHNGTN24T 2.2696 47.991 MET CONVERGENCE TOLERANCE
SOTHNGTN25T 2.3146 20.731 MET CONVERGENCE TOLERANCE
SOTHNGTN26T 2.2859 50.233 MET CONVERGENCE TOLERANCE
SOTHNGTN28T 2.2632 26.451 MET CONVERGENCE TOLERANCE
STEVENSNSTK 2.2672 44.470 MET CONVERGENCE TOLERANCE
STONYHILL1T 2.2411 87.949 MET CONVERGENCE TOLERANCE
TRPFALLST1 2.2373 101.82 MET CONVERGENCE TOLERANCE
TRIANGLE2T 47.819 524.73 ITERATION LIMIT EXCEEDED
TRIANGLE3T 37.574 341.67 ITERATION LIMIT EXCEEDED
TRIANGLE4T 2.2404 96.159 MET CONVERGENCE TOLERANCE
WALLING1TSTK 2.3000 22.058 MET CONVERGENCE TOLERANCE
WALLING2TSTK 2.2712 28.886 MET CONVERGENCE TOLERANCE
WALLING4TSTK 2.2713 35.133 MET CONVERGENCE TOLERANCE
WALLING5TSTK 2.2713 35.143 MET CONVERGENCE TOLERANCE
WATERST1TSTK 2.1525 20.524 MET CONVERGENCE TOLERANCE
WATERSIDE2T 2.2707 92.928 MET CONVERGENCE TOLERANCE
WBROOKFLD1T 2.2536 64.447 MET CONVERGENCE TOLERANCE
WESTON1T 2.1283 82.014 MET CONVERGENCE TOLERANCE
WOODMNT1TSTK 2.3181 22.169 MET CONVERGENCE TOLERANCE
NOMNTSTBKR 2.3314 43.965 MET CONVERGENCE TOLERANCE
NMSTBKREAC 2.3314 43.936 MET CONVERGENCE TOLERANCE
SGTN1TSTK 2.2863 37.678 MET CONVERGENCE TOLERANCE
NORWALKST1 2.2715 22.852 MET CONVERGENCE TOLERANCE
NORWALKST2 2.1526 20.255 MET CONVERGENCE TOLERANCE
NORWALKST3 2.3151 23.832 MET CONVERGENCE TOLERANCE
GLNBRKASTK 2.3002 25.508 MET CONVERGENCE TOLERANCE
GLNBRKA1STK 2.3259 20.803 MET CONVERGENCE TOLERANCE
GLNBRKA2STK 2.3172 25.906 MET CONVERGENCE TOLERANCE
GLNBRKA3STK 2.1530 21.572 MET CONVERGENCE TOLERANCE
GLNBRKB1STK 2.1529 20.438 MET CONVERGENCE TOLERANCE
GLNBRKB2STK 2.1530 28.326 MET CONVERGENCE TOLERANCE
GLNBRKCSTK 2.2716 21.187 MET CONVERGENCE TOLERANCE
GLNBRKDSTK 2.2715 25.802 MET CONVERGENCE TOLERANCE
DC2-BES-SIN 2.2763 29.386 MET CONVERGENCE TOLERANCE
DC5-DEV-NOR 2.2342 44.031 MET CONVERGENCE TOLERANCE
CONTINGENCY LEGEND
LABEL EVENTS
100LINE : OPEN LINE FROM BUS 73344 [MONTVLLE69.000] TO BUS 73343 [GALESF A69.000] CKT 1
100+400LINES: OPEN LINE FROM BUS 73344 [MONTVLLE69.000] TO BUS 73343 [GALESF A69.000] CKT 1
OPEN LINE FROM BUS 73343 [GALESF A69.000] TO BUS 73345 [LEDYARDJ69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73615 [BUDDGTN 69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73617 [TUNNEL 69.000] CKT 1
400LINE : OPEN LINE FROM BUS 73343 [GALESF A69.000] TO BUS 73345 [LEDYARDJ69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73615 [BUDDGTN 69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73617 [TUNNEL 69.000] CKT 1
500LINE : OPEN LINE FROM BUS 73617 [TUNNEL 69.000] TO BUS 73616 [SCRRA PF69.000] CKT 1
667-690LINE : OPEN LINE FROM BUS 73336 [FALLS V 69.000] TO BUS 73337 [SALISBRY69.000] CKT 1
694LINE : OPEN LINE FROM BUS 73336 [FALLS V 69.000] TO BUS 73335 [N.CANAAN69.000] CKT 1
1000LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
OPEN LINE FROM BUS 73612 [BEAN HLL115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
1050LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1050+1766LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
OPEN LINE FROM BUS 73255 [WESTSIDE115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1060LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
1070LINE : OPEN LINE FROM BUS 73218 [STKHOUSE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1070+1490LNS: OPEN LINE FROM BUS 73291 [FORTHF 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73218 [STKHOUSE115.00] TO BUS 73215 [CARD 115.00] CKT 1
1080LINE : OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1090LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1130+1416LNS: OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
1163LINE : OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
1163+1910LNS: OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
1207LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
1208LINE : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1235LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73151 [UNCASVLA115.00] CKT 1
1238LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
1238+1813LNS: OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
1250LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73152 [UNCASVLB115.00] CKT 1
1261LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73231 [BOKUM 115.00] CKT 1
1272LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1272+1445LNS: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1280LINE : OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1300LINE : OPEN LINE FROM BUS 73220 [ENFIELD 115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
OPEN LINE FROM BUS 73222 [WNDSRLK 115.00] TO BUS 73539 [DEXTR PF13.800] CKT 1
1337LINE : OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
1342LINE : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
1355LINE : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1410LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73613 [BUDDGTN2115.00] CKT 1
1443LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1443+1759LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1445LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1460LINE : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
1470LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
1490LINE : OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
1500LINE : OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73150 [FLNDRSA 115.00] CKT 1
OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73149 [WILIAMSA115.00] CKT 1
OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1505LINE : OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73223 [FRYBRT05115.00] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73236 [FRYBR05 115.00] CKT 1
OPEN LINE FROM BUS 73236 [FRYBR05 115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73476 [TRACY05 115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73270 [BROOKLYN115.00] TO BUS 73444 [BROOKLYN23.000] CKT 1
OPEN LINE FROM BUS 73475 [TRACY 23.000] TO BUS 73476 [TRACY05 115.00] CKT 1
1508LINE : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
1537LINE : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
1545LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
1545+SPS : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73705 [IND.WELL115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
1550LINE : OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1550+1950LNS: OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1560LINE : OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
1565LINE : OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
1570LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
1572LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1572+1772LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
OPEN LINE FROM BUS 73600 [CONN YAN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1575LINE : OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
1580LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1585LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1588LINE : OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
1605LINE : OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73238 [FLANDRSB115.00] CKT 1
OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73239 [WILIAMSB115.00] CKT 1
OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1607LINE : OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73226 [FRYBRT07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73229 [FRY BR07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73229 [FRY BR07115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73442 [TRACY 23.000] CKT 1
1610LINE : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1620SLINE : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
1622LINE : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
1625LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73161 [ROCKVILL115.00] CKT 1
1630LINE : OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
1670LINE : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
1675LINE : OPEN LINE FROM BUS 73612 [BEAN HLL115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1685LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1690LINE : OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73197 [HANOVERA115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1704LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73248 [SW.HTFD 115.00] CKT 1
1720LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
1722LINE : OPEN LINE FROM BUS 73248 [SW.HTFD 115.00] TO BUS 73279 [CDECCA 115.00] CKT 1
OPEN LINE FROM BUS 73261 [NW.HTFD 115.00] TO BUS 73279 [CDECCA 115.00] CKT 1
1726LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73247 [FARMNGTN115.00] CKT 1
1732LINE : OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73262 [CANTON 115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
1750LINE : OPEN LINE FROM BUS 73167 [SO.END 115.00] TO BUS 73144 [TOMAC 115.00] CKT 1
OPEN LINE FROM BUS 73144 [TOMAC 115.00] TO BUS 73163 [COS COB 115.00] CKT 1
1751LINE : OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1752LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73257 [ROCKY HL115.00] CKT 1
1759LINE : OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1760LINE : OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
1760+1876LNS: OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
1763LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73284 [SWINDT17115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73131 [S.WNDSRA115.00] CKT 1
OPEN LINE FROM BUS 73131 [S.WNDSRA115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1765LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73255 [WESTSIDE115.00] CKT 1
1766LINE : OPEN LINE FROM BUS 73255 [WESTSIDE115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1769LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73256 [E.NBRITN115.00] CKT 1
1770LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
1771LINE : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
1773LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73257 [ROCKY HL115.00] CKT 1
1775LINE : OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73274 [RIVDRHIA115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 73274 [RIVDRHIA115.00] TO BUS 73537 [RVRSD PF23.000] CKT 1
1777LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1783LINE : OPEN LINE FROM BUS 73254 [NEWINGTN115.00] TO BUS 73247 [FARMNGTN115.00] CKT 1
OPEN LINE FROM BUS 73254 [NEWINGTN115.00] TO BUS 73256 [E.NBRITN115.00] CKT 1
1784LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73288 [NESMBY 115.00] CKT 1
OPEN LINE FROM BUS 73288 [NESMBY 115.00] TO BUS 73262 [CANTON 115.00] CKT 1
1786LINE : OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73275 [RIVDRHIB115.00] CKT 1
OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
1800-1860LNS: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
1810LINE : OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1813LINE : OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
1820LINE : OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1821LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 72991 [SAGAR 115.00] CKT 1
1835LINE : OPEN LINE FROM BUS 73235 [CHIP HIL115.00] TO BUS 73240 [THOMASTN115.00] CKT 1
1836LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 72992 [SAGBR 115.00] CKT 1
1870LINE : OPEN LINE FROM BUS 73177 [MYSTICCT115.00] TO BUS 73285 [CTRI1870115.00] CKT 1
OPEN LINE FROM BUS 73285 [CTRI1870115.00] TO BUS 72581 [WOOD RIV115.00] CKT 1
1876LINE : OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
1880LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
1887LINE : OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
1890LINE : OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
1950LINE : OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
1977LINENEW : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
1990LINE : OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
8100LINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
8200LINE : OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
8300LINE : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
8400LINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
8804ALINE : OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
8809ALINE-1 : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
8904BLINE : OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
8909BLINE-1 : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
9502LINE : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
88003ALINE-2: OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
88003ALINE-3: OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
88005ALINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
88005ALINE-1: OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
88005ALINE-2: OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
88006ALINE : OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73694 [BAIRD A 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
89003BLINE-2: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
89003BLINE-3: OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
89005BLINE : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
89005BLINE-1: OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
89005BLINE-2: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
89006BLINE : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
89006BLINE-1: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
EDEVDEV1 : OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
EDEVDEV2 : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73129 [E.DEVONJ115.00] CKT 1
301-302LNS : OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72929 [BELCH301345.00] CKT 1
OPEN LINE FROM BUS 72929 [BELCH301345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
OPEN LINE FROM BUS 71796 [CARP HL 345.00] TO BUS 71797 [MILLBURY345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
310LINE : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
312LINE : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72926 [NRTHFLD 345.00] CKT 1
312+393LNS : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72926 [NRTHFLD 345.00] CKT 1
312+393REAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
347LINE : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
347LREAC : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
348NLINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
348N+AUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
352LINE : OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73105 [LONG MTN345.00] CKT 1
362ELINE : OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
362WLINE : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
368LINE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
371LINE : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
376LINE : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
381LINE : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
381LREAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
383LINE : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
387+AUTOS : OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73664 [NHHHVDCL345.00] TO BUS 73665 [NHHHVDCL191.50] CKT 1
393LINE : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
1060-1165DCT: OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
1060-1270DCT: OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
1070-1080DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
OPEN LINE FROM BUS 73291 [FORTHF 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
1080-1280DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1080-1490DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73214 [WAWECS J115.00] CKT 1
OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1100-1200DCT: OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
1100-1300DCT: OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
OPEN LINE FROM BUS 73220 [ENFIELD 115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
OPEN LINE FROM BUS 73222 [WNDSRLK 115.00] TO BUS 73539 [DEXTR PF13.800] CKT 1
1130-1430DCT: OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
1163-1550D-2: OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1207-1775DCT: OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73253 [1775 TAP115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73274 [RIVDRHIA115.00] CKT 1
OPEN LINE FROM BUS 73274 [RIVDRHIA115.00] TO BUS 73537 [RVRSD PF23.000] CKT 1
1208-1640DCT: OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1222-1730ADC: OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 1
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1280-1870DCT: OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73177 [MYSTICCT115.00] TO BUS 73285 [CTRI1870115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73285 [CTRI1870115.00] TO BUS 72581 [WOOD RIV115.00] CKT 1
1310-1763DCT: OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73284 [SWINDT17115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73131 [S.WNDSRA115.00] CKT 1
OPEN LINE FROM BUS 73131 [S.WNDSRA115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73221 [S.WNDSRB115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73283 [SWINDT13115.00] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73221 [S.WNDSRB115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1355-1610DCT: OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1389-1880DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
1394-1515DCT: OPEN LINE FROM BUS 72978 [FRANCONA115.00] TO BUS 73266 [SCITICO 115.00] CKT 1
OPEN LINE FROM BUS 73266 [SCITICO 115.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
1416-1867DCT: OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1416-1880DCT: OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1416-1890DCT: OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1440-1450DCT: OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
1470-1565DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73155 [RDGFLD J115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
1470-1637DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
1470-1720DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1505-1607DCT: OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73223 [FRYBRT05115.00] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73236 [FRYBR05 115.00] CKT 1
OPEN LINE FROM BUS 73236 [FRYBR05 115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73476 [TRACY05 115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73270 [BROOKLYN115.00] TO BUS 73444 [BROOKLYN23.000] CKT 1
OPEN LINE FROM BUS 73475 [TRACY 23.000] TO BUS 73476 [TRACY05 115.00] CKT 1
OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73226 [FRYBRT07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73229 [FRY BR07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73229 [FRY BR07115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73442 [TRACY 23.000] CKT 1
1560-1570DCT: OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
1570-1575DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
1570-1580DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1575-1585DCT: OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
1575-1990DCT: OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73186 [BALDWINA115.00] TO BUS 73386 [BALDWINA13.800] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
1580-1585DCT: OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 2
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
1580-1730BDC: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1620N-1975DC: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
1622-1887DCT: OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
1637-1720DCT: OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1640-1690DCT: OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73197 [HANOVERA115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1668-1721DCT: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1670-1771DCT: OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
1670-1830DCT: OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1732-1788DCT: OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73262 [CANTON 115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
OPEN LINE FROM BUS 73245 [TORR TER115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
1751-1777DCT: OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1770-1887DCT: OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
1777-1779DCT: OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
1800-1810DCT: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1800-1825DCT: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1810-1825DCT: OPEN LINE FROM BUS 73154 [SGTN B 115.00] TO BUS 73234 [CHIPP TP115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1867-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1880-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1890-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1466-362EDCT: OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
1460-387DCT : OPEN LINE FROM BUS 73107 [SCOVL RK345.00] TO BUS 73663 [E.SHORE 345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
1610-BSKDVDC: OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1975-362WDCT: OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
310-368DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
310-383DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
371-383DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73109 [MONTVILE345.00] CKT 1
MANCHAUTO1 : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
PLUMAUT : OPEN LINE FROM BUS 73115 [PLUMTREE345.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
ASHCREEKBKR : OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73763 [ASHCREEK13.800] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73763 [ASHCREEK13.800] CKT 2
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73714 [ASHCREAC115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73714 [ASHCREAC115.00] CKT 2
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
BAIRDASTK : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73696 [CONGRESS115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73755 [CONGRES213.800] CKT 1
BATESROCK1T : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
BECONFLSTK : OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73228 [BALDWNJB115.00] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73387 [BEACON F13.800] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73387 [BEACON F13.800] CKT 2
BOKUM2T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
BOKUM3T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73231 [BOKUM 115.00] CKT 1
BRANFORD1T : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
BRANFORD2T : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
BRANFORD4T : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
BRANFRDRR1T : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
BROADWYST1 : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
BUNKERH1T : OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
BUNKERH3T : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
COLONY1T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
DARIEN1T : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
DEVON7TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73573 [DEVGAS1413.800] CKT 1
DEVON11TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73571 [DEVGAS1213.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
DEVON24TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
DEVON26TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73554 [DEVON#8 13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
DEVON27TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
DEVSWST1TSTK: OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
DEVSWST2TSTK: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
DEVSWST3TSTK: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
DEVSWST4TSTK: OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
EMERIDEN1T : OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
FLAXHILL2T : OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
FROSTBR15T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
FROSTBR21T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
FROSTBR27T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73186 [BALDWINA115.00] TO BUS 73386 [BALDWINA13.800] CKT 1
GLENBROOK3T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
GLENBROOK8T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GRNDAV1TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
GRNDAV2TSTK : OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
GRNDAV3TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
GREENHLL2T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
HADDAM1T : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73600 [CONN YAN115.00] CKT 1
HAWTHORNST : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 2
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
JUNEST1 : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
MLLRVR1TSTK : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73737 [MILLRIV213.800] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73737 [MILLRIV213.800] TO BUS 73676 [MILL RVR115.00] CKT 2
MLLRVR2TSTK : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73736 [MILLRIV113.800] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73736 [MILLRIV113.800] TO BUS 73676 [MILL RVR115.00] CKT 2
MIXAVE1 : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
NOHAVN1TSTK : OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 2
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73670 [QUINNIP 115.00] CKT 1
NOHAVN2TSTK : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 1
NWALLING1T : OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
NORWALKST1 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73143 [RDGEFLDA115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
NORWALKST2 : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73292 [NRWLK RX115.00] CKT 2
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OLDTOWNST : OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 2
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
PEACEABLE1T : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73155 [RDGFLD J115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
PLUMTREE25T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
PLUMTREE28T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
PLUMTREE31T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
QUINIPACST1 : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
ROCKRIVER1T : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73147 [BULLS BR115.00] CKT 1
SACKETST1 : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
SASCOCR1T : OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
SHEPAUG13A : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
SOUTHEND5T : OPEN LINE FROM BUS 73167 [SO.END 115.00] TO BUS 73144 [TOMAC 115.00] CKT 1
OPEN LINE FROM BUS 73144 [TOMAC 115.00] TO BUS 73163 [COS COB 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
SNAUGA1T : OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 2
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
SOTHNGTN13T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOTHNGTN14T : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
SOTHNGTN15T : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
SOTHNGTN16T : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOTHNGTN20T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
SOTHNGTN22T : OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SOTHNGTN23T : OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN24T : OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN25T : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN26T : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
SOTHNGTN28T : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
STEVENSNSTK : OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
STONYHILL1T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
TRPFALLST1 : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
TRIANGLE2T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
TRIANGLE3T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
TRIANGLE4T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
OPEN LINE FROM BUS 73377 [TRIANGLA13.800] TO BUS 73383 [TRIANGLB13.800] CKT 1
WALLING1TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73594 [WALL LV113.800] CKT 1
WALLING2TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73195 [DEVON 115.00] CKT 1
WALLING4TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73595 [WALL LV213.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73596 [WALL LV313.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
WALLING5TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73594 [WALL LV113.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
WATERST1TSTK: OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
WATERSIDE2T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73162 [WATERSDE115.00] TO BUS 73163 [COS COB 115.00] CKT 1
WBROOKFLD1T : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
WESTON1T : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73292 [NRWLK RX115.00] CKT 2
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73158 [WESTON 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
WOODMNT1TSTK: OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73746 [WOODMONT13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
NOMNTSTBKR : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
NMSTBKREAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
SGTN1TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
NORWALKST1 : OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWALKST2 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
NORWALKST3 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
GLNBRKASTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
GLNBRKA1STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
GLNBRKA2STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
GLNBRKA3STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
GLNBRKB1STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
GLNBRKB2STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GLNBRKCSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
GLNBRKDSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
DC2-BES-SIN : REMOVE MACHINE 2 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 2 FROM BUS 73700 [PEQUONIC115.00]
DC5-DEV-NOR : REMOVE MACHINE 5 FROM BUS 73129 [E.DEVONJ115.00]
REMOVE MACHINE 5 FROM BUS 73293 [NORWALK 345.00]