## thermal
ACCC OVERLOAD REPORT: MONITORED ELEMENTS LOADED ABOVE 100.0 % OF RATING SET B
Sort This Column for Lookup | MONITORED ELEMENT | [8 empty] | CONTINGENCY | RATE | FLOW | % | Other Case | Diff
73172-73293-2-NORAUT | 73172 |  | NORWALK | 115 | 73293 | * | NORWALK | 345 | 2 | NORAUT | 600 | 579.7 | 96.6 | #N/A | 1.6
70525-70549-1-LOSSMP3 | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | LOSSMP3 | 20 | 21.2 | 106.2 | 104.8 | 1.4
70525-70549-1-LOSSMP2 | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | LOSSMP2 | 20 | 20.9 | 104.5 | 103.2 | 1.3
70525-70549-1-330+LAKE | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | 330+LAKE | 20 | 21 | 104.8 | 103.7 | 1.1
70525-70549-1-347+LAKE | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | 347+LAKE | 20 | 21 | 104.8 | 103.7 | 1.1
70525-70549-1-CARD1T+LAKE | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | CARD1T+LAKE | 20 | 21 | 105 | 103.9 | 1.1
70525-70549-1-CARD3T+LAKE | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | CARD3T+LAKE | 20 | 21 | 105 | 103.9 | 1.1
73680-73681-1-GRNDAV2TSTK | 73680 | * | WATER ST | 115 | 73681 |  | WEST RIV | 115 | 1 | GRNDAV2TSTK | 273 | 288.1 | 101.8 | 100.8 | 1
70506-70523-1-354LINE | 70506 |  | V.RD.TAP | 115 | 70523 | * | VTYANKEE | 115 | 1 | 354LINE | 264 | 263.3 | 96.1 | 95.3 | 0.8
70525-70549-1-BASE CASE | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | BASE CASE | 20 | 19.9 | 99.4 | 98.8 | 0.6
70525-70549-1-398LINE | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | 398LINE | 20 | 21.1 | 105.7 | 105.2 | 0.5
70525-70549-1-398LREAC | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | 398LREAC | 20 | 21.1 | 105.7 | 105.2 | 0.5
73107-73116-1-310-348WDCT | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | 310-348WDCT | 436 | 428.3 | 95.3 | #N/A | 0.3
73107-73116-1-1975-348DCT | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | 1975-348DCT | 436 | 428.4 | 95.2 | #N/A | 0.2
73244-73258-1-1207-1775DCT | 73258 | * | BLOOMFLD | 115 | 73244 |  | N.BLMFLD | 115 | 1 | 1207-1775DCT | 193 | 214.5 | 113.8 | 113.6 | 0.2
70521-70555-1-354LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 354LINE | 50 | 54.6 | 109.2 | 109.1 | 0.1
70512-70719-1-LOSSMP3 | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | LOSSMP3 | 50 | 51.3 | 102.5 | 102.4 | 0.1
73107-73116-1-348LINE | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | 348LINE | 436 | 428.4 | 95.1 | #N/A | 0.1
70490-70504-1-BASE CASE | 70490 | * | VERNONRD | 115 | 70504 |  | SBRAT 69 | 69 | 1 | BASE CASE | 24 | 25 | 104.2 | 104.2 | 0
70512-70719-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 50.3 | 100.5 | 100.5 | 0
70512-70735-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70735 |  | WILL #2 | 34.5 | 1 | BASE CASE | 50 | 48.8 | 97.6 | 97.6 | 0
70521-70555-1-BASE CASE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | BASE CASE | 50 | 52.7 | 105.3 | 105.3 | 0
70557-70714-1-BASE CASE | 70557 | * | Q CITY | 115 | 70714 |  | Q CTY 34 | 34.5 | 1 | BASE CASE | 50 | 52.7 | 105.4 | 105.4 | 0
70712-70719-1-BASE CASE | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 48.6 | 96.2 | 96.2 | 0
70721-70732-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70732 |  | MCNEIL T | 34.5 | 1 | BASE CASE | 30 | 29.6 | 101.4 | 101.4 | 0
70721-70740-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70740 |  | 10-20 | 13.8 | 1 | BASE CASE | 20 | 26.1 | 130.5 | 130.5 | 0
73107-73116-1-DC3-BES-DEV | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | DC3-BES-DEV | 436 | 428.4 | 95 | #N/A | 0
73107-73116-1-DEVON2TSTK | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | DEVON2TSTK | 436 | 428.4 | 95 | #N/A | 0
73107-73116-1-DEVON3TSTK | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | DEVON3TSTK | 436 | 428.4 | 95 | #N/A | 0
73107-73116-1-ESHORE12TSTK | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | ESHORE12TSTK | 436 | 428.4 | 95 | #N/A | 0
73107-73116-1-LOSSNHAV | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | LOSSNHAV | 436 | 428.4 | 95 | #N/A | 0
73144-73167-1-1440-1450DCT | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440-1450DCT | 252 | 255.2 | 99.2 | 99.2 | 0
73144-73167-1-1440LINE | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440LINE | 252 | 255.2 | 98.8 | 98.8 | 0
73144-73167-1-GLENBROOK3T | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLENBROOK3T | 252 | 255.2 | 98.8 | 98.8 | 0
73144-73167-1-GLNBRKCSTK | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLNBRKCSTK | 252 | 255.2 | 98.8 | 98.8 | 0
73162-73163-1-SOUTHEND6T | 73162 |  | WATERSDE | 115 | 73163 | * | COS COB | 115 | 1 | SOUTHEND6T | 239 | 298.7 | 124.7 | 124.7 | 0
73162-73168-1-SOUTHEND6T | 73162 | * | WATERSDE | 115 | 73168 |  | GLNBROOK | 115 | 1 | SOUTHEND6T | 352 | 367 | 102.4 | 102.4 | 0
73339-73340-1-1625LINE | 73339 |  | BARBR HL | 69 | 73340 | * | ROCKVILL | 69 | 1 | 1625LINE | 84 | 90.3 | 113 | 113.1 | -0.1
70525-70549-1-LONGMT5TSTK | 70525 |  | BLISSVIL | 115 | 70549 | * | BLISS 46 | 46 | 1 | LONGMT5TSTK | 20 | 21 | 104.8 | 104.9 | -0.1
73167-73294-1-1440-1450DCT | 73167 | * | SO.END | 115 | 73294 |  | GLNBRK J | 115 | 1 | 1440-1450DCT | 289 | 365.6 | 123.1 | 123.2 | -0.1
73144-73167-1-GLNBRKA2STK | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLNBRKA2STK | 252 | 255.3 | 99 | 99.2 | -0.2
73170-73176-1-1165LINE | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | 1165LINE | 138 | 144.8 | 104 | 104.2 | -0.2
73651-73668-1-WOODMNT1TSTK | 73651 | * | NH HARBR | 22 | 73668 |  | E.SHORE | 115 | 1 | WOODMNT1TSTK | 475 | 451.5 | 95 | 95.4 | -0.4
73251-73261-1-1207-1775DCT | 73251 |  | BLM JCT | 115 | 73261 | * | NW.HTFD | 115 | 1 | 1207-1775DCT | 228 | 239.7 | 107.9 | 108.4 | -0.5
73170-73176-1-PLUMTREE31T | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | PLUMTREE31T | 138 | 139.7 | 100 | 100.6 | -0.6
73170-73176-2-1060-1270DCT | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 2 | 1060-1270DCT | 166 | 224.8 | 134.3 | 135.1 | -0.8
73176-73268-1-1060-1165DCT | 73176 | * | TRIANGLE | 115 | 73268 |  | MIDDLRIV | 115 | 1 | 1060-1165DCT | 134 | 147 | 110.8 | 111.6 | -0.8
73170-73268-1-1060-1165DCT | 73170 |  | PLUMTREE | 115 | 73268 | * | MIDDLRIV | 115 | 1 | 1060-1165DCT | 126 | 226.2 | 180 | 181.2 | -1.2
73210-73611-1-1080LINE | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080LINE | 183 | 195.1 | 111 | 112.5 | -1.5
73210-73611-1-1070-1080DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1070-1080DCT | 183 | 195.1 | 110.9 | 112.5 | -1.6
73210-73611-1-1080-1280DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080-1280DCT | 183 | 195 | 111 | 112.6 | -1.6
73210-73611-1-1080-1490DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080-1490DCT | 183 | 195 | 110.9 | 112.5 | -1.6
73188-73192-1-BUNKERH2T | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | BUNKERH2T | 112 | 109.4 | 102.9 | 105.9 | -3
73188-73192-1-1272-1721DCT | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | 1272-1721DCT | 112 | 131 | 126.1 | 129.6 | -3.5

## voltage
MONITORED VOLTAGE REPORT
Sort This Column for Lookup | SYSTEM |  | CONTINGENCY | BUS |  |  | V-CONT | V-INIT | V-MAX | V-MIN | Other Case | Diff
70622-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70622 | WHITE RV | 13.8 | 1.0521 | 1.0521 | 1.05 | 0.9 | 1.0522 | -0.0001
70625-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70625 | WTRFORD | 34.5 | 1.058 | 1.058 | 1.05 | 0.9 | 1.058 | 0
70626-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70626 | GILMAN | 34.5 | 1.0593 | 1.0593 | 1.05 | 0.9 | 1.0594 | -0.0001
70639-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70639 | HGATE VL | 46 | 1.0554 | 1.0554 | 1.05 | 0.9 | 1.0554 | 0
70640-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70640 | MISSQ P | 48 | 1.0554 | 1.0554 | 1.05 | 0.9 | 1.0554 | 0
70693-318-362STKBR | ZONE 41 | RANGE | 318-362STKBR | 70693 | ESX-STAT | 3.2 | 1.0677 | 1.0628 | 1.05 | 0.9 | 1.0673 | 0.0004
70693-330+LAKE | ZONE 41 | RANGE | 330+LAKE | 70693 | ESX-STAT | 3.2 | 1.0728 | 1.0628 | 1.05 | 0.9 | 1.072 | 0.0008
70693-330LINE | ZONE 41 | RANGE | 330LINE | 70693 | ESX-STAT | 3.2 | 1.0598 | 1.0628 | 1.05 | 0.9 | 1.0597 | 0.0001
70693-347+LAKE | ZONE 41 | RANGE | 347+LAKE | 70693 | ESX-STAT | 3.2 | 1.0728 | 1.0628 | 1.05 | 0.9 | 1.0721 | 0.0007
70693-354LINE | ZONE 41 | RANGE | 354LINE | 70693 | ESX-STAT | 3.2 | 1.0663 | 1.0628 | 1.05 | 0.9 | 1.0656 | 0.0007
70693-384LINE | ZONE 41 | RANGE | 384LINE | 70693 | ESX-STAT | 3.2 | 1.0664 | 1.0628 | 1.05 | 0.9 | 1.066 | 0.0004
70693-398LINE | ZONE 41 | RANGE | 398LINE | 70693 | ESX-STAT | 3.2 | 1.0705 | 1.0628 | 1.05 | 0.9 | 1.0707 | -0.0002
70693-398LREAC | ZONE 41 | RANGE | 398LREAC | 70693 | ESX-STAT | 3.2 | 1.0705 | 1.0628 | 1.05 | 0.9 | 1.0707 | -0.0002
70693-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70693 | ESX-STAT | 3.2 | 1.0628 | 1.0628 | 1.05 | 0.9 | 1.0627 | 0.0001
70693-CARD1T+LAKE | ZONE 41 | RANGE | CARD1T+LAKE | 70693 | ESX-STAT | 3.2 | 1.0731 | 1.0628 | 1.05 | 0.9 | 1.0724 | 0.0007
70693-CARD1TSTK | ZONE 41 | RANGE | CARD1TSTK | 70693 | ESX-STAT | 3.2 | 1.06 | 1.0628 | 1.05 | 0.9 | 1.0598 | 0.0002
70693-CARD3T+LAKE | ZONE 41 | RANGE | CARD3T+LAKE | 70693 | ESX-STAT | 3.2 | 1.0731 | 1.0628 | 1.05 | 0.9 | 1.0724 | 0.0007
70693-CARD3TSTK | ZONE 41 | RANGE | CARD3TSTK | 70693 | ESX-STAT | 3.2 | 1.06 | 1.0628 | 1.05 | 0.9 | 1.0598 | 0.0002
70693-DEVON2TSTK | ZONE 41 | RANGE | DEVON2TSTK | 70693 | ESX-STAT | 3.2 | 1.0666 | 1.0628 | 1.05 | 0.9 | #N/A | 0.0166
70693-DEVON3TSTK | ZONE 41 | RANGE | DEVON3TSTK | 70693 | ESX-STAT | 3.2 | 1.0667 | 1.0628 | 1.05 | 0.9 | #N/A | 0.0167
70693-ESHORE12TSTK | ZONE 41 | RANGE | ESHORE12TSTK | 70693 | ESX-STAT | 3.2 | 1.0666 | 1.0628 | 1.05 | 0.9 | 1.0662 | 0.0004
70693-LOLAKERD | ZONE 41 | RANGE | LOLAKERD | 70693 | ESX-STAT | 3.2 | 1.066 | 1.0628 | 1.05 | 0.9 | 1.0658 | 0.0002
70693-LONGMT5TSTK | ZONE 41 | RANGE | LONGMT5TSTK | 70693 | ESX-STAT | 3.2 | 1.0692 | 1.0628 | 1.05 | 0.9 | 1.0703 | -0.0011
70693-LOSSBPT3 | ZONE 41 | RANGE | LOSSBPT3 | 70693 | ESX-STAT | 3.2 | 1.0654 | 1.0628 | 1.05 | 0.9 | 1.0653 | 0.0001
70693-LOSSMID4 | ZONE 41 | RANGE | LOSSMID4 | 70693 | ESX-STAT | 3.2 | 1.0664 | 1.0628 | 1.05 | 0.9 | 1.066 | 0.0004
70693-LOSSMON6 | ZONE 41 | RANGE | LOSSMON6 | 70693 | ESX-STAT | 3.2 | 1.0667 | 1.0628 | 1.05 | 0.9 | 1.0663 | 0.0004
70693-LOSSMP2 | ZONE 41 | RANGE | LOSSMP2 | 70693 | ESX-STAT | 3.2 | 1.0723 | 1.0628 | 1.05 | 0.9 | 1.0713 | 0.001
70693-LOSSMP3 | ZONE 41 | RANGE | LOSSMP3 | 70693 | ESX-STAT | 3.2 | 1.0768 | 1.0628 | 1.05 | 0.9 | 1.0752 | 0.0016
70693-LOSSNHAV | ZONE 41 | RANGE | LOSSNHAV | 70693 | ESX-STAT | 3.2 | 1.0666 | 1.0628 | 1.05 | 0.9 | 1.0663 | 0.0003
70693-PEQUON42TSTK | ZONE 41 | RANGE | PEQUON42TSTK | 70693 | ESX-STAT | 3.2 | 1.0654 | 1.0628 | 1.05 | 0.9 | 1.0652 | 0.0002
73129-1545-1570DCT | ZONE 171 | RANGE | 1545-1570DCT | 73129 | E.DEVONJ | 115 | 1.05 | 1.0455 | 1.05 | 0.9 | #N/A | 0
73129-DEVON6TSTK | ZONE 171 | RANGE | DEVON6TSTK | 73129 | E.DEVONJ | 115 | 1.05 | 1.0455 | 1.05 | 0.9 | #N/A | 0
73129-EDEVDEV1 | ZONE 171 | RANGE | EDEVDEV1 | 73129 | E.DEVONJ | 115 | 1.05 | 1.0455 | 1.05 | 0.9 | #N/A | 0
73129-EDEVDEV2 | ZONE 171 | RANGE | EDEVDEV2 | 73129 | E.DEVONJ | 115 | 1.05 | 1.0455 | 1.05 | 0.9 | #N/A | 0
73129-EDEVSTK | ZONE 171 | RANGE | EDEVSTK | 73129 | E.DEVONJ | 115 | 1.05 | 1.0455 | 1.05 | 0.9 | #N/A | 0
73151-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73151 | UNCASVLA | 115 | 1.0534 | 1.0105 | 1.05 | 0.9 | 1.0533 | 0.0001
73152-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73152 | UNCASVLB | 115 | 1.0536 | 1.0107 | 1.05 | 0.9 | 1.0535 | 0.0001
73153-1508LINE | ZONE 171 | RANGE | 1508LINE | 73153 | BRANFORD | 115 | 1.0507 | 1.0362 | 1.05 | 0.9 | #N/A | 0.0007
73153-BRANFORD1T | ZONE 171 | RANGE | BRANFORD1T | 73153 | BRANFORD | 115 | 1.0528 | 1.0362 | 1.05 | 0.9 | #N/A | 0.0028
73153-BRANFORD4T | ZONE 171 | RANGE | BRANFORD4T | 73153 | BRANFORD | 115 | 1.0536 | 1.0362 | 1.05 | 0.9 | #N/A | 0.0036
73160-1272-1721DCT | ZONE 171 | RANGE | 1272-1721DCT | 73160 | BALDWINB | 115 | 0.8992 | 1.015 | 1.05 | 0.9 | 0.8811 | 0.0181
73161-1625LINE | ZONE 171 | RANGE | 1625LINE | 73161 | ROCKVILL | 115 | 0.842 | 0.989 | 1.05 | 0.9 | 0.841 | 0.001
73185-1272-1721DCT | ZONE 171 | RANGE | 1272-1721DCT | 73185 | BUNKER H | 115 | 0.8995 | 1.0231 | 1.05 | 0.9 | 0.8814 | 0.0181
73189-1272-1721DCT | ZONE 171 | RANGE | 1272-1721DCT | 73189 | FREIGHT | 115 | 0.898 | 1.0243 | 1.05 | 0.9 | 0.8799 | 0.0181
73202-329-352DCT | ZONE 171 | RANGE | 329-352DCT | 73202 | FROST BR | 115 | 1.0501 | 1.0312 | 1.05 | 0.9 | #N/A | 0.0001
73202-352+AUTO | ZONE 171 | RANGE | 352+AUTO | 73202 | FROST BR | 115 | 1.0503 | 1.0312 | 1.05 | 0.9 | #N/A | 0.0003
73210-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73210 | MONTVLLE | 115 | 1.0538 | 1.0109 | 1.05 | 0.9 | 1.0537 | 0.0001
73267-1867-1977DCT | ZONE 171 | RANGE | 1867-1977DCT | 73267 | DARIEN | 115 | 1.0658 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0158
73267-1880-1977DCT | ZONE 171 | RANGE | 1880-1977DCT | 73267 | DARIEN | 115 | 1.0658 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0158
73267-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73267 | DARIEN | 115 | 1.0658 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0158
73267-1977LINENEW | ZONE 171 | RANGE | 1977LINENEW | 73267 | DARIEN | 115 | 1.0658 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0158
73267-GLNBRKASTK | ZONE 171 | RANGE | GLNBRKASTK | 73267 | DARIEN | 115 | 1.0658 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0158
73267-SOUTHEND5T | ZONE 171 | RANGE | SOUTHEND5T | 73267 | DARIEN | 115 | 1.0658 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0158
73267-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73267 | DARIEN | 115 | 1.0658 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0158
73270-1070-1080DCT | ZONE 171 | RANGE | 1070-1080DCT | 73270 | BROOKLYN | 115 | 0.8907 | 0.947 | 1.05 | 0.9 | 0.8819 | 0.0088
73270-1080-1280DCT | ZONE 171 | RANGE | 1080-1280DCT | 73270 | BROOKLYN | 115 | 0.8904 | 0.947 | 1.05 | 0.9 | 0.8813 | 0.0091
73270-1080-1490DCT | ZONE 171 | RANGE | 1080-1490DCT | 73270 | BROOKLYN | 115 | 0.8909 | 0.947 | 1.05 | 0.9 | 0.882 | 0.0089
73270-1080LINE | ZONE 171 | RANGE | 1080LINE | 73270 | BROOKLYN | 115 | 0.8907 | 0.947 | 1.05 | 0.9 | 0.8819 | 0.0088
73278-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73278 | MONT DSL | 115 | 1.0538 | 1.0109 | 1.05 | 0.9 | 1.0537 | 0.0001
73286-1867-1977DCT | ZONE 171 | RANGE | 1867-1977DCT | 73286 | COMPO | 115 | 1.0559 | 1.0393 | 1.05 | 0.9 | #N/A | 0.0059
73286-1880-1977DCT | ZONE 171 | RANGE | 1880-1977DCT | 73286 | COMPO | 115 | 1.0559 | 1.0393 | 1.05 | 0.9 | #N/A | 0.0059
73286-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73286 | COMPO | 115 | 1.0559 | 1.0393 | 1.05 | 0.9 | #N/A | 0.0059
73286-1977LINENEW | ZONE 171 | RANGE | 1977LINENEW | 73286 | COMPO | 115 | 1.0559 | 1.0393 | 1.05 | 0.9 | #N/A | 0.0059
73286-GLNBRKASTK | ZONE 171 | RANGE | GLNBRKASTK | 73286 | COMPO | 115 | 1.0559 | 1.0393 | 1.05 | 0.9 | #N/A | 0.0059
73286-SOUTHEND5T | ZONE 171 | RANGE | SOUTHEND5T | 73286 | COMPO | 115 | 1.0559 | 1.0393 | 1.05 | 0.9 | #N/A | 0.0059
73286-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73286 | COMPO | 115 | 1.0559 | 1.0393 | 1.05 | 0.9 | #N/A | 0.0059
73293-1565-PLNRDCT | '345KV ' | RANGE | 1565-PLNRDCT | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.95 | #N/A | 0
73293-1565-PLNRDCT | ZONE 171 | RANGE | 1565-PLNRDCT | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.9 | #N/A | 0
73293-1618-321DCT | '345KV ' | RANGE | 1618-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.95 | #N/A | 0
73293-1618-321DCT | ZONE 171 | RANGE | 1618-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.9 | #N/A | 0
73293-1770-321DCT | '345KV ' | RANGE | 1770-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.95 | #N/A | 0
73293-1770-321DCT | ZONE 171 | RANGE | 1770-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.9 | #N/A | 0
73293-1887-321DCT | '345KV ' | RANGE | 1887-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.95 | #N/A | 0
73293-1887-321DCT | ZONE 171 | RANGE | 1887-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.9 | #N/A | 0
73293-321LINE | '345KV ' | RANGE | 321LINE | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.95 | #N/A | 0
73293-321LINE | ZONE 171 | RANGE | 321LINE | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.9 | #N/A | 0
73293-398LINE | '345KV ' | RANGE | 398LINE | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.95 | #N/A | 0
73293-398LINE | ZONE 171 | RANGE | 398LINE | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.9 | #N/A | 0
73293-398LREAC | '345KV ' | RANGE | 398LREAC | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.95 | #N/A | 0
73293-398LREAC | ZONE 171 | RANGE | 398LREAC | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.9 | #N/A | 0
73293-LONGMT5TSTK | '345KV ' | RANGE | LONGMT5TSTK | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.95 | #N/A | 0
73293-LONGMT5TSTK | ZONE 171 | RANGE | LONGMT5TSTK | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.9 | #N/A | 0
73293-PLUMNOR | '345KV ' | RANGE | PLUMNOR | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.95 | #N/A | 0
73293-PLUMNOR | ZONE 171 | RANGE | PLUMNOR | 73293 | NORWALK | 345 | 1.05 | 1.0162 | 1.05 | 0.9 | #N/A | 0
73300-1867-1977DCT | ZONE 171 | RANGE | 1867-1977DCT | 73300 | ELYTAP | 115 | 1.0615 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0115
73300-1880-1977DCT | ZONE 171 | RANGE | 1880-1977DCT | 73300 | ELYTAP | 115 | 1.0615 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0115
73300-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73300 | ELYTAP | 115 | 1.0615 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0115
73300-1977LINENEW | ZONE 171 | RANGE | 1977LINENEW | 73300 | ELYTAP | 115 | 1.0615 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0115
73300-GLNBRKASTK | ZONE 171 | RANGE | GLNBRKASTK | 73300 | ELYTAP | 115 | 1.0615 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0115
73300-SOUTHEND5T | ZONE 171 | RANGE | SOUTHEND5T | 73300 | ELYTAP | 115 | 1.0615 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0115
73300-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73300 | ELYTAP | 115 | 1.0615 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0115
73388-1130-1430DCT | ZONE 171 | RANGE | 1130-1430DCT | 73388 | SO.NAUG | 13.8 | 1.0543 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0043
73388-113091001DCT | ZONE 171 | RANGE | 113091001DCT | 73388 | SO.NAUG | 13.8 | 1.0532 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0032
73388-1385LN+AUTO | ZONE 171 | RANGE | 1385LN+AUTO | 73388 | SO.NAUG | 13.8 | 1.0545 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0045
73388-1416-1890DCT | ZONE 171 | RANGE | 1416-1890DCT | 73388 | SO.NAUG | 13.8 | 1.0544 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0044
73388-1545-1570DCT | ZONE 171 | RANGE | 1545-1570DCT | 73388 | SO.NAUG | 13.8 | 1.0534 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0034
73388-1570LINE | ZONE 171 | RANGE | 1570LINE | 73388 | SO.NAUG | 13.8 | 1.0537 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0037
73388-1618-321DCT | ZONE 171 | RANGE | 1618-321DCT | 73388 | SO.NAUG | 13.8 | 1.0547 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0047
73388-1668-1721DCT | ZONE 171 | RANGE | 1668-1721DCT | 73388 | SO.NAUG | 13.8 | 1.0536 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0036
73388-1710-1730BDC | ZONE 171 | RANGE | 1710-1730BDC | 73388 | SO.NAUG | 13.8 | 1.0528 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0028
73388-1710-1730CDC | ZONE 171 | RANGE | 1710-1730CDC | 73388 | SO.NAUG | 13.8 | 1.0514 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0014
73388-1721LINE | ZONE 171 | RANGE | 1721LINE | 73388 | SO.NAUG | 13.8 | 1.054 | 1.0573 | 1.05 | 0.9 | #N/A | 0.004
73388-1730CLINE | ZONE 171 | RANGE | 1730CLINE | 73388 | SO.NAUG | 13.8 | 1.0546 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0046
73388-1770-321DCT | ZONE 171 | RANGE | 1770-321DCT | 73388 | SO.NAUG | 13.8 | 1.0518 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0018
73388-1770LINE | ZONE 171 | RANGE | 1770LINE | 73388 | SO.NAUG | 13.8 | 1.0543 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0043
73388-1887-321DCT | ZONE 171 | RANGE | 1887-321DCT | 73388 | SO.NAUG | 13.8 | 1.0527 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0027
73388-321LINE | ZONE 171 | RANGE | 321LINE | 73388 | SO.NAUG | 13.8 | 1.0534 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0034
73388-329-352DCT | ZONE 171 | RANGE | 329-352DCT | 73388 | SO.NAUG | 13.8 | 1.0682 | 1.0573 | 1.05 | 0.9 | 1.0559 | 0.0123
73388-329LINE | ZONE 171 | RANGE | 329LINE | 73388 | SO.NAUG | 13.8 | 1.0539 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0039
73388-352+AUTO | ZONE 171 | RANGE | 352+AUTO | 73388 | SO.NAUG | 13.8 | 1.0683 | 1.0573 | 1.05 | 0.9 | 1.056 | 0.0123
73388-8100-8200DCT | ZONE 171 | RANGE | 8100-8200DCT | 73388 | SO.NAUG | 13.8 | 1.0517 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0017
73388-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73388 | SO.NAUG | 13.8 | 1.0573 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0073
73388-DC1-BES-NOR | ZONE 171 | RANGE | DC1-BES-NOR | 73388 | SO.NAUG | 13.8 | 1.0535 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0035
73388-DC3-BES-DEV | ZONE 171 | RANGE | DC3-BES-DEV | 73388 | SO.NAUG | 13.8 | 1.0502 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0002
73388-DC5-DEV-NOR | ZONE 171 | RANGE | DC5-DEV-NOR | 73388 | SO.NAUG | 13.8 | 1.0523 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0023
73388-DEVON24TSTK | ZONE 171 | RANGE | DEVON24TSTK | 73388 | SO.NAUG | 13.8 | 1.0548 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0048
73388-DEVON6TSTK | ZONE 171 | RANGE | DEVON6TSTK | 73388 | SO.NAUG | 13.8 | 1.0534 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0034
73388-DEVON7TSTK | ZONE 171 | RANGE | DEVON7TSTK | 73388 | SO.NAUG | 13.8 | 1.0537 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0037
73388-FROSTBR27T | ZONE 171 | RANGE | FROSTBR27T | 73388 | SO.NAUG | 13.8 | 1.0524 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0024
73388-LOSSBPT3 | ZONE 171 | RANGE | LOSSBPT3 | 73388 | SO.NAUG | 13.8 | 1.052 | 1.0573 | 1.05 | 0.9 | #N/A | 0.002
73388-NORWLKHAR3T | ZONE 171 | RANGE | NORWLKHAR3T | 73388 | SO.NAUG | 13.8 | 1.0545 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0045
73388-NORWLKHAR3T | ZONE 171 | RANGE | NORWLKHAR3T | 73388 | SO.NAUG | 13.8 | 1.0545 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0045
73388-NORWLKHARBT | ZONE 171 | RANGE | NORWLKHARBT | 73388 | SO.NAUG | 13.8 | 1.0545 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0045
73388-PEQUON22TSTK | ZONE 171 | RANGE | PEQUON22TSTK | 73388 | SO.NAUG | 13.8 | 1.0539 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0039
73388-PEQUON32TSTK | ZONE 171 | RANGE | PEQUON32TSTK | 73388 | SO.NAUG | 13.8 | 1.0546 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0046
73388-PEQUON42TSTK | ZONE 171 | RANGE | PEQUON42TSTK | 73388 | SO.NAUG | 13.8 | 1.0503 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0003
73388-PLUMTREE25T | ZONE 171 | RANGE | PLUMTREE25T | 73388 | SO.NAUG | 13.8 | 1.0539 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0039
73388-SGTN3TSTK | ZONE 171 | RANGE | SGTN3TSTK | 73388 | SO.NAUG | 13.8 | 1.0544 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0044
73388-SGTN4TSTK | ZONE 171 | RANGE | SGTN4TSTK | 73388 | SO.NAUG | 13.8 | 1.0544 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0044
73388-SGTN5TSTK | ZONE 171 | RANGE | SGTN5TSTK | 73388 | SO.NAUG | 13.8 | 1.0537 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0037
73388-SOTHNGTN22T | ZONE 171 | RANGE | SOTHNGTN22T | 73388 | SO.NAUG | 13.8 | 1.0547 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0047
73388-WOODMNT1TSTK | ZONE 171 | RANGE | WOODMNT1TSTK | 73388 | SO.NAUG | 13.8 | 1.0534 | 1.0573 | 1.05 | 0.9 | #N/A | 0.0034
73399-329-352DCT | ZONE 171 | RANGE | 329-352DCT | 73399 | NOERA | 13.8 | 1.0586 | 1.0424 | 1.05 | 0.9 | 1.0526 | 0.006
73399-352+AUTO | ZONE 171 | RANGE | 352+AUTO | 73399 | NOERA | 13.8 | 1.0589 | 1.0424 | 1.05 | 0.9 | 1.0527 | 0.0062
73418-SGTN7TSTK | ZONE 171 | RANGE | SGTN7TSTK | 73418 | BLKRK B | 13.8 | 1.0514 | 1.0387 | 1.05 | 0.9 | #N/A | 0.0014
73448-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73448 | UNCASVIL | 27.6 | 1.0511 | 1.0081 | 1.05 | 0.9 | 1.051 | 0.0001
73476-1070-1080DCT | ZONE 171 | RANGE | 1070-1080DCT | 73476 | TRACY05 | 115 | 0.8849 | 0.9418 | 1.05 | 0.9 | 0.876 | 0.0089
73476-1080-1280DCT | ZONE 171 | RANGE | 1080-1280DCT | 73476 | TRACY05 | 115 | 0.8845 | 0.9418 | 1.05 | 0.9 | 0.8754 | 0.0091
73476-1080-1490DCT | ZONE 171 | RANGE | 1080-1490DCT | 73476 | TRACY05 | 115 | 0.8851 | 0.9418 | 1.05 | 0.9 | 0.8761 | 0.009
73476-1080LINE | ZONE 171 | RANGE | 1080LINE | 73476 | TRACY05 | 115 | 0.8849 | 0.9418 | 1.05 | 0.9 | 0.876 | 0.0089
73620-MONTVSTBKR | ZONE 178 | RANGE | MONTVSTBKR | 73620 | BUDDGTNB | 34.5 | 1.0798 | 1.0353 | 1.05 | 0.9 | 1.0798 | 0
73657-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73657 | ENGLISH7 | 13.8 | 1.0516 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0016
73657-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73657 | ENGLISH7 | 13.8 | 1.057 | 1.0604 | 1.05 | 0.9 | #N/A | 0.007
73657-1508LINE | ZONE 185 | RANGE | 1508LINE | 73657 | ENGLISH7 | 13.8 | 1.0633 | 1.0604 | 1.05 | 0.9 | 1.0538 | 0.0095
73657-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73657 | ENGLISH7 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73657-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73657 | ENGLISH7 | 13.8 | 1.0574 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0074
73657-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73657 | ENGLISH7 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73657-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73657 | ENGLISH7 | 13.8 | 1.0572 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0072
73657-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73657 | ENGLISH7 | 13.8 | 1.0565 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0065
73657-321LINE | ZONE 185 | RANGE | 321LINE | 73657 | ENGLISH7 | 13.8 | 1.0572 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0072
73657-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73657 | ENGLISH7 | 13.8 | 1.0576 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0076
73657-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73657 | ENGLISH7 | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73657-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0577 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0077
73657-88006ALINE | ZONE 185 | RANGE | 88006ALINE | 73657 | ENGLISH7 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73657-8809ALINE-1 | ZONE 185 | RANGE | 8809ALINE-1 | 73657 | ENGLISH7 | 13.8 | 1.0574 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0074
73657-8809ALINE-2 | ZONE 185 | RANGE | 8809ALINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0575 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0075
73657-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73657 | ENGLISH7 | 13.8 | 1.0578 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0078
73657-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73657 | ENGLISH7 | 13.8 | 1.0578 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0078
73657-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0577 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0077
73657-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73657 | ENGLISH7 | 13.8 | 1.0556 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0056
73657-89006BLINE-1 | ZONE 185 | RANGE | 89006BLINE-1 | 73657 | ENGLISH7 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73657-8909BLINE-1 | ZONE 185 | RANGE | 8909BLINE-1 | 73657 | ENGLISH7 | 13.8 | 1.0574 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0074
73657-8909BLINE-2 | ZONE 185 | RANGE | 8909BLINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0575 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0075
73657-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0543 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0043
73657-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0545 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0045
73657-BAIRDASTK | ZONE 185 | RANGE | BAIRDASTK | 73657 | ENGLISH7 | 13.8 | 1.0567 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0067
73657-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73657 | ENGLISH7 | 13.8 | 1.0554 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0054
73657-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73657 | ENGLISH7 | 13.8 | 1.0604 | 1.0604 | 1.05 | 0.9 | 1.0507 | 0.0097
73657-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73657 | ENGLISH7 | 13.8 | 1.0633 | 1.0604 | 1.05 | 0.9 | 1.0539 | 0.0094
73657-BUNKERH2T | ZONE 185 | RANGE | BUNKERH2T | 73657 | ENGLISH7 | 13.8 | 1.0578 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0078
73657-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73657 | ENGLISH7 | 13.8 | 1.052 | 1.0604 | 1.05 | 0.9 | #N/A | 0.002
73657-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0551 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0051
73657-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73657 | ENGLISH7 | 13.8 | 1.0544 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0044
73657-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0561 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0061
73657-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0563 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0063
73657-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73657 | ENGLISH7 | 13.8 | 1.0561 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0061
73657-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73657-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73657 | ENGLISH7 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73657-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0556 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0056
73657-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73657 | ENGLISH7 | 13.8 | 1.0565 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0065
73657-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73657 | ENGLISH7 | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73657-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73657 | ENGLISH7 | 13.8 | 1.0544 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0044
73657-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73657 | ENGLISH7 | 13.8 | 1.0557 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0057
73657-PEQUON22TSTK | ZONE 185 | RANGE | PEQUON22TSTK | 73657 | ENGLISH7 | 13.8 | 1.0571 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0071
73657-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73657 | ENGLISH7 | 13.8 | 1.0512 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0012
73657-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73657 | ENGLISH7 | 13.8 | 1.0577 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0077
73657-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73657-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0565 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0065
73658-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73658 | ENGLISH8 | 13.8 | 1.0516 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0016
73658-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73658 | ENGLISH8 | 13.8 | 1.057 | 1.0604 | 1.05 | 0.9 | #N/A | 0.007
73658-1508LINE | ZONE 185 | RANGE | 1508LINE | 73658 | ENGLISH8 | 13.8 | 1.0633 | 1.0604 | 1.05 | 0.9 | 1.0538 | 0.0095
73658-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73658 | ENGLISH8 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73658-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73658 | ENGLISH8 | 13.8 | 1.0574 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0074
73658-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73658 | ENGLISH8 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73658-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73658 | ENGLISH8 | 13.8 | 1.0572 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0072
73658-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73658 | ENGLISH8 | 13.8 | 1.0565 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0065
73658-321LINE | ZONE 185 | RANGE | 321LINE | 73658 | ENGLISH8 | 13.8 | 1.0572 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0072
73658-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73658 | ENGLISH8 | 13.8 | 1.0576 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0076
73658-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73658 | ENGLISH8 | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73658-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0577 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0077
73658-88006ALINE | ZONE 185 | RANGE | 88006ALINE | 73658 | ENGLISH8 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73658-8809ALINE-1 | ZONE 185 | RANGE | 8809ALINE-1 | 73658 | ENGLISH8 | 13.8 | 1.0574 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0074
73658-8809ALINE-2 | ZONE 185 | RANGE | 8809ALINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0575 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0075
73658-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73658 | ENGLISH8 | 13.8 | 1.0578 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0078
73658-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73658 | ENGLISH8 | 13.8 | 1.0578 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0078
73658-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0577 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0077
73658-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73658 | ENGLISH8 | 13.8 | 1.0556 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0056
73658-89006BLINE-1 | ZONE 185 | RANGE | 89006BLINE-1 | 73658 | ENGLISH8 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73658-8909BLINE-1 | ZONE 185 | RANGE | 8909BLINE-1 | 73658 | ENGLISH8 | 13.8 | 1.0574 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0074
73658-8909BLINE-2 | ZONE 185 | RANGE | 8909BLINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0575 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0075
73658-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0543 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0043
73658-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0545 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0045
73658-BAIRDASTK | ZONE 185 | RANGE | BAIRDASTK | 73658 | ENGLISH8 | 13.8 | 1.0567 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0067
73658-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73658 | ENGLISH8 | 13.8 | 1.0554 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0054
73658-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73658 | ENGLISH8 | 13.8 | 1.0604 | 1.0604 | 1.05 | 0.9 | 1.0507 | 0.0097
73658-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73658 | ENGLISH8 | 13.8 | 1.0633 | 1.0604 | 1.05 | 0.9 | 1.0539 | 0.0094
73658-BUNKERH2T | ZONE 185 | RANGE | BUNKERH2T | 73658 | ENGLISH8 | 13.8 | 1.0578 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0078
73658-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73658 | ENGLISH8 | 13.8 | 1.052 | 1.0604 | 1.05 | 0.9 | #N/A | 0.002
73658-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0551 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0051
73658-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73658 | ENGLISH8 | 13.8 | 1.0544 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0044
73658-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0561 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0061
73658-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0563 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0063
73658-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73658 | ENGLISH8 | 13.8 | 1.0561 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0061
73658-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73658-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73658 | ENGLISH8 | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73658-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0556 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0056
73658-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73658 | ENGLISH8 | 13.8 | 1.0565 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0065
73658-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73658 | ENGLISH8 | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73658-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73658 | ENGLISH8 | 13.8 | 1.0544 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0044
73658-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73658 | ENGLISH8 | 13.8 | 1.0557 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0057
73658-PEQUON22TSTK | ZONE 185 | RANGE | PEQUON22TSTK | 73658 | ENGLISH8 | 13.8 | 1.0571 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0071
73658-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73658 | ENGLISH8 | 13.8 | 1.0512 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0012
73658-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73658 | ENGLISH8 | 13.8 | 1.0577 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0077
73658-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73658-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0565 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0065
73665-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73665 | NHHHVDCL | 192 | 1.0571 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0071
73665-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73665 | NHHHVDCL | 192 | 1.0613 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0113
73665-1508LINE | ZONE 185 | RANGE | 1508LINE | 73665 | NHHHVDCL | 192 | 1.055 | 1.0638 | 1.05 | 0.9 | #N/A | 0.005
73665-1545-1570DCT | ZONE 185 | RANGE | 1545-1570DCT | 73665 | NHHHVDCL | 192 | 1.0597 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0097
73665-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73665 | NHHHVDCL | 192 | 1.0601 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0101
73665-1630LINE | ZONE 185 | RANGE | 1630LINE | 73665 | NHHHVDCL | 192 | 1.0593 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0093
73665-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73665 | NHHHVDCL | 192 | 1.0607 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0107
73665-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73665 | NHHHVDCL | 192 | 1.0602 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0102
73665-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73665 | NHHHVDCL | 192 | 1.0605 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0105
73665-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73665 | NHHHVDCL | 192 | 1.0592 | 1.0638 | 1.05 | 0.9 | 1.0538 | 0.0054
73665-321LINE | ZONE 185 | RANGE | 321LINE | 73665 | NHHHVDCL | 192 | 1.0605 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0105
73665-330+LAKE | ZONE 185 | RANGE | 330+LAKE | 73665 | NHHHVDCL | 192 | 1.0594 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0094
73665-347+LAKE | ZONE 185 | RANGE | 347+LAKE | 73665 | NHHHVDCL | 192 | 1.0594 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0094
73665-384LINE | ZONE 185 | RANGE | 384LINE | 73665 | NHHHVDCL | 192 | 1.0611 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0111
73665-84004LINE | ZONE 185 | RANGE | 84004LINE | 73665 | NHHHVDCL | 192 | 1.0566 | 1.0638 | 1.05 | 0.9 | 1.0596 | -0.003
73665-88003ALINE-2 | ZONE 185 | RANGE | 88003ALINE-2 | 73665 | NHHHVDCL | 192 | 1.0602 | 1.0638 | 1.05 | 0.9 | 1.0597 | 0.0005
73665-89003BLINE-2 | ZONE 185 | RANGE | 89003BLINE-2 | 73665 | NHHHVDCL | 192 | 1.0602 | 1.0638 | 1.05 | 0.9 | 1.0597 | 0.0005
73665-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73665 | NHHHVDCL | 192 | 1.0609 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0109
73665-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73665 | NHHHVDCL | 192 | 1.0605 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0105
73665-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73665 | NHHHVDCL | 192 | 1.0606 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0106
73665-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73665 | NHHHVDCL | 192 | 1.0608 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0108
73665-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73665 | NHHHVDCL | 192 | 1.0638 | 1.0638 | 1.05 | 0.9 | 1.0569 | 0.0069
73665-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73665 | NHHHVDCL | 192 | 1.0547 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0047
73665-BRANFORD2T | ZONE 185 | RANGE | BRANFORD2T | 73665 | NHHHVDCL | 192 | 1.0559 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0059
73665-BRANFORD4T | ZONE 185 | RANGE | BRANFORD4T | 73665 | NHHHVDCL | 192 | 1.0574 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0074
73665-CARD1T+LAKE | ZONE 185 | RANGE | CARD1T+LAKE | 73665 | NHHHVDCL | 192 | 1.0595 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0095
73665-CARD3T+LAKE | ZONE 185 | RANGE | CARD3T+LAKE | 73665 | NHHHVDCL | 192 | 1.0595 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0095
73665-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73665 | NHHHVDCL | 192 | 1.0569 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0069
73665-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73665 | NHHHVDCL | 192 | 1.0596 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0096
73665-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73665 | NHHHVDCL | 192 | 1.0588 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0088
73665-DEVON6TSTK | ZONE 185 | RANGE | DEVON6TSTK | 73665 | NHHHVDCL | 192 | 1.0597 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0097
73665-EDEVDEV2 | ZONE 185 | RANGE | EDEVDEV2 | 73665 | NHHHVDCL | 192 | 1.0586 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0086
73665-ESHORE12TSTK | ZONE 185 | RANGE | ESHORE12TSTK | 73665 | NHHHVDCL | 192 | 1.0579 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0079
73665-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73665 | NHHHVDCL | 192 | 1.0593 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0093
73665-LOSSMID4 | ZONE 185 | RANGE | LOSSMID4 | 73665 | NHHHVDCL | 192 | 1.0611 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0111
73665-LOSSMP2 | ZONE 185 | RANGE | LOSSMP2 | 73665 | NHHHVDCL | 192 | 1.0592 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0092
73665-LOSSMP3 | ZONE 185 | RANGE | LOSSMP3 | 73665 | NHHHVDCL | 192 | 1.058 | 1.0638 | 1.05 | 0.9 | #N/A | 0.008
73665-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73665 | NHHHVDCL | 192 | 1.0577 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0077
73665-MLLRVR2TSTK | ZONE 185 | RANGE | MLLRVR2TSTK | 73665 | NHHHVDCL | 192 | 1.058 | 1.0638 | 1.05 | 0.9 | #N/A | 0.008
73665-NOHAVN2TSTK | ZONE 185 | RANGE | NOHAVN2TSTK | 73665 | NHHHVDCL | 192 | 1.0603 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0103
73665-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73665 | NHHHVDCL | 192 | 1.0576 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0076
73665-SCOVRK7TSTK | ZONE 185 | RANGE | SCOVRK7TSTK | 73665 | NHHHVDCL | 192 | 1.0598 | 1.0638 | 1.05 | 0.9 | 1.0601 | -0.0003
73665-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73665 | NHHHVDCL | 192 | 1.061 | 1.0638 | 1.05 | 0.9 | #N/A | 0.011
73665-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73665 | NHHHVDCL | 192 | 1.0612 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0112
73665-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73665 | NHHHVDCL | 192 | 1.061 | 1.0638 | 1.05 | 0.9 | #N/A | 0.011
73665-WALLING1TSTK | ZONE 185 | RANGE | WALLING1TSTK | 73665 | NHHHVDCL | 192 | 1.0593 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0093
73665-WALLING2TSTK | ZONE 185 | RANGE | WALLING2TSTK | 73665 | NHHHVDCL | 192 | 1.0587 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0087
73665-WOODMNT1TSTK | ZONE 185 | RANGE | WOODMNT1TSTK | 73665 | NHHHVDCL | 192 | 1.0584 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0084
73665-WOODMNT2TSTK | ZONE 185 | RANGE | WOODMNT2TSTK | 73665 | NHHHVDCL | 192 | 1.0583 | 1.0638 | 1.05 | 0.9 | #N/A | 0.0083
73671-1630LINE | ZONE 185 | RANGE | 1630LINE | 73671 | NO.HAVEN | 115 | 1.0538 | 1.0421 | 1.05 | 0.9 | #N/A | 0.0038
73671-NOHAVN2TSTK | ZONE 185 | RANGE | NOHAVN2TSTK | 73671 | NO.HAVEN | 115 | 1.0612 | 1.0421 | 1.05 | 0.9 | 1.0501 | 0.0111
73671-WALLING1TSTK | ZONE 185 | RANGE | WALLING1TSTK | 73671 | NO.HAVEN | 115 | 1.0538 | 1.0421 | 1.05 | 0.9 | #N/A | 0.0038
73671-WALLING2TSTK | ZONE 185 | RANGE | WALLING2TSTK | 73671 | NO.HAVEN | 115 | 1.0539 | 1.0421 | 1.05 | 0.9 | #N/A | 0.0039
73672-84004LINE | ZONE 185 | RANGE | 84004LINE | 73672 | SACKETT | 115 | 1.053 | 1.0442 | 1.05 | 0.9 | #N/A | 0.003
73700-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73700 | PEQUONIC | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73716-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73716 | PEQBETAP | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73729-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73729 | ENGLISH | 13.8 | 1.0516 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0016
73729-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73729 | ENGLISH | 13.8 | 1.057 | 1.0604 | 1.05 | 0.9 | #N/A | 0.007
73729-1508LINE | ZONE 185 | RANGE | 1508LINE | 73729 | ENGLISH | 13.8 | 1.0633 | 1.0604 | 1.05 | 0.9 | 1.0538 | 0.0095
73729-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73729 | ENGLISH | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73729-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73729 | ENGLISH | 13.8 | 1.0574 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0074
73729-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73729 | ENGLISH | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73729-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73729 | ENGLISH | 13.8 | 1.0572 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0072
73729-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73729 | ENGLISH | 13.8 | 1.0565 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0065
73729-321LINE | ZONE 185 | RANGE | 321LINE | 73729 | ENGLISH | 13.8 | 1.0572 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0072
73729-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73729 | ENGLISH | 13.8 | 1.0576 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0076
73729-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73729 | ENGLISH | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73729-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73729 | ENGLISH | 13.8 | 1.0577 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0077
73729-88006ALINE | ZONE 185 | RANGE | 88006ALINE | 73729 | ENGLISH | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73729-8809ALINE-1 | ZONE 185 | RANGE | 8809ALINE-1 | 73729 | ENGLISH | 13.8 | 1.0574 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0074
73729-8809ALINE-2 | ZONE 185 | RANGE | 8809ALINE-2 | 73729 | ENGLISH | 13.8 | 1.0575 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0075
73729-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73729 | ENGLISH | 13.8 | 1.0578 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0078
73729-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73729 | ENGLISH | 13.8 | 1.0578 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0078
73729-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73729 | ENGLISH | 13.8 | 1.0577 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0077
73729-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73729 | ENGLISH | 13.8 | 1.0556 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0056
73729-89006BLINE-1 | ZONE 185 | RANGE | 89006BLINE-1 | 73729 | ENGLISH | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73729-8909BLINE-1 | ZONE 185 | RANGE | 8909BLINE-1 | 73729 | ENGLISH | 13.8 | 1.0574 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0074
73729-8909BLINE-2 | ZONE 185 | RANGE | 8909BLINE-2 | 73729 | ENGLISH | 13.8 | 1.0575 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0075
73729-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73729 | ENGLISH | 13.8 | 1.0543 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0043
73729-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73729 | ENGLISH | 13.8 | 1.0545 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0045
73729-BAIRDASTK | ZONE 185 | RANGE | BAIRDASTK | 73729 | ENGLISH | 13.8 | 1.0567 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0067
73729-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73729 | ENGLISH | 13.8 | 1.0554 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0054
73729-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73729 | ENGLISH | 13.8 | 1.0604 | 1.0604 | 1.05 | 0.9 | 1.0507 | 0.0097
73729-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73729 | ENGLISH | 13.8 | 1.0633 | 1.0604 | 1.05 | 0.9 | 1.0539 | 0.0094
73729-BUNKERH2T | ZONE 185 | RANGE | BUNKERH2T | 73729 | ENGLISH | 13.8 | 1.0578 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0078
73729-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73729 | ENGLISH | 13.8 | 1.052 | 1.0604 | 1.05 | 0.9 | #N/A | 0.002
73729-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73729 | ENGLISH | 13.8 | 1.0551 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0051
73729-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73729 | ENGLISH | 13.8 | 1.0544 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0044
73729-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73729 | ENGLISH | 13.8 | 1.0561 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0061
73729-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73729 | ENGLISH | 13.8 | 1.0563 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0063
73729-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73729 | ENGLISH | 13.8 | 1.0561 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0061
73729-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73729 | ENGLISH | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73729-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73729 | ENGLISH | 13.8 | 1.0569 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0069
73729-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73729 | ENGLISH | 13.8 | 1.0556 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0056
73729-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73729 | ENGLISH | 13.8 | 1.0565 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0065
73729-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73729 | ENGLISH | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73729-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73729 | ENGLISH | 13.8 | 1.0544 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0044
73729-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73729 | ENGLISH | 13.8 | 1.0557 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0057
73729-PEQUON22TSTK | ZONE 185 | RANGE | PEQUON22TSTK | 73729 | ENGLISH | 13.8 | 1.0571 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0071
73729-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73729 | ENGLISH | 13.8 | 1.0512 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0012
73729-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73729 | ENGLISH | 13.8 | 1.0577 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0077
73729-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73729 | ENGLISH | 13.8 | 1.0566 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0066
73729-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73729 | ENGLISH | 13.8 | 1.0565 | 1.0604 | 1.05 | 0.9 | #N/A | 0.0065
73746-WOODMNT1TSTK | ZONE 186 | RANGE | WOODMNT1TSTK | 73746 | WOODMONT | 13.8 | 0.413 | 1.0311 | 1.05 | 0.9 | 0.4111 | 0.0019
73746-WOODMNT2TSTK | ZONE 186 | RANGE | WOODMNT2TSTK | 73746 | WOODMONT | 13.8 | 0.4245 | 1.0311 | 1.05 | 0.9 | 0.4183 | 0.0062

## contingencies
CONTINGENCY LEGEND
LABEL EVENTS
100LINE : OPEN LINE FROM BUS 73344 [MONTVLLE69.000] TO BUS 73343 [GALESF A69.000] CKT 1
100+400LINES: OPEN LINE FROM BUS 73344 [MONTVLLE69.000] TO BUS 73343 [GALESF A69.000] CKT 1
OPEN LINE FROM BUS 73343 [GALESF A69.000] TO BUS 73345 [LEDYARDJ69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73615 [BUDDGTN 69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73617 [TUNNEL 69.000] CKT 1
400LINE : OPEN LINE FROM BUS 73343 [GALESF A69.000] TO BUS 73345 [LEDYARDJ69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73615 [BUDDGTN 69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73617 [TUNNEL 69.000] CKT 1
500LINE : OPEN LINE FROM BUS 73617 [TUNNEL 69.000] TO BUS 73616 [SCRRA PF69.000] CKT 1
667-690LINE : OPEN LINE FROM BUS 73336 [FALLS V 69.000] TO BUS 73337 [SALISBRY69.000] CKT 1
689LINE : OPEN LINE FROM BUS 73346 [TORRGTN 69.000] TO BUS 73336 [FALLS V 69.000] CKT 1
693LINE : OPEN LINE FROM BUS 73346 [TORRGTN 69.000] TO BUS 73336 [FALLS V 69.000] CKT 2
694LINE : OPEN LINE FROM BUS 73336 [FALLS V 69.000] TO BUS 73335 [N.CANAAN69.000] CKT 1
1000LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
OPEN LINE FROM BUS 73612 [BEAN HLL115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
1050LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1050+1766LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
OPEN LINE FROM BUS 73255 [WESTSIDE115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1060LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
1070LINE : OPEN LINE FROM BUS 73218 [STKHOUSE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1070+1490LNS: OPEN LINE FROM BUS 73291 [FORTHF 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73218 [STKHOUSE115.00] TO BUS 73215 [CARD 115.00] CKT 1
1080LINE : OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1090LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1100LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
1130LINE : OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1130+1416LNS: OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
1163LINE : OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
1163+1910LNS: OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
1165LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
1191LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
1200LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
1206LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73600 [CONN YAN115.00] CKT 1
1207LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
1208LINE : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1222LINE : OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 1
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 2
1235LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73151 [UNCASVLA115.00] CKT 1
1238LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
1238+1813LNS: OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
1250LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73152 [UNCASVLB115.00] CKT 1
1261LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73231 [BOKUM 115.00] CKT 1
1270LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
1272LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1272+1445LNS: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1280LINE : OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1300LINE : OPEN LINE FROM BUS 73220 [ENFIELD 115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
OPEN LINE FROM BUS 73222 [WNDSRLK 115.00] TO BUS 73539 [DEXTR PF13.800] CKT 1
1310LINE : OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73221 [S.WNDSRB115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73283 [SWINDT13115.00] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73221 [S.WNDSRB115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1337LINE : OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
1342LINE : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
ONE1385 : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
1385LN+AUTO : OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 2
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 3
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1389LINE : OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1394LINE : OPEN LINE FROM BUS 73266 [SCITICO 115.00] TO BUS 72978 [FRANCONA115.00] CKT 1
1410LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73613 [BUDDGTN2115.00] CKT 1
1416LINE : OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1430LINE : OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
1440LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
1443LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1445LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1450LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
1460LINE : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
1466LINE : OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
1470LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
1490LINE : OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
1508LINE : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
1515LINE : OPEN LINE FROM BUS 72972 [LUDLOW 115.00] TO BUS 73266 [SCITICO 115.00] CKT 1
1537LINE : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
1545LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
1545+SPS : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73705 [IND.WELL115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
1550LINE : OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1550+1950LNS: OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1560LINE : OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
1565LINE : OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
1570LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
1572LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1572+1772LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
OPEN LINE FROM BUS 73600 [CONN YAN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1575LINE : OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
1580LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1585LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1588LINE : OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
1594LINE : OPEN LINE FROM BUS 73705 [IND.WELL115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
1607LINE : OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73226 [FRYBRT07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73229 [FRY BR07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73229 [FRY BR07115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73442 [TRACY 23.000] CKT 1
1610LINE : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1618LINE : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
1620NLINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73241 [MIDDLTWN115.00] CKT 1
1620SLINE : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
1622LINE : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
1625LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73161 [ROCKVILL115.00] CKT 1
1630LINE : OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
1637LINE : OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
1640LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1655LINE : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
1668LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1670LINE : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
1675LINE : OPEN LINE FROM BUS 73612 [BEAN HLL115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1685LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1704LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73248 [SW.HTFD 115.00] CKT 1
1710LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
1720LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
1721LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1722LINE : OPEN LINE FROM BUS 73248 [SW.HTFD 115.00] TO BUS 73279 [CDECCA 115.00] CKT 1
OPEN LINE FROM BUS 73261 [NW.HTFD 115.00] TO BUS 73279 [CDECCA 115.00] CKT 1
1726LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73247 [FARMNGTN115.00] CKT 1
1730ALINE : OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1730BLINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1730CLINE : OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1732LINE : OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73262 [CANTON 115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
1740LINE : OPEN LINE FROM BUS 73162 [WATERSDE115.00] TO BUS 73163 [COS COB 115.00] CKT 1
1751LINE : OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1752LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73257 [ROCKY HL115.00] CKT 1
1753LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
1756LINE : OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
1759LINE : OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1760LINE : OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
1763LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73284 [SWINDT17115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73131 [S.WNDSRA115.00] CKT 1
OPEN LINE FROM BUS 73131 [S.WNDSRA115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1765LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73255 [WESTSIDE115.00] CKT 1
1766LINE : OPEN LINE FROM BUS 73255 [WESTSIDE115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1767LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73259 [HOPEWELL115.00] CKT 1
1769LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73256 [E.NBRITN115.00] CKT 1
1770LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
1771LINE : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
1772LINE : OPEN LINE FROM BUS 73600 [CONN YAN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1773LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73257 [ROCKY HL115.00] CKT 1
1775LINE : OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73274 [RIVDRHIA115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 73274 [RIVDRHIA115.00] TO BUS 73537 [RVRSD PF23.000] CKT 1
1777LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1779LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1780LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
1783LINE : OPEN LINE FROM BUS 73254 [NEWINGTN115.00] TO BUS 73247 [FARMNGTN115.00] CKT 1
OPEN LINE FROM BUS 73254 [NEWINGTN115.00] TO BUS 73256 [E.NBRITN115.00] CKT 1
1784LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73288 [NESMBY 115.00] CKT 1
OPEN LINE FROM BUS 73288 [NESMBY 115.00] TO BUS 73262 [CANTON 115.00] CKT 1
1785LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73254 [NEWINGTN115.00] CKT 1
1786LINE : OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73275 [RIVDRHIB115.00] CKT 1
OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
1788LINE : OPEN LINE FROM BUS 73245 [TORR TER115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
1790LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
1792LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
1800-1860LNS: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
1810LINE : OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1813LINE : OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
1821LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 72991 [SAGAR 115.00] CKT 1
1825LINE : OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1830LINE : OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1835LINE : OPEN LINE FROM BUS 73235 [CHIP HIL115.00] TO BUS 73240 [THOMASTN115.00] CKT 1
1836LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 72992 [SAGBR 115.00] CKT 1
1867LINE : OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
1870LINE : OPEN LINE FROM BUS 73177 [MYSTICCT115.00] TO BUS 73285 [CTRI1870115.00] CKT 1
OPEN LINE FROM BUS 73285 [CTRI1870115.00] TO BUS 72581 [WOOD RIV115.00] CKT 1
1876LINE : OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
1880LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
1887LINE : OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
1890LINE : OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
1900LINE : OPEN LINE FROM BUS 73203 [CAMPV PH115.00] TO BUS 73245 [TORR TER115.00] CKT 1
1910LINE : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
1921LINE : OPEN LINE FROM BUS 73203 [CAMPV PH115.00] TO BUS 73240 [THOMASTN115.00] CKT 1
1950LINE : OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
1975LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
1977LINENEW : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
1990LINE : OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
8100LINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
8200LINE : OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
8300LINE : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
8400LINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
8500LINE : OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
8600LINE : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
8700LINE : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
8804ALINE : OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
8809ALINE-1 : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
8809ALINE-2 : OPEN LINE FROM BUS 73694 [BAIRD A 115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
8904BLINE : OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
8909BLINE-1 : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
8909BLINE-2 : OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
9500LINE : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
9502LINE : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
84004LINE : OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
88003ALINE : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
88003ALINE-1: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
88003ALINE-2: OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
88003ALINE-3: OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
88005ALINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
88005ALINE-1: OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
88005ALINE-2: OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
88006ALINE : OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73694 [BAIRD A 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
89003BLINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
89003BLINE-1: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
89003BLINE-2: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
89003BLINE-3: OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
89005BLINE : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
89005BLINE-1: OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
89005BLINE-2: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
89006BLINE : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
89006BLINE-1: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
91001LINE : OPEN LINE FROM BUS 73701 [CRRA JCT115.00] TO BUS 73702 [CRRA XFO115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
EDEVDEV1 : OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
EDEVDEV2 : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73129 [E.DEVONJ115.00] CKT 1
301-302LNS : OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72929 [BELCH301345.00] CKT 1
OPEN LINE FROM BUS 72929 [BELCH301345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
OPEN LINE FROM BUS 71796 [CARP HL 345.00] TO BUS 71797 [MILLBURY345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
310LINE : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
312LINE : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72926 [NRTHFLD 345.00] CKT 1
312+393LNS : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72926 [NRTHFLD 345.00] CKT 1
312+393REAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
318LINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
321LINE : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
329LINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
330LINE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
330+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73566 [LAKERD#221.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73567 [LAKERD#321.000] CKT 1
347+LAKE : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73566 [LAKERD#221.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73567 [LAKERD#321.000] CKT 1
348LINE : OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
348NLINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
348N+AUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
352LINE : OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73105 [LONG MTN345.00] CKT 1
352+AUTO : OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73105 [LONG MTN345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73202 [FROST BR115.00] CKT 1
353LINE : OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
353+AUTO : OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
354LINE : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
362ELINE : OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
362WLINE : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
364+AUTO : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
368LINE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
371LINE : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
371+AUTO : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
376LINE : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
381LINE : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
381LREAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
383LINE : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
384LINE : OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
393LINE : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
395LINE : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
395+AUTO : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
398LINE : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
398LREAC : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
PLUMNOR : OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73133 [PLUMUG 345.00] CKT 2
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73134 [NORUG 345.00] CKT 3
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 2
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 3
OPEN LINE FROM BUS 73135 [NOROH 345.00] TO BUS 73293 [NORWALK 345.00] CKT 3
1000-1090DCT: OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
OPEN LINE FROM BUS 73611 [DUDLEY T115.00] TO BUS 73612 [BEAN HLL115.00] CKT 1
OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1060-1165DCT: OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
1060-1270DCT: OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
1070-1080DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
OPEN LINE FROM BUS 73291 [FORTHF 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
1080-1280DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1080-1490DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73214 [WAWECS J115.00] CKT 1
OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1100-1300DCT: OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
OPEN LINE FROM BUS 73220 [ENFIELD 115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
OPEN LINE FROM BUS 73222 [WNDSRLK 115.00] TO BUS 73539 [DEXTR PF13.800] CKT 1
1130-1430DCT: OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
113091001DCT: OPEN LINE FROM BUS 73701 [CRRA JCT115.00] TO BUS 73702 [CRRA XFO115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1207-1775DCT: OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73253 [1775 TAP115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73274 [RIVDRHIA115.00] CKT 1
OPEN LINE FROM BUS 73274 [RIVDRHIA115.00] TO BUS 73537 [RVRSD PF23.000] CKT 1
1208-1640DCT: OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1222-1730ADC: OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 1
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1261-1620SDC: OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
1272-1721DCT: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1355-1610DCT: OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1389-1880DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
1416-1867DCT: OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1416-1880DCT: OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1416-1890DCT: OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1440-1450DCT: OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
1470-1637DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
1470-1720DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1545-1570DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
1570-1580DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1575-1585DCT: OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
1575-1990DCT: OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73186 [BALDWINA115.00] TO BUS 73386 [BALDWINA13.800] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
1580-1730BDC: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1620N-1975DC: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
1622-1887DCT: OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
1637-1720DCT: OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1668-1721DCT: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1670-1771DCT: OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
1710-1730ADC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1710-1730BDC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1710-1730CDC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1720-1730ADC: OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1732-1788DCT: OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73262 [CANTON 115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
OPEN LINE FROM BUS 73245 [TORR TER115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
1751-1777DCT: OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1777-1779DCT: OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
1810-1825DCT: OPEN LINE FROM BUS 73154 [SGTN B 115.00] TO BUS 73234 [CHIPP TP115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1867-1880DCT: OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
1867-1890DCT: OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
1867-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1880-1890DCT: OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1880-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1890-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
8100-8200DCT: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
1466-362EDCT: OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
1565-PLNRDCT: OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73133 [PLUMUG 345.00] CKT 2
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73134 [NORUG 345.00] CKT 3
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 2
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 3
OPEN LINE FROM BUS 73135 [NOROH 345.00] TO BUS 73293 [NORWALK 345.00] CKT 3
1610-BSKDVDC: OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1618-321DCT : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
1751-395DCT : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
1759-353DCT : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73114 [PORT JCT345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1767-353DCT : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73259 [HOPEWELL115.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73114 [PORT JCT345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1770-321DCT : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
1779-395DCT : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
1887-321DCT : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
1975-348DCT : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
1975-362WDCT: OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
310-348WDCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
310-368DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
329-352DCT : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73106 [SOUTHGTN345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73202 [FROST BR115.00] CKT 1
362W-376DCT : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
371-383DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73109 [MONTVILE345.00] CKT 1
MANCHAUTO1 : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
NORAUT : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73293 [NORWALK 345.00] CKT 1
PLUMAUT : OPEN LINE FROM BUS 73115 [PLUMTREE345.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
SOUTH1XAUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOUTH2XAUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
LOSSBPT3 : OPEN LINE FROM BUS 73648 [BPTHBR#322.000] TO BUS 73700 [PEQUONIC115.00] CKT 1
LOSSDEV7 : OPEN LINE FROM BUS 73553 [DEVON#7 13.800] TO BUS 73195 [DEVON 115.00] CKT 1
LOLAKERD : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
LOSSMID4 : OPEN LINE FROM BUS 73557 [MIDDTN#422.000] TO BUS 73116 [MIDDLTWN345.00] CKT 1
LOSSMP2 : OPEN LINE FROM BUS 73562 [MILL#2 24.000] TO BUS 73110 [MILLSTNE345.00] CKT 1
LOSSMP3 : OPEN LINE FROM BUS 73563 [MILL#3 24.000] TO BUS 73110 [MILLSTNE345.00] CKT 1
LOSSMON6 : OPEN LINE FROM BUS 73559 [MONTV#6 22.000] TO BUS 73210 [MONTVLLE115.00] CKT 1
LOSSNHAV : OPEN LINE FROM BUS 73651 [NH HARBR22.000] TO BUS 73668 [E.SHORE 115.00] CKT 1
LOSSNOR1 : OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
LOSSNOR2 : OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
ALLINGS1TSTK: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
ALLINGS2TSTK: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73685 [ALLINGSB115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
ASHCREEKBKR : OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73763 [ASHCREEK13.800] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73763 [ASHCREEK13.800] CKT 2
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73714 [ASHCREAC115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73714 [ASHCREAC115.00] CKT 2
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
BAIRDASTK : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73696 [CONGRESS115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73755 [CONGRES213.800] CKT 1
BAIRDBSTK : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73697 [CONGRESS115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73755 [CONGRES213.800] CKT 1
BOKUM2T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
BOKUM3T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73231 [BOKUM 115.00] CKT 1
BRANFORD1T : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
BRANFORD2T : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
BRANFORD4T : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
BRANFRDRR1T : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
BUNKERH1T : OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
BUNKERH2T : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
BUNKERH3T : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
DEVON1TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
DEVON2TSTK : OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73125 [MILFORD 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
DEVON3TSTK : OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73125 [MILFORD 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73570 [DEVGAS1113.800] CKT 1
DEVON6TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
DEVON7TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73573 [DEVGAS1413.800] CKT 1
DEVON8TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73573 [DEVGAS1413.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
DEVON10TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73571 [DEVGAS1213.800] CKT 1
DEVON11TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73571 [DEVGAS1213.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
DEVON12TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73570 [DEVGAS1113.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73572 [DEVGAS1313.800] CKT 1
DEVON23TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73553 [DEVON#7 13.800] CKT 1
DEVON24TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
DEVON25TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73554 [DEVON#8 13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
DEVON26TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73554 [DEVON#8 13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
DEVON27TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
DEVSWST1TSTK: OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
DEVSWST2TSTK: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
DEVSWST3TSTK: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
DEVSWST4TSTK: OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
EDEVSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73129 [E.DEVONJ115.00] CKT 1
OPEN LINE FROM BUS 73125 [MILFORD 115.00] TO BUS 73129 [E.DEVONJ115.00] CKT 1
OPEN LINE FROM BUS 73125 [MILFORD 115.00] TO BUS 73574 [MILFD#1 13.800] CKT 1
OPEN LINE FROM BUS 73125 [MILFORD 115.00] TO BUS 73575 [MILFD#2 13.800] CKT 1
ESHORE12TSTK: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73651 [NH HARBR22.000] CKT 1
FROSTBR21T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
FROSTBR27T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73186 [BALDWINA115.00] TO BUS 73386 [BALDWINA13.800] CKT 1
GLENBROOK3T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
GLENBROOK8T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GRNDAV1TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
GRNDAV2TSTK : OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
GRNDAV3TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
GRNDAV4TSTK : OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
GRNDAV5TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
GRNDAV6TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
GRNDAV7TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
HADDAM1T : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73600 [CONN YAN115.00] CKT 1
MLLRVR2TSTK : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73736 [MILLRIV113.800] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73736 [MILLRIV113.800] TO BUS 73676 [MILL RVR115.00] CKT 2
NOHAVN2TSTK : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 1
NWALLING1T : OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
NORWALKST1 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73143 [RDGEFLDA115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
NORWALKST2 : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73292 [NRWLK RX115.00] CKT 2
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
NORWLKHAR1T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR2T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR3T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR4T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR7T : OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
PEQUON22TSTK: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73696 [CONGRESS115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
PEQUON32TSTK: OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73647 [BPTHBR#220.000] CKT 1
PEQUON42TSTK: OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73697 [CONGRESS115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73648 [BPTHBR#322.000] CKT 1
PLUMTREE25T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
PLUMTREE31T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
ROCKRIVER1T : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73147 [BULLS BR115.00] CKT 1
SASCOCR1T : OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
SHEPAUG13A : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
SOUTHEND5T : OPEN LINE FROM BUS 73167 [SO.END 115.00] TO BUS 73144 [TOMAC 115.00] CKT 1
OPEN LINE FROM BUS 73144 [TOMAC 115.00] TO BUS 73163 [COS COB 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
SOUTHEND6T : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
SOTHNGTN12T : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
SOTHNGTN13T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOTHNGTN14T : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
SOTHNGTN15T : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
SOTHNGTN22T : OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SOTHNGTN25T : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN26T : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
WALLING1TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73594 [WALL LV113.800] CKT 1
WALLING2TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73195 [DEVON 115.00] CKT 1
WALLING3TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73595 [WALL LV213.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73596 [WALL LV313.800] CKT 1
WALLING4TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73595 [WALL LV213.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73596 [WALL LV313.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
WALLING5TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73594 [WALL LV113.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
WATERST1TSTK: OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
WATERST2TSTK: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
WRIVER1TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
WRIVER2TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
WOODMNT1TSTK: OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73746 [WOODMONT13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
WOODMNT2TSTK: OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73746 [WOODMONT13.800] CKT 1
OPEN LINE FROM BUS 73685 [ALLINGSB115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
318-362STKBR: OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73588 [MERIDEN121.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73589 [MERIDEN221.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73590 [MERIDEN321.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73106 [SOUTHGTN345.00] CKT 1
CARD1TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
CARD1T+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73565 [LAKERD#121.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73566 [LAKERD#221.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73567 [LAKERD#321.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
CARD2TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
CARD3TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
CARD3T+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73565 [LAKERD#121.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73566 [LAKERD#221.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73567 [LAKERD#321.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
HADNKSTBKR : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73109 [MONTVILE345.00] CKT 1
LONGMT5TSTK : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
LUDLOWSTBKR : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72929 [BELCH301345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
OPEN LINE FROM BUS 72929 [BELCH301345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
OPEN LINE FROM BUS 71797 [MILLBURY345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
MANCH21TSTK : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
MONTVSTBKR : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 2
NOMNTSTBKR : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
NMSTBKREAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
SCOVRK4TSTK : OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK5TSTK : OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73664 [NHHHVDCL345.00] TO BUS 73665 [NHHHVDCL191.50] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK7TSTK : OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK8TSTK : OPEN LINE FROM BUS 73107 [SCOVL RK345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SGTN1TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SGTN3TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SGTN4TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
SGTN5TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
SGTN6TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
SGTN7TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
NORGLENLINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
NHBRGLENLINE: OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWALKST1 : OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWALKST2 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
NORWALKST3 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR1T : OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
NORWLKHAR2T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR3T : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 2
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 3
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR4T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR7T : OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHARBT : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 2
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 3
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
GLNBRKASTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
GLNBRKA1STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
GLNBRKA2STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
GLNBRKA3STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
GLNBRKA4STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
GLNBRKBSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
GLNBRKB1STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
GLNBRKB2STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GLNBRKB3STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
GLNBRKB4STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
GLNBRKCSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
GLNBRKDSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GLNBRKESTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
DC1-BES-NOR : REMOVE MACHINE 1 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 1 FROM BUS 73293 [NORWALK 345.00]
DC2-BES-SIN : REMOVE MACHINE 2 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 2 FROM BUS 73700 [PEQUONIC115.00]
DC3-BES-DEV : REMOVE MACHINE 3 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 3 FROM BUS 73129 [E.DEVONJ115.00]
DC4-SIN-NOR : REMOVE MACHINE 4 FROM BUS 73700 [PEQUONIC115.00]
REMOVE MACHINE 4 FROM BUS 73293 [NORWALK 345.00]
DC5-DEV-NOR : REMOVE MACHINE 5 FROM BUS 73129 [E.DEVONJ115.00]
REMOVE MACHINE 5 FROM BUS 73293 [NORWALK 345.00]

## nonconverged
ACCC NON-CONVERGED NETWORK REPORT:
BUS MISMATCH TOLERANCE= 2.5000 MVA
SYSTEM MISMATCH TOLERANCE= 20.0000 MVA
DISTRIBUTION FACTOR FILE: DC-ph2-alt2-ny-ne-091503-2-upg-SCD1.dfx
SUBSYSTEM DESCRIPTION FILE: swctnew.sub
MONITORED ELEMENT FILE: swct0802.mon
CONTINGENCY DESCRIPTION FILE: contigphase2-091503-newDC.con
X--MISMATCH (MVA)--X
CONTINGENCY BUS SYSTEM TERMINATION CONDITION
1355LINE 2.3173 30.393 MET CONVERGENCE TOLERANCE
1443+1759LNS 2.2692 60.715 MET CONVERGENCE TOLERANCE
1500LINE 2.3110 32.613 MET CONVERGENCE TOLERANCE
1505LINE 2.3133 21.338 MET CONVERGENCE TOLERANCE
1605LINE 2.3112 32.602 MET CONVERGENCE TOLERANCE
1690LINE 2.3153 30.441 MET CONVERGENCE TOLERANCE
1750LINE 2.1510 57.164 MET CONVERGENCE TOLERANCE
1760+1876LNS 2.2755 34.104 MET CONVERGENCE TOLERANCE
1820LINE 2.3200 30.412 MET CONVERGENCE TOLERANCE
347LINE 2.3329 33.016 MET CONVERGENCE TOLERANCE
347LREAC 2.3329 32.939 MET CONVERGENCE TOLERANCE
387+AUTOS 2.2626 37.953 MET CONVERGENCE TOLERANCE
1100-1200DCT 2.3109 27.005 MET CONVERGENCE TOLERANCE
1163-1550D-2 2.2848 34.501 MET CONVERGENCE TOLERANCE
1280-1870DCT 2.3113 32.102 MET CONVERGENCE TOLERANCE
1310-1763DCT 2.2554 24.999 MET CONVERGENCE TOLERANCE
1394-1515DCT 2.2968 34.671 MET CONVERGENCE TOLERANCE
1470-1565DCT 2.2912 24.263 MET CONVERGENCE TOLERANCE
1505-1607DCT 2.2913 23.564 MET CONVERGENCE TOLERANCE
1560-1570DCT 2.2795 51.052 MET CONVERGENCE TOLERANCE
1570-1575DCT 2.3011 35.768 MET CONVERGENCE TOLERANCE
1580-1585DCT 2.1495 57.653 MET CONVERGENCE TOLERANCE
1640-1690DCT 2.3173 30.461 MET CONVERGENCE TOLERANCE
1670-1830DCT 2.3160 30.405 MET CONVERGENCE TOLERANCE
1770-1887DCT 2.2551 86.155 MET CONVERGENCE TOLERANCE
1800-1810DCT 2.2885 20.720 MET CONVERGENCE TOLERANCE
1800-1825DCT 2.3039 33.991 MET CONVERGENCE TOLERANCE
1460-387DCT 2.1897 35.221 MET CONVERGENCE TOLERANCE
310-383DCT 2.3009 27.171 MET CONVERGENCE TOLERANCE
BATESROCK1T 2.1533 42.757 MET CONVERGENCE TOLERANCE
BECONFLSTK 2.3162 30.465 MET CONVERGENCE TOLERANCE
BROADWYST1 2.2765 29.425 MET CONVERGENCE TOLERANCE
COLONY1T 2.3017 35.065 MET CONVERGENCE TOLERANCE
DARIEN1T 2.2588 60.574 MET CONVERGENCE TOLERANCE
EMERIDEN1T 2.1453 64.875 MET CONVERGENCE TOLERANCE
FLAXHILL2T 2.1453 67.287 MET CONVERGENCE TOLERANCE
FROSTBR15T 2.3240 23.136 MET CONVERGENCE TOLERANCE
GREENHLL2T 2.2965 23.816 MET CONVERGENCE TOLERANCE
HAWTHORNST 2.2592 85.076 MET CONVERGENCE TOLERANCE
JUNEST1 2.2626 72.350 MET CONVERGENCE TOLERANCE
MLLRVR1TSTK 2.3237 24.800 MET CONVERGENCE TOLERANCE
MIXAVE1 2.2874 26.007 MET CONVERGENCE TOLERANCE
NOHAVN1TSTK 2.1451 76.291 MET CONVERGENCE TOLERANCE
OLDTOWNST 2.2518 100.97 MET CONVERGENCE TOLERANCE
PEACEABLE1T 2.2912 24.263 MET CONVERGENCE TOLERANCE
PLUMTREE28T 2.2756 33.895 MET CONVERGENCE TOLERANCE
QUINIPACST1 2.2941 23.584 MET CONVERGENCE TOLERANCE
SACKETST1 2.3102 35.350 MET CONVERGENCE TOLERANCE
SNAUGA1T 2.1495 57.653 MET CONVERGENCE TOLERANCE
SOTHNGTN16T 2.3160 30.405 MET CONVERGENCE TOLERANCE
SOTHNGTN20T 2.3181 30.216 MET CONVERGENCE TOLERANCE
SOTHNGTN23T 2.3231 32.674 MET CONVERGENCE TOLERANCE
SOTHNGTN24T 2.2885 20.720 MET CONVERGENCE TOLERANCE
SOTHNGTN28T 2.2848 34.501 MET CONVERGENCE TOLERANCE
STEVENSNSTK 2.2914 34.079 MET CONVERGENCE TOLERANCE
STONYHILL1T 2.2551 86.155 MET CONVERGENCE TOLERANCE
TRPFALLST1 2.2624 37.664 MET CONVERGENCE TOLERANCE
TRIANGLE2T 87.165 735.16 ITERATION LIMIT EXCEEDED
TRIANGLE3T 63.455 584.50 ITERATION LIMIT EXCEEDED
TRIANGLE4T 2.3087 30.722 MET CONVERGENCE TOLERANCE
WATERSIDE2T 2.2669 42.162 MET CONVERGENCE TOLERANCE
WBROOKFLD1T 2.2790 31.875 MET CONVERGENCE TOLERANCE
WESTON1T 2.2606 82.483 MET CONVERGENCE TOLERANCE
CONTINGENCY LEGEND
LABEL EVENTS
1355LINE : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1443+1759LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1500LINE : OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73150 [FLNDRSA 115.00] CKT 1
OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73149 [WILIAMSA115.00] CKT 1
OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1505LINE : OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73223 [FRYBRT05115.00] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73236 [FRYBR05 115.00] CKT 1
OPEN LINE FROM BUS 73236 [FRYBR05 115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73476 [TRACY05 115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73270 [BROOKLYN115.00] TO BUS 73444 [BROOKLYN23.000] CKT 1
OPEN LINE FROM BUS 73475 [TRACY 23.000] TO BUS 73476 [TRACY05 115.00] CKT 1
1605LINE : OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73238 [FLANDRSB115.00] CKT 1
OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73239 [WILIAMSB115.00] CKT 1
OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1690LINE : OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73197 [HANOVERA115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1750LINE : OPEN LINE FROM BUS 73167 [SO.END 115.00] TO BUS 73144 [TOMAC 115.00] CKT 1
OPEN LINE FROM BUS 73144 [TOMAC 115.00] TO BUS 73163 [COS COB 115.00] CKT 1
1760+1876LNS: OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
1820LINE : OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
347LINE : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
347LREAC : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
387+AUTOS : OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73664 [NHHHVDCL345.00] TO BUS 73665 [NHHHVDCL191.50] CKT 1
1100-1200DCT: OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
1163-1550D-2: OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1280-1870DCT: OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73177 [MYSTICCT115.00] TO BUS 73285 [CTRI1870115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73285 [CTRI1870115.00] TO BUS 72581 [WOOD RIV115.00] CKT 1
1310-1763DCT: OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73284 [SWINDT17115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73131 [S.WNDSRA115.00] CKT 1
OPEN LINE FROM BUS 73131 [S.WNDSRA115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73221 [S.WNDSRB115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73283 [SWINDT13115.00] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73221 [S.WNDSRB115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1394-1515DCT: OPEN LINE FROM BUS 72978 [FRANCONA115.00] TO BUS 73266 [SCITICO 115.00] CKT 1
OPEN LINE FROM BUS 73266 [SCITICO 115.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
1470-1565DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73155 [RDGFLD J115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
1505-1607DCT: OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73223 [FRYBRT05115.00] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73236 [FRYBR05 115.00] CKT 1
OPEN LINE FROM BUS 73236 [FRYBR05 115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73476 [TRACY05 115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73270 [BROOKLYN115.00] TO BUS 73444 [BROOKLYN23.000] CKT 1
OPEN LINE FROM BUS 73475 [TRACY 23.000] TO BUS 73476 [TRACY05 115.00] CKT 1
OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73226 [FRYBRT07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73229 [FRY BR07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73229 [FRY BR07115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73442 [TRACY 23.000] CKT 1
1560-1570DCT: OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
1570-1575DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
1580-1585DCT: OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 2
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
1640-1690DCT: OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73197 [HANOVERA115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1670-1830DCT: OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1770-1887DCT: OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
1800-1810DCT: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1800-1825DCT: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1460-387DCT : OPEN LINE FROM BUS 73107 [SCOVL RK345.00] TO BUS 73663 [E.SHORE 345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
310-383DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
BATESROCK1T : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
BECONFLSTK : OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73228 [BALDWNJB115.00] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73387 [BEACON F13.800] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73387 [BEACON F13.800] CKT 2
BROADWYST1 : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
COLONY1T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
DARIEN1T : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
EMERIDEN1T : OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
FLAXHILL2T : OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
FROSTBR15T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
GREENHLL2T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
HAWTHORNST : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 2
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
JUNEST1 : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
MLLRVR1TSTK : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73737 [MILLRIV213.800] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73737 [MILLRIV213.800] TO BUS 73676 [MILL RVR115.00] CKT 2
MIXAVE1 : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
NOHAVN1TSTK : OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 2
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73670 [QUINNIP 115.00] CKT 1
OLDTOWNST : OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 2
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
PEACEABLE1T : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73155 [RDGFLD J115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
PLUMTREE28T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
QUINIPACST1 : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
SACKETST1 : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
SNAUGA1T : OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 2
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
SOTHNGTN16T : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOTHNGTN20T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
SOTHNGTN23T : OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN24T : OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN28T : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
STEVENSNSTK : OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
STONYHILL1T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
TRPFALLST1 : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
TRIANGLE2T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
TRIANGLE3T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
TRIANGLE4T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
OPEN LINE FROM BUS 73377 [TRIANGLA13.800] TO BUS 73383 [TRIANGLB13.800] CKT 1
WATERSIDE2T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73162 [WATERSDE115.00] TO BUS 73163 [COS COB 115.00] CKT 1
WBROOKFLD1T : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
WESTON1T : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73292 [NRWLK RX115.00] CKT 2
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73158 [WESTON 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1