## thermal
ACCC OVERLOAD REPORT: MONITORED ELEMENTS LOADED ABOVE 100.0 % OF RATING SET B
Sort This Column for Lookup | MONITORED ELEMENT | [8 empty] | CONTINGENCY | RATE | FLOW | % | Other Case | Diff
73106-73154-2-SGTN5TSTK | 73106 | * | SOUTHGTN | 345 | 73154 |  | SGTN B | 115 | 2 | SGTN5TSTK | 585 | 737 | 126 | 107.3 | 18.7
73210-73611-1-1080-1280DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080-1280DCT | 183 | 195.2 | 111.4 | 109.9 | 1.5
73210-73611-1-1070-1080DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1070-1080DCT | 183 | 194.4 | 110.8 | 109.9 | 0.9
73210-73611-1-1080-1490DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080-1490DCT | 183 | 194.4 | 110.8 | 109.9 | 0.9
73210-73611-1-1080LINE | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080LINE | 183 | 194.4 | 110.8 | 109.9 | 0.9
73167-73294-1-1440-1450DCT | 73167 | * | SO.END | 115 | 73294 |  | GLNBRK J | 115 | 1 | 1440-1450DCT | 289 | 366 | 123.3 | 123.1 | 0.2
70521-70555-1-312+393LNS | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 312+393LNS | 50 | 53.3 | 106.7 | 106.5 | 0.2
70521-70555-1-312+393REAC | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 312+393REAC | 50 | 53.3 | 106.7 | 106.5 | 0.2
70521-70555-1-312LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 312LINE | 50 | 53.3 | 106.7 | 106.5 | 0.2
70521-70555-1-NMSTBKREAC | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | NMSTBKREAC | 50 | 53.4 | 106.7 | 106.6 | 0.1
70521-70555-1-NOMNTSTBKR | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | NOMNTSTBKR | 50 | 53.4 | 106.7 | 106.6 | 0.1
73162-73163-1-SOUTHEND6T | 73162 |  | WATERSDE | 115 | 73163 | * | COS COB | 115 | 1 | SOUTHEND6T | 239 | 298.9 | 124.8 | 124.7 | 0.1
70521-70555-1-393LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 393LINE | 50 | 52.9 | 105.8 | 105.7 | 0.1
70721-70740-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70740 |  | 10-20 | 13.8 | 1 | BASE CASE | 20 | 26.1 | 130.5 | 130.5 | 0
70521-70555-1-354LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 354LINE | 50 | 53.3 | 106.6 | 106.6 | 0
70521-70555-1-381LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 381LINE | 50 | 53 | 105.9 | 105.9 | 0
70521-70555-1-381LREAC | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 381LREAC | 50 | 53 | 105.9 | 105.9 | 0
70490-70504-1-BASE CASE | 70490 | * | VERNONRD | 115 | 70504 |  | SBRAT 69 | 69 | 1 | BASE CASE | 24 | 25 | 104.2 | 104.2 | 0
70557-70714-1-BASE CASE | 70557 | * | Q CITY | 115 | 70714 |  | Q CTY 34 | 34.5 | 1 | BASE CASE | 50 | 52.1 | 104.2 | 104.2 | 0
70521-70555-1-BASE CASE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | BASE CASE | 50 | 51.9 | 103.8 | 103.8 | 0
70721-70732-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70732 |  | MCNEIL T | 34.5 | 1 | BASE CASE | 30 | 29.9 | 102.5 | 102.5 | 0
73162-73168-1-SOUTHEND6T | 73162 | * | WATERSDE | 115 | 73168 |  | GLNBROOK | 115 | 1 | SOUTHEND6T | 352 | 367 | 102.4 | 102.4 | 0
70512-70719-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 50.2 | 100.4 | 100.4 | 0
73680-73681-1-GRNDAV2TSTK | 73680 | * | WATER ST | 115 | 73681 |  | WEST RIV | 115 | 1 | GRNDAV2TSTK | 273 | 283.1 | 100.4 | 100.5 | -0.1
73339-73340-1-1625LINE | 73339 |  | BARBR HL | 69 | 73340 | * | ROCKVILL | 69 | 1 | 1625LINE | 84 | 91.2 | 114.5 | 114.8 | -0.3
73251-73261-1-1207-1775DCT | 73251 |  | BLM JCT | 115 | 73261 | * | NW.HTFD | 115 | 1 | 1207-1775DCT | 228 | 252.5 | 113.7 | 114 | -0.3
73170-73176-1-1165LINE | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | 1165LINE | 138 | 144.8 | 103.9 | 104.2 | -0.3
73244-73258-1-1207-1775DCT | 73258 | * | BLOOMFLD | 115 | 73244 |  | N.BLMFLD | 115 | 1 | 1207-1775DCT | 193 | 221.9 | 117.7 | 118.3 | -0.6
73214-73215-1-CARD2TSTK | 73214 |  | WAWECS J | 115 | 73215 | * | CARD | 115 | 1 | CARD2TSTK | 181 | 187.2 | 104 | 104.8 | -0.8
73176-73268-1-1060-1165DCT | 73176 | * | TRIANGLE | 115 | 73268 |  | MIDDLRIV | 115 | 1 | 1060-1165DCT | 134 | 147.3 | 110.9 | 111.8 | -0.9
73170-73176-2-1060-1270DCT | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 2 | 1060-1270DCT | 166 | 224.7 | 134 | 134.9 | -0.9
73170-73268-1-1060-1165DCT | 73170 |  | PLUMTREE | 115 | 73268 | * | MIDDLRIV | 115 | 1 | 1060-1165DCT | 126 | 226.4 | 180 | 181.4 | -1.4
73188-73192-1-BUNKERH2T | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | BUNKERH2T | 112 | 109.7 | 103.4 | 105.9 | -2.5
73188-73192-1-1272-1721DCT | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | 1272-1721DCT | 112 | 131.4 | 126.9 | 129.7 | -2.8
73669-73681-1-GRNDAV2TSTK | 73669 |  | GRAND AV | 115 | 73681 | * | WEST RIV | 115 | 1 | GRNDAV2TSTK | 258 | 271.7 | 101.7 | 105.2 | -3.5
73669-73681-2-GRNDAV2TSTK | 73669 |  | GRAND AV | 115 | 73681 | * | WEST RIV | 115 | 2 | GRNDAV2TSTK | 258 | 271.7 | 101.7 | 105.2 | -3.5
73170-73176-1-PLUMTREE31T | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | PLUMTREE31T | 138 | 139.7 | 99.8 | 100.5 | -0.7
73144-73167-1-1440-1450DCT | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440-1450DCT | 252 | 255.5 | 99.3 | 99.3 | 0
73144-73167-1-1440LINE | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440LINE | 252 | 256.1 | 99.2 | 98.8 | 0.4
73144-73167-1-GLNBRKA2STK | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLNBRKA2STK | 252 | 255.6 | 99.2 | 99.2 | 0
73144-73167-1-GLENBROOK3T | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLENBROOK3T | 252 | 255.5 | 98.9 | 98.8 | 0.1
73144-73167-1-GLNBRKCSTK | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLNBRKCSTK | 252 | 255.5 | 98.9 | 98.8 | 0.1
73227-73633-1-SGTN7TSTK | 73227 | * | E.MERIDN | 115 | 73633 |  | NO.WALLF | 115 | 1 | SGTN7TSTK | 112 | 112.3 | 98.7 | 98.6 | 0.1
70512-70735-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70735 |  | WILL #2 | 34.5 | 1 | BASE CASE | 50 | 48.7 | 97.5 | 97.5 | 0
70712-70719-1-BASE CASE | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 48.6 | 96.1 | 96.1 | 0
73225-73700-2-113091001DCT | 73225 | * | TRMB J B | 115 | 73700 |  | PEQUONIC | 115 | 2 | 113091001DCT | 231 | 229.8 | 96.1 | #N/A | 1.1
73651-73668-1-WOODMNT1TSTK | 73651 | * | NH HARBR | 22 | 73668 |  | E.SHORE | 115 | 1 | WOODMNT1TSTK | 475 | 454.9 | 95.8 | 96.4 | -0.6
73651-73668-1-WOODMNT2TSTK | 73651 | * | NH HARBR | 22 | 73668 |  | E.SHORE | 115 | 1 | WOODMNT2TSTK | 475 | 453.2 | 95.4 | 96.6 | -1.2
73107-73116-1-BASE CASE | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | BASE CASE | 436 | 428.4 | 95.2 | 95.4 | -0.2

## voltage
MONITORED VOLTAGE REPORT
Sort This Column for Lookup | SYSTEM |  | CONTINGENCY | BUS |  |  | V-CONT | V-INIT | V-MAX | V-MIN | Other Case | Diff
70622-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70622 | WHITE RV | 13.8 | 1.0547 | 1.0547 | 1.05 | 0.9 | 1.0548 | -0.0001
70625-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70625 | WTRFORD | 34.5 | 1.0587 | 1.0587 | 1.05 | 0.9 | 1.0587 | 0
70626-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70626 | GILMAN | 34.5 | 1.0603 | 1.0603 | 1.05 | 0.9 | 1.0603 | 0
70639-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70639 | HGATE VL | 46 | 1.0554 | 1.0554 | 1.05 | 0.9 | 1.0554 | 0
70640-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70640 | MISSQ P | 48 | 1.0554 | 1.0554 | 1.05 | 0.9 | 1.0554 | 0
70693-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70693 | ESX-STAT | 3.2 | 1.0607 | 1.0607 | 1.05 | 0.9 | 1.0608 | -0.0001
73388-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73388 | SO.NAUG | 13.8 | 1.0542 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0042
73657-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73657 | ENGLISH7 | 13.8 | 1.0566 | 1.0566 | 1.05 | 0.9 | 1.0506 | 0.006
73658-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73658 | ENGLISH8 | 13.8 | 1.0566 | 1.0566 | 1.05 | 0.9 | 1.0506 | 0.006
73665-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73665 | NHHHVDCL | 192 | 1.0593 | 1.0593 | 1.05 | 0.9 | 1.0548 | 0.0045
73700-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73700 | PEQUONIC | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73716-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73716 | PEQBETAP | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73729-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73729 | ENGLISH | 13.8 | 1.0566 | 1.0566 | 1.05 | 0.9 | 1.0506 | 0.006
73270-1080LINE | ZONE 171 | RANGE | 1080LINE | 73270 | BROOKLYN | 115 | 0.8907 | 0.9497 | 1.05 | 0.9 | 0.8976 | -0.0069
73476-1080LINE | ZONE 171 | RANGE | 1080LINE | 73476 | TRACY05 | 115 | 0.8849 | 0.9446 | 1.05 | 0.9 | 0.892 | -0.0071
73665-1342LINE | ZONE 185 | RANGE | 1342LINE | 73665 | NHHHVDCL | 192 | 1.0566 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0066
73657-1508LINE | ZONE 185 | RANGE | 1508LINE | 73657 | ENGLISH7 | 13.8 | 1.0612 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0112
73658-1508LINE | ZONE 185 | RANGE | 1508LINE | 73658 | ENGLISH8 | 13.8 | 1.0612 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0112
73665-1508LINE | ZONE 185 | RANGE | 1508LINE | 73665 | NHHHVDCL | 192 | 1.0622 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0122
73729-1508LINE | ZONE 185 | RANGE | 1508LINE | 73729 | ENGLISH | 13.8 | 1.0612 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0112
73388-1570LINE | ZONE 171 | RANGE | 1570LINE | 73388 | SO.NAUG | 13.8 | 1.051 | 1.0542 | 1.05 | 0.9 | #N/A | 0.001
73388-1575LINE | ZONE 171 | RANGE | 1575LINE | 73388 | SO.NAUG | 13.8 | 1.0576 | 1.0542 | 1.05 | 0.9 | 1.0505 | 0.0071
73161-1625LINE | ZONE 171 | RANGE | 1625LINE | 73161 | ROCKVILL | 115 | 0.8352 | 0.9848 | 1.05 | 0.9 | 0.8329 | 0.0023
73657-1630LINE | ZONE 185 | RANGE | 1630LINE | 73657 | ENGLISH7 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73658-1630LINE | ZONE 185 | RANGE | 1630LINE | 73658 | ENGLISH8 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73671-1630LINE | ZONE 185 | RANGE | 1630LINE | 73671 | NO.HAVEN | 115 | 1.0504 | 1.039 | 1.05 | 0.9 | #N/A | 0.0004
73729-1630LINE | ZONE 185 | RANGE | 1630LINE | 73729 | ENGLISH | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73388-1721LINE | ZONE 171 | RANGE | 1721LINE | 73388 | SO.NAUG | 13.8 | 1.0511 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0011
73388-1730CLINE | ZONE 171 | RANGE | 1730CLINE | 73388 | SO.NAUG | 13.8 | 1.0514 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0014
73267-1977LINENEW | ZONE 171 | RANGE | 1977LINENEW | 73267 | DARIEN | 115 | 1.0658 | 1.0375 | 1.05 | 0.9 | #N/A | 0.0158
73286-1977LINENEW | ZONE 171 | RANGE | 1977LINENEW | 73286 | COMPO | 115 | 1.0559 | 1.0385 | 1.05 | 0.9 | #N/A | 0.0059
73300-1977LINENEW | ZONE 171 | RANGE | 1977LINENEW | 73300 | ELYTAP | 115 | 1.0615 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0115
73657-8809ALINE-1 | ZONE 185 | RANGE | 8809ALINE-1 | 73657 | ENGLISH7 | 13.8 | 1.0525 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0025
73658-8809ALINE-1 | ZONE 185 | RANGE | 8809ALINE-1 | 73658 | ENGLISH8 | 13.8 | 1.0525 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0025
73665-8809ALINE-1 | ZONE 185 | RANGE | 8809ALINE-1 | 73665 | NHHHVDCL | 192 | 1.0568 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0068
73729-8809ALINE-1 | ZONE 185 | RANGE | 8809ALINE-1 | 73729 | ENGLISH | 13.8 | 1.0525 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0025
73657-8809ALINE-2 | ZONE 185 | RANGE | 8809ALINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0532 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0032
73658-8809ALINE-2 | ZONE 185 | RANGE | 8809ALINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0532 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0032
73729-8809ALINE-2 | ZONE 185 | RANGE | 8809ALINE-2 | 73729 | ENGLISH | 13.8 | 1.0532 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0032
73657-8909BLINE-1 | ZONE 185 | RANGE | 8909BLINE-1 | 73657 | ENGLISH7 | 13.8 | 1.0525 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0025
73658-8909BLINE-1 | ZONE 185 | RANGE | 8909BLINE-1 | 73658 | ENGLISH8 | 13.8 | 1.0525 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0025
73665-8909BLINE-1 | ZONE 185 | RANGE | 8909BLINE-1 | 73665 | NHHHVDCL | 192 | 1.0568 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0068
73729-8909BLINE-1 | ZONE 185 | RANGE | 8909BLINE-1 | 73729 | ENGLISH | 13.8 | 1.0525 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0025
73657-8909BLINE-2 | ZONE 185 | RANGE | 8909BLINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0532 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0032
73658-8909BLINE-2 | ZONE 185 | RANGE | 8909BLINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0532 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0032
73729-8909BLINE-2 | ZONE 185 | RANGE | 8909BLINE-2 | 73729 | ENGLISH | 13.8 | 1.0532 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0032
73657-84004LINE | ZONE 185 | RANGE | 84004LINE | 73657 | ENGLISH7 | 13.8 | 1.0605 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0105
73658-84004LINE | ZONE 185 | RANGE | 84004LINE | 73658 | ENGLISH8 | 13.8 | 1.0605 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0105
73665-84004LINE | ZONE 185 | RANGE | 84004LINE | 73665 | NHHHVDCL | 192 | 1.0621 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0121
73672-84004LINE | ZONE 185 | RANGE | 84004LINE | 73672 | SACKETT | 115 | 1.0507 | 1.0406 | 1.05 | 0.9 | #N/A | 0.0007
73729-84004LINE | ZONE 185 | RANGE | 84004LINE | 73729 | ENGLISH | 13.8 | 1.0605 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0105
73657-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73657 | ENGLISH7 | 13.8 | 1.053 | 1.0566 | 1.05 | 0.9 | #N/A | 0.003
73658-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73658 | ENGLISH8 | 13.8 | 1.053 | 1.0566 | 1.05 | 0.9 | #N/A | 0.003
73729-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73729 | ENGLISH | 13.8 | 1.053 | 1.0566 | 1.05 | 0.9 | #N/A | 0.003
73657-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73657 | ENGLISH7 | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73658-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73658 | ENGLISH8 | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73665-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73665 | NHHHVDCL | 192 | 1.0565 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0065
73729-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73729 | ENGLISH | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73657-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0536 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0036
73658-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0536 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0036
73729-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73729 | ENGLISH | 13.8 | 1.0536 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0036
73657-88006ALINE | ZONE 185 | RANGE | 88006ALINE | 73657 | ENGLISH7 | 13.8 | 1.0522 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0022
73658-88006ALINE | ZONE 185 | RANGE | 88006ALINE | 73658 | ENGLISH8 | 13.8 | 1.0522 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0022
73665-88006ALINE | ZONE 185 | RANGE | 88006ALINE | 73665 | NHHHVDCL | 192 | 1.0566 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0066
73729-88006ALINE | ZONE 185 | RANGE | 88006ALINE | 73729 | ENGLISH | 13.8 | 1.0522 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0022
73657-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73657 | ENGLISH7 | 13.8 | 1.0529 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0029
73658-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73658 | ENGLISH8 | 13.8 | 1.0529 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0029
73729-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73729 | ENGLISH | 13.8 | 1.0529 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0029
73657-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73657 | ENGLISH7 | 13.8 | 1.0538 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0038
73658-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73658 | ENGLISH8 | 13.8 | 1.0538 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0038
73729-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73729 | ENGLISH | 13.8 | 1.0538 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0038
73657-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0536 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0036
73658-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0536 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0036
73729-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73729 | ENGLISH | 13.8 | 1.0536 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0036
73657-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73657 | ENGLISH7 | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73658-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73658 | ENGLISH8 | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73665-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73665 | NHHHVDCL | 192 | 1.0559 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0059
73729-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73729 | ENGLISH | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73657-89006BLINE-1 | ZONE 185 | RANGE | 89006BLINE-1 | 73657 | ENGLISH7 | 13.8 | 1.0521 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0021
73658-89006BLINE-1 | ZONE 185 | RANGE | 89006BLINE-1 | 73658 | ENGLISH8 | 13.8 | 1.0521 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0021
73665-89006BLINE-1 | ZONE 185 | RANGE | 89006BLINE-1 | 73665 | NHHHVDCL | 192 | 1.0566 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0066
73729-89006BLINE-1 | ZONE 185 | RANGE | 89006BLINE-1 | 73729 | ENGLISH | 13.8 | 1.0521 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0021
73125-EDEVDEV1 | ZONE 171 | RANGE | EDEVDEV1 | 73125 | MILFORD | 115 | 1.0501 | 1.0429 | 1.05 | 0.9 | #N/A | 0.0001
73129-EDEVDEV1 | ZONE 171 | RANGE | EDEVDEV1 | 73129 | E.DEVONJ | 115 | 1.0505 | 1.0433 | 1.05 | 0.9 | #N/A | 0.0005
73388-EDEVDEV1 | ZONE 171 | RANGE | EDEVDEV1 | 73388 | SO.NAUG | 13.8 | 1.0569 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0069
73575-EDEVDEV1 | ZONE 171 | RANGE | EDEVDEV1 | 73575 | MILFD#2 | 13.8 | 1.0501 | 1.0429 | 1.05 | 0.9 | #N/A | 0.0001
73657-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73657 | ENGLISH7 | 13.8 | 1.0539 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0039
73658-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73658 | ENGLISH8 | 13.8 | 1.0539 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0039
73729-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73729 | ENGLISH | 13.8 | 1.0539 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0039
73129-EDEVDEV2 | ZONE 171 | RANGE | EDEVDEV2 | 73129 | E.DEVONJ | 115 | 1.0501 | 1.0433 | 1.05 | 0.9 | #N/A | 0.0001
73657-EDEVDEV2 | ZONE 185 | RANGE | EDEVDEV2 | 73657 | ENGLISH7 | 13.8 | 1.0602 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0102
73658-EDEVDEV2 | ZONE 185 | RANGE | EDEVDEV2 | 73658 | ENGLISH8 | 13.8 | 1.0602 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0102
73665-EDEVDEV2 | ZONE 185 | RANGE | EDEVDEV2 | 73665 | NHHHVDCL | 192 | 1.0623 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0123
73729-EDEVDEV2 | ZONE 185 | RANGE | EDEVDEV2 | 73729 | ENGLISH | 13.8 | 1.0602 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0102
70622-312LINE | ZONE 41 | RANGE | 312LINE | 70622 | WHITE RV | 13.8 | 1.0515 | 1.0547 | 1.05 | 0.9 | 1.0519 | -0.0004
70693-312LINE | ZONE 41 | RANGE | 312LINE | 70693 | ESX-STAT | 3.2 | 1.0577 | 1.0607 | 1.05 | 0.9 | 1.0576 | 0.0001
73388-312LINE | ZONE 171 | RANGE | 312LINE | 73388 | SO.NAUG | 13.8 | 1.0517 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0017
73657-312LINE | ZONE 185 | RANGE | 312LINE | 73657 | ENGLISH7 | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73658-312LINE | ZONE 185 | RANGE | 312LINE | 73658 | ENGLISH8 | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73665-312LINE | ZONE 185 | RANGE | 312LINE | 73665 | NHHHVDCL | 192 | 1.0545 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0045
73729-312LINE | ZONE 185 | RANGE | 312LINE | 73729 | ENGLISH | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
70622-312+393LNS | ZONE 41 | RANGE | 312+393LNS | 70622 | WHITE RV | 13.8 | 1.0515 | 1.0547 | 1.05 | 0.9 | 1.0519 | -0.0004
70693-312+393LNS | ZONE 41 | RANGE | 312+393LNS | 70693 | ESX-STAT | 3.2 | 1.0577 | 1.0607 | 1.05 | 0.9 | 1.0576 | 0.0001
73388-312+393LNS | ZONE 171 | RANGE | 312+393LNS | 73388 | SO.NAUG | 13.8 | 1.0517 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0017
73657-312+393LNS | ZONE 185 | RANGE | 312+393LNS | 73657 | ENGLISH7 | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73658-312+393LNS | ZONE 185 | RANGE | 312+393LNS | 73658 | ENGLISH8 | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73665-312+393LNS | ZONE 185 | RANGE | 312+393LNS | 73665 | NHHHVDCL | 192 | 1.0545 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0045
73729-312+393LNS | ZONE 185 | RANGE | 312+393LNS | 73729 | ENGLISH | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
70622-312+393REAC | ZONE 41 | RANGE | 312+393REAC | 70622 | WHITE RV | 13.8 | 1.0515 | 1.0547 | 1.05 | 0.9 | 1.0519 | -0.0004
70693-312+393REAC | ZONE 41 | RANGE | 312+393REAC | 70693 | ESX-STAT | 3.2 | 1.0577 | 1.0607 | 1.05 | 0.9 | 1.0577 | 0
73388-312+393REAC | ZONE 171 | RANGE | 312+393REAC | 73388 | SO.NAUG | 13.8 | 1.0517 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0017
73657-312+393REAC | ZONE 185 | RANGE | 312+393REAC | 73657 | ENGLISH7 | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73658-312+393REAC | ZONE 185 | RANGE | 312+393REAC | 73658 | ENGLISH8 | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73665-312+393REAC | ZONE 185 | RANGE | 312+393REAC | 73665 | NHHHVDCL | 192 | 1.0545 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0045
73729-312+393REAC | ZONE 185 | RANGE | 312+393REAC | 73729 | ENGLISH | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73388-318LINE | ZONE 171 | RANGE | 318LINE | 73388 | SO.NAUG | 13.8 | 1.0506 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0006
73657-318LINE | ZONE 185 | RANGE | 318LINE | 73657 | ENGLISH7 | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73658-318LINE | ZONE 185 | RANGE | 318LINE | 73658 | ENGLISH8 | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73665-318LINE | ZONE 185 | RANGE | 318LINE | 73665 | NHHHVDCL | 192 | 1.0527 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0027
73729-318LINE | ZONE 185 | RANGE | 318LINE | 73729 | ENGLISH | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73293-321LINE | '345KV ' | RANGE | 321LINE | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.95 | #N/A | 0
73293-321LINE | ZONE 171 | RANGE | 321LINE | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.9 | #N/A | 0
73388-321LINE | ZONE 171 | RANGE | 321LINE | 73388 | SO.NAUG | 13.8 | 1.0502 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0002
73657-321LINE | ZONE 185 | RANGE | 321LINE | 73657 | ENGLISH7 | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73658-321LINE | ZONE 185 | RANGE | 321LINE | 73658 | ENGLISH8 | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73665-321LINE | ZONE 185 | RANGE | 321LINE | 73665 | NHHHVDCL | 192 | 1.0544 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0044
73729-321LINE | ZONE 185 | RANGE | 321LINE | 73729 | ENGLISH | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73657-329LINE | ZONE 185 | RANGE | 329LINE | 73657 | ENGLISH7 | 13.8 | 1.0513 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0013
73658-329LINE | ZONE 185 | RANGE | 329LINE | 73658 | ENGLISH8 | 13.8 | 1.0513 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0013
73665-329LINE | ZONE 185 | RANGE | 329LINE | 73665 | NHHHVDCL | 192 | 1.0539 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0039
73729-329LINE | ZONE 185 | RANGE | 329LINE | 73729 | ENGLISH | 13.8 | 1.0513 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0013
70622-330LINE | ZONE 41 | RANGE | 330LINE | 70622 | WHITE RV | 13.8 | 1.0504 | 1.0547 | 1.05 | 0.9 | 1.0503 | 0.0001
70693-330+LAKE | ZONE 41 | RANGE | 330+LAKE | 70693 | ESX-STAT | 3.2 | 1.067 | 1.0607 | 1.05 | 0.9 | 1.0665 | 0.0005
73657-330+LAKE | ZONE 185 | RANGE | 330+LAKE | 73657 | ENGLISH7 | 13.8 | 1.0594 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0094
73658-330+LAKE | ZONE 185 | RANGE | 330+LAKE | 73658 | ENGLISH8 | 13.8 | 1.0594 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0094
73665-330+LAKE | ZONE 185 | RANGE | 330+LAKE | 73665 | NHHHVDCL | 192 | 1.063 | 1.0593 | 1.05 | 0.9 | #N/A | 0.013
73729-330+LAKE | ZONE 185 | RANGE | 330+LAKE | 73729 | ENGLISH | 13.8 | 1.0594 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0094
70693-347+LAKE | ZONE 41 | RANGE | 347+LAKE | 70693 | ESX-STAT | 3.2 | 1.067 | 1.0607 | 1.05 | 0.9 | 1.0665 | 0.0005
73657-347+LAKE | ZONE 185 | RANGE | 347+LAKE | 73657 | ENGLISH7 | 13.8 | 1.0594 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0094
73658-347+LAKE | ZONE 185 | RANGE | 347+LAKE | 73658 | ENGLISH8 | 13.8 | 1.0594 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0094
73665-347+LAKE | ZONE 185 | RANGE | 347+LAKE | 73665 | NHHHVDCL | 192 | 1.0631 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0131
73729-347+LAKE | ZONE 185 | RANGE | 347+LAKE | 73729 | ENGLISH | 13.8 | 1.0594 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0094
73657-348LINE | ZONE 185 | RANGE | 348LINE | 73657 | ENGLISH7 | 13.8 | 1.0518 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0018
73658-348LINE | ZONE 185 | RANGE | 348LINE | 73658 | ENGLISH8 | 13.8 | 1.0518 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0018
73665-348LINE | ZONE 185 | RANGE | 348LINE | 73665 | NHHHVDCL | 192 | 1.0531 | 1.0593 | 1.05 | 0.9 | 1.0516 | 0.0015
73729-348LINE | ZONE 185 | RANGE | 348LINE | 73729 | ENGLISH | 13.8 | 1.0518 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0018
73657-348NLINE | ZONE 185 | RANGE | 348NLINE | 73657 | ENGLISH7 | 13.8 | 1.0532 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0032
73658-348NLINE | ZONE 185 | RANGE | 348NLINE | 73658 | ENGLISH8 | 13.8 | 1.0532 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0032
73665-348NLINE | ZONE 185 | RANGE | 348NLINE | 73665 | NHHHVDCL | 192 | 1.0554 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0054
73729-348NLINE | ZONE 185 | RANGE | 348NLINE | 73729 | ENGLISH | 13.8 | 1.0532 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0032
73657-348N+AUTO | ZONE 185 | RANGE | 348N+AUTO | 73657 | ENGLISH7 | 13.8 | 1.0538 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0038
73658-348N+AUTO | ZONE 185 | RANGE | 348N+AUTO | 73658 | ENGLISH8 | 13.8 | 1.0538 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0038
73665-348N+AUTO | ZONE 185 | RANGE | 348N+AUTO | 73665 | NHHHVDCL | 192 | 1.0555 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0055
73729-348N+AUTO | ZONE 185 | RANGE | 348N+AUTO | 73729 | ENGLISH | 13.8 | 1.0538 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0038
73388-352+AUTO | ZONE 171 | RANGE | 352+AUTO | 73388 | SO.NAUG | 13.8 | 1.0614 | 1.0542 | 1.05 | 0.9 | 1.0525 | 0.0089
73657-352+AUTO | ZONE 185 | RANGE | 352+AUTO | 73657 | ENGLISH7 | 13.8 | 1.0514 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0014
73658-352+AUTO | ZONE 185 | RANGE | 352+AUTO | 73658 | ENGLISH8 | 13.8 | 1.0514 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0014
73665-352+AUTO | ZONE 185 | RANGE | 352+AUTO | 73665 | NHHHVDCL | 192 | 1.054 | 1.0593 | 1.05 | 0.9 | #N/A | 0.004
73729-352+AUTO | ZONE 185 | RANGE | 352+AUTO | 73729 | ENGLISH | 13.8 | 1.0514 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0014
73665-353LINE | ZONE 185 | RANGE | 353LINE | 73665 | NHHHVDCL | 192 | 1.062 | 1.0593 | 1.05 | 0.9 | #N/A | 0.012
73665-353+AUTO | ZONE 185 | RANGE | 353+AUTO | 73665 | NHHHVDCL | 192 | 1.0619 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0119
70693-384LINE | ZONE 41 | RANGE | 384LINE | 70693 | ESX-STAT | 3.2 | 1.0638 | 1.0607 | 1.05 | 0.9 | 1.0637 | 0.0001
73665-384LINE | ZONE 185 | RANGE | 384LINE | 73665 | NHHHVDCL | 192 | 1.0558 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0058
73388-387+AUTOS | ZONE 171 | RANGE | 387+AUTOS | 73388 | SO.NAUG | 13.8 | 1.0503 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0003
73657-387+AUTOS | ZONE 185 | RANGE | 387+AUTOS | 73657 | ENGLISH7 | 13.8 | 1.0535 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0035
73658-387+AUTOS | ZONE 185 | RANGE | 387+AUTOS | 73658 | ENGLISH8 | 13.8 | 1.0535 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0035
73729-387+AUTOS | ZONE 185 | RANGE | 387+AUTOS | 73729 | ENGLISH | 13.8 | 1.0535 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0035
70693-393LINE | ZONE 41 | RANGE | 393LINE | 70693 | ESX-STAT | 3.2 | 1.0575 | 1.0607 | 1.05 | 0.9 | 1.0576 | -0.0001
73657-393LINE | ZONE 185 | RANGE | 393LINE | 73657 | ENGLISH7 | 13.8 | 1.053 | 1.0566 | 1.05 | 0.9 | #N/A | 0.003
73658-393LINE | ZONE 185 | RANGE | 393LINE | 73658 | ENGLISH8 | 13.8 | 1.053 | 1.0566 | 1.05 | 0.9 | #N/A | 0.003
73665-393LINE | ZONE 185 | RANGE | 393LINE | 73665 | NHHHVDCL | 192 | 1.0553 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0053
73729-393LINE | ZONE 185 | RANGE | 393LINE | 73729 | ENGLISH | 13.8 | 1.053 | 1.0566 | 1.05 | 0.9 | #N/A | 0.003
73665-395LINE | ZONE 185 | RANGE | 395LINE | 73665 | NHHHVDCL | 192 | 1.0619 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0119
73665-395+AUTO | ZONE 185 | RANGE | 395+AUTO | 73665 | NHHHVDCL | 192 | 1.0619 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0119
73388-398LINE | ZONE 171 | RANGE | 398LINE | 73388 | SO.NAUG | 13.8 | 1.0569 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0069
73388-398LREAC | ZONE 171 | RANGE | 398LREAC | 73388 | SO.NAUG | 13.8 | 1.0569 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0069
73293-PLUMNOR | '345KV ' | RANGE | PLUMNOR | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.95 | #N/A | 0
73293-PLUMNOR | ZONE 171 | RANGE | PLUMNOR | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.9 | #N/A | 0
73270-1070-1080DCT | ZONE 171 | RANGE | 1070-1080DCT | 73270 | BROOKLYN | 115 | 0.8909 | 0.9497 | 1.05 | 0.9 | 0.8979 | -0.007
73476-1070-1080DCT | ZONE 171 | RANGE | 1070-1080DCT | 73476 | TRACY05 | 115 | 0.8851 | 0.9446 | 1.05 | 0.9 | 0.8922 | -0.0071
73270-1080-1280DCT | ZONE 171 | RANGE | 1080-1280DCT | 73270 | BROOKLYN | 115 | 0.8881 | 0.9497 | 1.05 | 0.9 | 0.8963 | -0.0082
73476-1080-1280DCT | ZONE 171 | RANGE | 1080-1280DCT | 73476 | TRACY05 | 115 | 0.8823 | 0.9446 | 1.05 | 0.9 | 0.8906 | -0.0083
73270-1080-1490DCT | ZONE 171 | RANGE | 1080-1490DCT | 73270 | BROOKLYN | 115 | 0.8909 | 0.9497 | 1.05 | 0.9 | 0.8979 | -0.007
73476-1080-1490DCT | ZONE 171 | RANGE | 1080-1490DCT | 73476 | TRACY05 | 115 | 0.8851 | 0.9446 | 1.05 | 0.9 | 0.8922 | -0.0071
73388-1130-1430DCT | ZONE 171 | RANGE | 1130-1430DCT | 73388 | SO.NAUG | 13.8 | 1.0505 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0005
73665-1130-1430DCT | ZONE 185 | RANGE | 1130-1430DCT | 73665 | NHHHVDCL | 192 | 1.062 | 1.0593 | 1.05 | 0.9 | #N/A | 0.012
73665-113091001DCT | ZONE 185 | RANGE | 113091001DCT | 73665 | NHHHVDCL | 192 | 1.0621 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0121
73388-1163-1550D-2 | ZONE 171 | RANGE | 1163-1550D-2 | 73388 | SO.NAUG | 13.8 | 1.0571 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0071
73657-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73657 | ENGLISH7 | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73658-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73658 | ENGLISH8 | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73665-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73665 | NHHHVDCL | 192 | 1.0541 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0041
73729-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73729 | ENGLISH | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73160-1272-1721DCT | ZONE 171 | RANGE | 1272-1721DCT | 73160 | BALDWINB | 115 | 0.896 | 1.0117 | 1.05 | 0.9 | 0.88 | 0.016
73185-1272-1721DCT | ZONE 171 | RANGE | 1272-1721DCT | 73185 | BUNKER H | 115 | 0.8963 | 1.0198 | 1.05 | 0.9 | 0.8803 | 0.016
73189-1272-1721DCT | ZONE 171 | RANGE | 1272-1721DCT | 73189 | FREIGHT | 115 | 0.8948 | 1.0209 | 1.05 | 0.9 | 0.8787 | 0.0161
73657-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73657 | ENGLISH7 | 13.8 | 1.0519 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0019
73658-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73658 | ENGLISH8 | 13.8 | 1.0519 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0019
73665-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73665 | NHHHVDCL | 192 | 1.0556 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0056
73729-1272-1721DCT | ZONE 185 | RANGE | 1272-1721DCT | 73729 | ENGLISH | 13.8 | 1.0519 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0019
73388-1416-1890DCT | ZONE 171 | RANGE | 1416-1890DCT | 73388 | SO.NAUG | 13.8 | 1.0507 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0007
73665-1416-1890DCT | ZONE 185 | RANGE | 1416-1890DCT | 73665 | NHHHVDCL | 192 | 1.0619 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0119
73129-1545-1570DCT | ZONE 171 | RANGE | 1545-1570DCT | 73129 | E.DEVONJ | 115 | 1.05 | 1.0433 | 1.05 | 0.9 | #N/A | 0
73657-1545-1570DCT | ZONE 185 | RANGE | 1545-1570DCT | 73657 | ENGLISH7 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73658-1545-1570DCT | ZONE 185 | RANGE | 1545-1570DCT | 73658 | ENGLISH8 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73729-1545-1570DCT | ZONE 185 | RANGE | 1545-1570DCT | 73729 | ENGLISH | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73388-1570-1575DCT | ZONE 171 | RANGE | 1570-1575DCT | 73388 | SO.NAUG | 13.8 | 1.0588 | 1.0542 | 1.05 | 0.9 | 1.0511 | 0.0077
73267-1867-1977DCT | ZONE 171 | RANGE | 1867-1977DCT | 73267 | DARIEN | 115 | 1.0658 | 1.0375 | 1.05 | 0.9 | #N/A | 0.0158
73286-1867-1977DCT | ZONE 171 | RANGE | 1867-1977DCT | 73286 | COMPO | 115 | 1.0559 | 1.0385 | 1.05 | 0.9 | #N/A | 0.0059
73300-1867-1977DCT | ZONE 171 | RANGE | 1867-1977DCT | 73300 | ELYTAP | 115 | 1.0615 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0115
73267-1880-1977DCT | ZONE 171 | RANGE | 1880-1977DCT | 73267 | DARIEN | 115 | 1.0658 | 1.0375 | 1.05 | 0.9 | #N/A | 0.0158
73286-1880-1977DCT | ZONE 171 | RANGE | 1880-1977DCT | 73286 | COMPO | 115 | 1.0559 | 1.0385 | 1.05 | 0.9 | #N/A | 0.0059
73300-1880-1977DCT | ZONE 171 | RANGE | 1880-1977DCT | 73300 | ELYTAP | 115 | 1.0615 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0115
73267-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73267 | DARIEN | 115 | 1.0658 | 1.0375 | 1.05 | 0.9 | #N/A | 0.0158
73286-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73286 | COMPO | 115 | 1.0559 | 1.0385 | 1.05 | 0.9 | #N/A | 0.0059
73300-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73300 | ELYTAP | 115 | 1.0615 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0115
73388-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73388 | SO.NAUG | 13.8 | 1.0516 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0016
73388-1460-387DCT | ZONE 171 | RANGE | 1460-387DCT | 73388 | SO.NAUG | 13.8 | 1.0505 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0005
73293-1565-PLNRDCT | '345KV ' | RANGE | 1565-PLNRDCT | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.95 | #N/A | 0
73293-1565-PLNRDCT | ZONE 171 | RANGE | 1565-PLNRDCT | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.9 | #N/A | 0
73657-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73657 | ENGLISH7 | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73658-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73658 | ENGLISH8 | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73665-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73665 | NHHHVDCL | 192 | 1.0542 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0042
73729-1618-321DCT | ZONE 185 | RANGE | 1618-321DCT | 73729 | ENGLISH | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73665-1767-353DCT | ZONE 185 | RANGE | 1767-353DCT | 73665 | NHHHVDCL | 192 | 1.062 | 1.0593 | 1.05 | 0.9 | #N/A | 0.012
73293-1770-321DCT | '345KV ' | RANGE | 1770-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.95 | #N/A | 0
73293-1770-321DCT | ZONE 171 | RANGE | 1770-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.9 | #N/A | 0
73657-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73657 | ENGLISH7 | 13.8 | 1.0524 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0024
73658-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73658 | ENGLISH8 | 13.8 | 1.0524 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0024
73665-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73665 | NHHHVDCL | 192 | 1.0549 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0049
73729-1770-321DCT | ZONE 185 | RANGE | 1770-321DCT | 73729 | ENGLISH | 13.8 | 1.0524 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0024
73665-1779-395DCT | ZONE 185 | RANGE | 1779-395DCT | 73665 | NHHHVDCL | 192 | 1.0619 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0119
73293-1887-321DCT | '345KV ' | RANGE | 1887-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.95 | #N/A | 0
73293-1887-321DCT | ZONE 171 | RANGE | 1887-321DCT | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.9 | #N/A | 0
73657-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73657 | ENGLISH7 | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73658-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73658 | ENGLISH8 | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73665-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73665 | NHHHVDCL | 192 | 1.0543 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0043
73729-1887-321DCT | ZONE 185 | RANGE | 1887-321DCT | 73729 | ENGLISH | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73657-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73657 | ENGLISH7 | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73658-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73658 | ENGLISH8 | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73665-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73665 | NHHHVDCL | 192 | 1.0531 | 1.0593 | 1.05 | 0.9 | 1.0515 | 0.0016
73729-1975-348DCT | ZONE 185 | RANGE | 1975-348DCT | 73729 | ENGLISH | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73657-1975-362WDCT | ZONE 185 | RANGE | 1975-362WDCT | 73657 | ENGLISH7 | 13.8 | 1.0541 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0041
73658-1975-362WDCT | ZONE 185 | RANGE | 1975-362WDCT | 73658 | ENGLISH8 | 13.8 | 1.0541 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0041
73665-1975-362WDCT | ZONE 185 | RANGE | 1975-362WDCT | 73665 | NHHHVDCL | 192 | 1.0565 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0065
73729-1975-362WDCT | ZONE 185 | RANGE | 1975-362WDCT | 73729 | ENGLISH | 13.8 | 1.0541 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0041
73657-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73657 | ENGLISH7 | 13.8 | 1.0518 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0018
73658-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73658 | ENGLISH8 | 13.8 | 1.0518 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0018
73665-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73665 | NHHHVDCL | 192 | 1.0517 | 1.0593 | 1.05 | 0.9 | 1.05 | 0.0017
73729-310-348WDCT | ZONE 185 | RANGE | 310-348WDCT | 73729 | ENGLISH | 13.8 | 1.0518 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0018
73388-329-352DCT | ZONE 171 | RANGE | 329-352DCT | 73388 | SO.NAUG | 13.8 | 1.0613 | 1.0542 | 1.05 | 0.9 | 1.0524 | 0.0089
73657-329-352DCT | ZONE 185 | RANGE | 329-352DCT | 73657 | ENGLISH7 | 13.8 | 1.0514 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0014
73658-329-352DCT | ZONE 185 | RANGE | 329-352DCT | 73658 | ENGLISH8 | 13.8 | 1.0514 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0014
73665-329-352DCT | ZONE 185 | RANGE | 329-352DCT | 73665 | NHHHVDCL | 192 | 1.054 | 1.0593 | 1.05 | 0.9 | #N/A | 0.004
73729-329-352DCT | ZONE 185 | RANGE | 329-352DCT | 73729 | ENGLISH | 13.8 | 1.0514 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0014
73657-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73657 | ENGLISH7 | 13.8 | 1.0509 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0009
73658-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73658 | ENGLISH8 | 13.8 | 1.0509 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0009
73665-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73665 | NHHHVDCL | 192 | 1.0543 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0043
73729-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73729 | ENGLISH | 13.8 | 1.0509 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0009
70693-LOLAKERD | ZONE 41 | RANGE | LOLAKERD | 70693 | ESX-STAT | 3.2 | 1.0634 | 1.0607 | 1.05 | 0.9 | 1.0633 | 0.0001
70693-LOSSMID4 | ZONE 41 | RANGE | LOSSMID4 | 70693 | ESX-STAT | 3.2 | 1.0638 | 1.0607 | 1.05 | 0.9 | 1.0637 | 0.0001
73665-LOSSMID4 | ZONE 185 | RANGE | LOSSMID4 | 73665 | NHHHVDCL | 192 | 1.0559 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0059
70693-LOSSMP2 | ZONE 41 | RANGE | LOSSMP2 | 70693 | ESX-STAT | 3.2 | 1.0691 | 1.0607 | 1.05 | 0.9 | 1.0686 | 0.0005
73657-LOSSMP2 | ZONE 185 | RANGE | LOSSMP2 | 73657 | ENGLISH7 | 13.8 | 1.0593 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0093
73658-LOSSMP2 | ZONE 185 | RANGE | LOSSMP2 | 73658 | ENGLISH8 | 13.8 | 1.0593 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0093
73665-LOSSMP2 | ZONE 185 | RANGE | LOSSMP2 | 73665 | NHHHVDCL | 192 | 1.0629 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0129
73729-LOSSMP2 | ZONE 185 | RANGE | LOSSMP2 | 73729 | ENGLISH | 13.8 | 1.0593 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0093
70693-LOSSMP3 | ZONE 41 | RANGE | LOSSMP3 | 70693 | ESX-STAT | 3.2 | 1.0729 | 1.0607 | 1.05 | 0.9 | 1.0719 | 0.001
73657-LOSSMP3 | ZONE 185 | RANGE | LOSSMP3 | 73657 | ENGLISH7 | 13.8 | 1.06 | 1.0566 | 1.05 | 0.9 | #N/A | 0.01
73658-LOSSMP3 | ZONE 185 | RANGE | LOSSMP3 | 73658 | ENGLISH8 | 13.8 | 1.06 | 1.0566 | 1.05 | 0.9 | #N/A | 0.01
73665-LOSSMP3 | ZONE 185 | RANGE | LOSSMP3 | 73665 | NHHHVDCL | 192 | 1.0636 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0136
73729-LOSSMP3 | ZONE 185 | RANGE | LOSSMP3 | 73729 | ENGLISH | 13.8 | 1.06 | 1.0566 | 1.05 | 0.9 | #N/A | 0.01
70693-LOSSMON6 | ZONE 41 | RANGE | LOSSMON6 | 70693 | ESX-STAT | 3.2 | 1.0641 | 1.0607 | 1.05 | 0.9 | 1.064 | 0.0001
70693-LOSSNHAV | ZONE 41 | RANGE | LOSSNHAV | 70693 | ESX-STAT | 3.2 | 1.064 | 1.0607 | 1.05 | 0.9 | 1.064 | 0
73657-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73657 | ENGLISH7 | 13.8 | 1.0504 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0004
73658-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73658 | ENGLISH8 | 13.8 | 1.0504 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0004
73665-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73665 | NHHHVDCL | 192 | 1.0505 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0005
73729-LOSSNHAV | ZONE 185 | RANGE | LOSSNHAV | 73729 | ENGLISH | 13.8 | 1.0504 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0004
73657-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0508 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0008
73658-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0508 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0008
73665-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73665 | NHHHVDCL | 192 | 1.0562 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0062
73729-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73729 | ENGLISH | 13.8 | 1.0508 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0008
73657-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0508 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0008
73658-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0508 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0008
73665-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73665 | NHHHVDCL | 192 | 1.0562 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0062
73729-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73729 | ENGLISH | 13.8 | 1.0508 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0008
73701-ASHCREEKBKR | ZONE 185 | RANGE | ASHCREEKBKR | 73701 | CRRA JCT | 115 | 1.0516 | 1.0489 | 1.05 | 0.9 | #N/A | 0.0016
73702-ASHCREEKBKR | ZONE 185 | RANGE | ASHCREEKBKR | 73702 | CRRA XFO | 115 | 1.0522 | 1.0495 | 1.05 | 0.9 | #N/A | 0.0022
73657-BAIRDASTK | ZONE 185 | RANGE | BAIRDASTK | 73657 | ENGLISH7 | 13.8 | 1.0519 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0019
73658-BAIRDASTK | ZONE 185 | RANGE | BAIRDASTK | 73658 | ENGLISH8 | 13.8 | 1.0519 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0019
73665-BAIRDASTK | ZONE 185 | RANGE | BAIRDASTK | 73665 | NHHHVDCL | 192 | 1.0565 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0065
73729-BAIRDASTK | ZONE 185 | RANGE | BAIRDASTK | 73729 | ENGLISH | 13.8 | 1.0519 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0019
73657-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73657 | ENGLISH7 | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73658-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73658 | ENGLISH8 | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73665-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73665 | NHHHVDCL | 192 | 1.0559 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0059
73729-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73729 | ENGLISH | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73388-BECONFLSTK | ZONE 171 | RANGE | BECONFLSTK | 73388 | SO.NAUG | 13.8 | 1.0571 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0071
73665-BOKUM2T | ZONE 185 | RANGE | BOKUM2T | 73665 | NHHHVDCL | 192 | 1.0566 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0066
73665-BOKUM3T | ZONE 185 | RANGE | BOKUM3T | 73665 | NHHHVDCL | 192 | 1.0566 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0066
73153-BRANFORD1T | ZONE 171 | RANGE | BRANFORD1T | 73153 | BRANFORD | 115 | 1.0508 | 1.0324 | 1.05 | 0.9 | #N/A | 0.0008
73657-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73657 | ENGLISH7 | 13.8 | 1.0614 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0114
73658-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73658 | ENGLISH8 | 13.8 | 1.0614 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0114
73665-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73665 | NHHHVDCL | 192 | 1.0624 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0124
73729-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73729 | ENGLISH | 13.8 | 1.0614 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0114
73657-BRANFORD2T | ZONE 185 | RANGE | BRANFORD2T | 73657 | ENGLISH7 | 13.8 | 1.0603 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0103
73658-BRANFORD2T | ZONE 185 | RANGE | BRANFORD2T | 73658 | ENGLISH8 | 13.8 | 1.0603 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0103
73665-BRANFORD2T | ZONE 185 | RANGE | BRANFORD2T | 73665 | NHHHVDCL | 192 | 1.0624 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0124
73729-BRANFORD2T | ZONE 185 | RANGE | BRANFORD2T | 73729 | ENGLISH | 13.8 | 1.0603 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0103
73153-BRANFORD4T | ZONE 171 | RANGE | BRANFORD4T | 73153 | BRANFORD | 115 | 1.0516 | 1.0324 | 1.05 | 0.9 | #N/A | 0.0016
73657-BRANFORD4T | ZONE 185 | RANGE | BRANFORD4T | 73657 | ENGLISH7 | 13.8 | 1.06 | 1.0566 | 1.05 | 0.9 | #N/A | 0.01
73658-BRANFORD4T | ZONE 185 | RANGE | BRANFORD4T | 73658 | ENGLISH8 | 13.8 | 1.06 | 1.0566 | 1.05 | 0.9 | #N/A | 0.01
73729-BRANFORD4T | ZONE 185 | RANGE | BRANFORD4T | 73729 | ENGLISH | 13.8 | 1.06 | 1.0566 | 1.05 | 0.9 | #N/A | 0.01
73388-BUNKERH1T | ZONE 171 | RANGE | BUNKERH1T | 73388 | SO.NAUG | 13.8 | 1.057 | 1.0542 | 1.05 | 0.9 | #N/A | 0.007
73657-BUNKERH2T | ZONE 185 | RANGE | BUNKERH2T | 73657 | ENGLISH7 | 13.8 | 1.0531 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0031
73658-BUNKERH2T | ZONE 185 | RANGE | BUNKERH2T | 73658 | ENGLISH8 | 13.8 | 1.0531 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0031
73665-BUNKERH2T | ZONE 185 | RANGE | BUNKERH2T | 73665 | NHHHVDCL | 192 | 1.0566 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0066
73729-BUNKERH2T | ZONE 185 | RANGE | BUNKERH2T | 73729 | ENGLISH | 13.8 | 1.0531 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0031
73657-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73657 | ENGLISH7 | 13.8 | 1.052 | 1.0566 | 1.05 | 0.9 | #N/A | 0.002
73658-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73658 | ENGLISH8 | 13.8 | 1.052 | 1.0566 | 1.05 | 0.9 | #N/A | 0.002
73665-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73665 | NHHHVDCL | 192 | 1.0555 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0055
73729-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73729 | ENGLISH | 13.8 | 1.052 | 1.0566 | 1.05 | 0.9 | #N/A | 0.002
73657-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73657 | ENGLISH7 | 13.8 | 1.0514 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0014
73658-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73658 | ENGLISH8 | 13.8 | 1.0514 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0014
73665-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73665 | NHHHVDCL | 192 | 1.0547 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0047
73729-DEVON3TSTK | ZONE 185 | RANGE | DEVON3TSTK | 73729 | ENGLISH | 13.8 | 1.0514 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0014
73129-DEVON6TSTK | ZONE 171 | RANGE | DEVON6TSTK | 73129 | E.DEVONJ | 115 | 1.05 | 1.0433 | 1.05 | 0.9 | #N/A | 0
73657-DEVON6TSTK | ZONE 185 | RANGE | DEVON6TSTK | 73657 | ENGLISH7 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73658-DEVON6TSTK | ZONE 185 | RANGE | DEVON6TSTK | 73658 | ENGLISH8 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73729-DEVON6TSTK | ZONE 185 | RANGE | DEVON6TSTK | 73729 | ENGLISH | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73388-DEVON7TSTK | ZONE 171 | RANGE | DEVON7TSTK | 73388 | SO.NAUG | 13.8 | 1.051 | 1.0542 | 1.05 | 0.9 | #N/A | 0.001
73657-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73657 | ENGLISH7 | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73658-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73658 | ENGLISH8 | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73665-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73665 | NHHHVDCL | 192 | 1.056 | 1.0593 | 1.05 | 0.9 | #N/A | 0.006
73729-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73729 | ENGLISH | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73657-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0511 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0011
73658-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0511 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0011
73665-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73665 | NHHHVDCL | 192 | 1.0559 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0059
73729-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73729 | ENGLISH | 13.8 | 1.0511 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0011
73657-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73657 | ENGLISH7 | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73658-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73658 | ENGLISH8 | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73665-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73665 | NHHHVDCL | 192 | 1.056 | 1.0593 | 1.05 | 0.9 | #N/A | 0.006
73729-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73729 | ENGLISH | 13.8 | 1.051 | 1.0566 | 1.05 | 0.9 | #N/A | 0.001
73657-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73658-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73665-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73665 | NHHHVDCL | 192 | 1.0565 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0065
73729-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73729 | ENGLISH | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73129-EDEVSTK | ZONE 171 | RANGE | EDEVSTK | 73129 | E.DEVONJ | 115 | 1.05 | 1.0433 | 1.05 | 0.9 | #N/A | 0
70693-ESHORE12TSTK | ZONE 41 | RANGE | ESHORE12TSTK | 70693 | ESX-STAT | 3.2 | 1.064 | 1.0607 | 1.05 | 0.9 | 1.0639 | 0.0001
73665-ESHORE12TSTK | ZONE 185 | RANGE | ESHORE12TSTK | 73665 | NHHHVDCL | 192 | 1.0508 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0008
73657-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0506 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0006
73658-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0506 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0006
73729-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73729 | ENGLISH | 13.8 | 1.0506 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0006
73657-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73657 | ENGLISH7 | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73658-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73658 | ENGLISH8 | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73729-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73729 | ENGLISH | 13.8 | 1.0517 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0017
73657-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73657 | ENGLISH7 | 13.8 | 1.0519 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0019
73658-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73658 | ENGLISH8 | 13.8 | 1.0519 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0019
73729-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73729 | ENGLISH | 13.8 | 1.0519 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0019
73657-GREENHLL2T | ZONE 185 | RANGE | GREENHLL2T | 73657 | ENGLISH7 | 13.8 | 1.0612 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0112
73658-GREENHLL2T | ZONE 185 | RANGE | GREENHLL2T | 73658 | ENGLISH8 | 13.8 | 1.0612 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0112
73665-GREENHLL2T | ZONE 185 | RANGE | GREENHLL2T | 73665 | NHHHVDCL | 192 | 1.0621 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0121
73729-GREENHLL2T | ZONE 185 | RANGE | GREENHLL2T | 73729 | ENGLISH | 13.8 | 1.0612 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0112
73657-MLLRVR2TSTK | ZONE 185 | RANGE | MLLRVR2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73658-MLLRVR2TSTK | ZONE 185 | RANGE | MLLRVR2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73665-MLLRVR2TSTK | ZONE 185 | RANGE | MLLRVR2TSTK | 73665 | NHHHVDCL | 192 | 1.062 | 1.0593 | 1.05 | 0.9 | #N/A | 0.012
73729-MLLRVR2TSTK | ZONE 185 | RANGE | MLLRVR2TSTK | 73729 | ENGLISH | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73657-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73657 | ENGLISH7 | 13.8 | 1.0619 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0119
73658-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73658 | ENGLISH8 | 13.8 | 1.0619 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0119
73665-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73665 | NHHHVDCL | 192 | 1.0629 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0129
73672-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73672 | SACKETT | 115 | 1.0521 | 1.0406 | 1.05 | 0.9 | #N/A | 0.0021
73729-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73729 | ENGLISH | 13.8 | 1.0619 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0119
73657-NOHAVN1TSTK | ZONE 185 | RANGE | NOHAVN1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0538 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0038
73658-NOHAVN1TSTK | ZONE 185 | RANGE | NOHAVN1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0538 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0038
73729-NOHAVN1TSTK | ZONE 185 | RANGE | NOHAVN1TSTK | 73729 | ENGLISH | 13.8 | 1.0538 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0038
73657-NOHAVN2TSTK | ZONE 185 | RANGE | NOHAVN2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0592 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0092
73658-NOHAVN2TSTK | ZONE 185 | RANGE | NOHAVN2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0592 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0092
73671-NOHAVN2TSTK | ZONE 185 | RANGE | NOHAVN2TSTK | 73671 | NO.HAVEN | 115 | 1.0572 | 1.039 | 1.05 | 0.9 | #N/A | 0.0072
73729-NOHAVN2TSTK | ZONE 185 | RANGE | NOHAVN2TSTK | 73729 | ENGLISH | 13.8 | 1.0592 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0092
73388-PEQUON22TSTK | ZONE 171 | RANGE | PEQUON22TSTK | 73388 | SO.NAUG | 13.8 | 1.0505 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0005
73657-PEQUON22TSTK | ZONE 185 | RANGE | PEQUON22TSTK | 73657 | ENGLISH7 | 13.8 | 1.0531 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0031
73658-PEQUON22TSTK | ZONE 185 | RANGE | PEQUON22TSTK | 73658 | ENGLISH8 | 13.8 | 1.0531 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0031
73729-PEQUON22TSTK | ZONE 185 | RANGE | PEQUON22TSTK | 73729 | ENGLISH | 13.8 | 1.0531 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0031
73388-PEQUON32TSTK | ZONE 171 | RANGE | PEQUON32TSTK | 73388 | SO.NAUG | 13.8 | 1.0514 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0014
73657-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73657 | ENGLISH7 | 13.8 | 1.0506 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0006
73658-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73658 | ENGLISH8 | 13.8 | 1.0506 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0006
73665-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73665 | NHHHVDCL | 192 | 1.0545 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0045
73729-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73729 | ENGLISH | 13.8 | 1.0506 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0006
73388-PLUMTREE25T | ZONE 171 | RANGE | PLUMTREE25T | 73388 | SO.NAUG | 13.8 | 1.0517 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0017
73657-QUINIPACST1 | ZONE 185 | RANGE | QUINIPACST1 | 73657 | ENGLISH7 | 13.8 | 1.0605 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0105
73658-QUINIPACST1 | ZONE 185 | RANGE | QUINIPACST1 | 73658 | ENGLISH8 | 13.8 | 1.0605 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0105
73665-QUINIPACST1 | ZONE 185 | RANGE | QUINIPACST1 | 73665 | NHHHVDCL | 192 | 1.0626 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0126
73729-QUINIPACST1 | ZONE 185 | RANGE | QUINIPACST1 | 73729 | ENGLISH | 13.8 | 1.0605 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0105
73267-SOUTHEND5T | ZONE 171 | RANGE | SOUTHEND5T | 73267 | DARIEN | 115 | 1.0658 | 1.0375 | 1.05 | 0.9 | #N/A | 0.0158
73286-SOUTHEND5T | ZONE 171 | RANGE | SOUTHEND5T | 73286 | COMPO | 115 | 1.0559 | 1.0385 | 1.05 | 0.9 | #N/A | 0.0059
73300-SOUTHEND5T | ZONE 171 | RANGE | SOUTHEND5T | 73300 | ELYTAP | 115 | 1.0615 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0115
73267-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73267 | DARIEN | 115 | 1.0658 | 1.0375 | 1.05 | 0.9 | #N/A | 0.0158
73286-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73286 | COMPO | 115 | 1.0559 | 1.0385 | 1.05 | 0.9 | #N/A | 0.0059
73300-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73300 | ELYTAP | 115 | 1.0615 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0115
73665-SOTHNGTN12T | ZONE 185 | RANGE | SOTHNGTN12T | 73665 | NHHHVDCL | 192 | 1.0568 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0068
73388-SOTHNGTN28T | ZONE 171 | RANGE | SOTHNGTN28T | 73388 | SO.NAUG | 13.8 | 1.0571 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0071
73388-STEVENSNSTK | ZONE 171 | RANGE | STEVENSNSTK | 73388 | SO.NAUG | 13.8 | 1.057 | 1.0542 | 1.05 | 0.9 | #N/A | 0.007
73657-WALLING1TSTK | ZONE 185 | RANGE | WALLING1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73658-WALLING1TSTK | ZONE 185 | RANGE | WALLING1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73671-WALLING1TSTK | ZONE 185 | RANGE | WALLING1TSTK | 73671 | NO.HAVEN | 115 | 1.0504 | 1.039 | 1.05 | 0.9 | #N/A | 0.0004
73729-WALLING1TSTK | ZONE 185 | RANGE | WALLING1TSTK | 73729 | ENGLISH | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73657-WALLING2TSTK | ZONE 185 | RANGE | WALLING2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73658-WALLING2TSTK | ZONE 185 | RANGE | WALLING2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73671-WALLING2TSTK | ZONE 185 | RANGE | WALLING2TSTK | 73671 | NO.HAVEN | 115 | 1.0503 | 1.039 | 1.05 | 0.9 | #N/A | 0.0003
73729-WALLING2TSTK | ZONE 185 | RANGE | WALLING2TSTK | 73729 | ENGLISH | 13.8 | 1.0596 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0096
73657-WATERST1TSTK | ZONE 185 | RANGE | WATERST1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0541 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0041
73658-WATERST1TSTK | ZONE 185 | RANGE | WATERST1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0541 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0041
73729-WATERST1TSTK | ZONE 185 | RANGE | WATERST1TSTK | 73729 | ENGLISH | 13.8 | 1.0541 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0041
73657-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73658-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73665-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73665 | NHHHVDCL | 192 | 1.0567 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0067
73729-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73729 | ENGLISH | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73657-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73658-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73665-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73665 | NHHHVDCL | 192 | 1.0567 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0067
73729-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73729 | ENGLISH | 13.8 | 1.0516 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0016
73388-WOODMNT1TSTK | ZONE 171 | RANGE | WOODMNT1TSTK | 73388 | SO.NAUG | 13.8 | 1.051 | 1.0542 | 1.05 | 0.9 | #N/A | 0.001
73665-WOODMNT1TSTK | ZONE 185 | RANGE | WOODMNT1TSTK | 73665 | NHHHVDCL | 192 | 1.0563 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0063
73746-WOODMNT1TSTK | ZONE 186 | RANGE | WOODMNT1TSTK | 73746 | WOODMONT | 13.8 | 0.413 | 1.0354 | 1.05 | 0.9 | 0.4107 | 0.0023
73665-WOODMNT2TSTK | ZONE 185 | RANGE | WOODMNT2TSTK | 73665 | NHHHVDCL | 192 | 1.0562 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0062
73746-WOODMNT2TSTK | ZONE 186 | RANGE | WOODMNT2TSTK | 73746 | WOODMONT | 13.8 | 0.4237 | 1.0354 | 1.05 | 0.9 | 0.4182 | 0.0055
70693-318-362STKBR | ZONE 41 | RANGE | 318-362STKBR | 70693 | ESX-STAT | 3.2 | 1.0647 | 1.0607 | 1.05 | 0.9 | 1.0649 | -0.0002
70622-CARD1TSTK | ZONE 41 | RANGE | CARD1TSTK | 70622 | WHITE RV | 13.8 | 1.0503 | 1.0547 | 1.05 | 0.9 | 1.0501 | 0.0002
70693-CARD1T+LAKE | ZONE 41 | RANGE | CARD1T+LAKE | 70693 | ESX-STAT | 3.2 | 1.0672 | 1.0607 | 1.05 | 0.9 | 1.0667 | 0.0005
73657-CARD1T+LAKE | ZONE 185 | RANGE | CARD1T+LAKE | 73657 | ENGLISH7 | 13.8 | 1.0603 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0103
73658-CARD1T+LAKE | ZONE 185 | RANGE | CARD1T+LAKE | 73658 | ENGLISH8 | 13.8 | 1.0603 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0103
73665-CARD1T+LAKE | ZONE 185 | RANGE | CARD1T+LAKE | 73665 | NHHHVDCL | 192 | 1.0636 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0136
73729-CARD1T+LAKE | ZONE 185 | RANGE | CARD1T+LAKE | 73729 | ENGLISH | 13.8 | 1.0603 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0103
70622-CARD3TSTK | ZONE 41 | RANGE | CARD3TSTK | 70622 | WHITE RV | 13.8 | 1.0503 | 1.0547 | 1.05 | 0.9 | 1.0502 | 0.0001
70693-CARD3T+LAKE | ZONE 41 | RANGE | CARD3T+LAKE | 70693 | ESX-STAT | 3.2 | 1.0672 | 1.0607 | 1.05 | 0.9 | 1.0667 | 0.0005
73657-CARD3T+LAKE | ZONE 185 | RANGE | CARD3T+LAKE | 73657 | ENGLISH7 | 13.8 | 1.0603 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0103
73658-CARD3T+LAKE | ZONE 185 | RANGE | CARD3T+LAKE | 73658 | ENGLISH8 | 13.8 | 1.0603 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0103
73665-CARD3T+LAKE | ZONE 185 | RANGE | CARD3T+LAKE | 73665 | NHHHVDCL | 192 | 1.0636 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0136
73729-CARD3T+LAKE | ZONE 185 | RANGE | CARD3T+LAKE | 73729 | ENGLISH | 13.8 | 1.0603 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0103
73293-LONGMT5TSTK | '345KV ' | RANGE | LONGMT5TSTK | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.95 | #N/A | 0
73293-LONGMT5TSTK | ZONE 171 | RANGE | LONGMT5TSTK | 73293 | NORWALK | 345 | 1.05 | 1.0193 | 1.05 | 0.9 | #N/A | 0
73657-LONGMT5TSTK | ZONE 185 | RANGE | LONGMT5TSTK | 73657 | ENGLISH7 | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73658-LONGMT5TSTK | ZONE 185 | RANGE | LONGMT5TSTK | 73658 | ENGLISH8 | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73665-LONGMT5TSTK | ZONE 185 | RANGE | LONGMT5TSTK | 73665 | NHHHVDCL | 192 | 1.0551 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0051
73729-LONGMT5TSTK | ZONE 185 | RANGE | LONGMT5TSTK | 73729 | ENGLISH | 13.8 | 1.0523 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0023
73151-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73151 | UNCASVLA | 115 | 1.0538 | 1.0143 | 1.05 | 0.9 | 1.0537 | 0.0001
73152-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73152 | UNCASVLB | 115 | 1.054 | 1.0146 | 1.05 | 0.9 | 1.0539 | 0.0001
73210-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73210 | MONTVLLE | 115 | 1.0542 | 1.0148 | 1.05 | 0.9 | 1.0541 | 0.0001
73216-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73216 | WHIP JCT | 115 | 1.0506 | 1.0134 | 1.05 | 0.9 | 1.0506 | 0
73278-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73278 | MONT DSL | 115 | 1.0542 | 1.0148 | 1.05 | 0.9 | 1.0541 | 0.0001
73448-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73448 | UNCASVIL | 27.6 | 1.0515 | 1.012 | 1.05 | 0.9 | 1.0514 | 0.0001
73620-MONTVSTBKR | ZONE 178 | RANGE | MONTVSTBKR | 73620 | BUDDGTNB | 34.5 | 1.0807 | 1.0398 | 1.05 | 0.9 | 1.0806 | 0.0001
70622-NOMNTSTBKR | ZONE 41 | RANGE | NOMNTSTBKR | 70622 | WHITE RV | 13.8 | 1.0514 | 1.0547 | 1.05 | 0.9 | 1.0517 | -0.0003
70693-NOMNTSTBKR | ZONE 41 | RANGE | NOMNTSTBKR | 70693 | ESX-STAT | 3.2 | 1.0578 | 1.0607 | 1.05 | 0.9 | 1.0577 | 0.0001
73388-NOMNTSTBKR | ZONE 171 | RANGE | NOMNTSTBKR | 73388 | SO.NAUG | 13.8 | 1.0517 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0017
73657-NOMNTSTBKR | ZONE 185 | RANGE | NOMNTSTBKR | 73657 | ENGLISH7 | 13.8 | 1.0522 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0022
73658-NOMNTSTBKR | ZONE 185 | RANGE | NOMNTSTBKR | 73658 | ENGLISH8 | 13.8 | 1.0522 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0022
73665-NOMNTSTBKR | ZONE 185 | RANGE | NOMNTSTBKR | 73665 | NHHHVDCL | 192 | 1.0544 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0044
73729-NOMNTSTBKR | ZONE 185 | RANGE | NOMNTSTBKR | 73729 | ENGLISH | 13.8 | 1.0522 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0022
70622-NMSTBKREAC | ZONE 41 | RANGE | NMSTBKREAC | 70622 | WHITE RV | 13.8 | 1.0514 | 1.0547 | 1.05 | 0.9 | 1.0517 | -0.0003
70693-NMSTBKREAC | ZONE 41 | RANGE | NMSTBKREAC | 70693 | ESX-STAT | 3.2 | 1.0578 | 1.0607 | 1.05 | 0.9 | 1.0577 | 0.0001
73388-NMSTBKREAC | ZONE 171 | RANGE | NMSTBKREAC | 73388 | SO.NAUG | 13.8 | 1.0517 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0017
73657-NMSTBKREAC | ZONE 185 | RANGE | NMSTBKREAC | 73657 | ENGLISH7 | 13.8 | 1.0522 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0022
73658-NMSTBKREAC | ZONE 185 | RANGE | NMSTBKREAC | 73658 | ENGLISH8 | 13.8 | 1.0522 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0022
73665-NMSTBKREAC | ZONE 185 | RANGE | NMSTBKREAC | 73665 | NHHHVDCL | 192 | 1.0544 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0044
73729-NMSTBKREAC | ZONE 185 | RANGE | NMSTBKREAC | 73729 | ENGLISH | 13.8 | 1.0522 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0022
73665-SCOVRK7TSTK | ZONE 185 | RANGE | SCOVRK7TSTK | 73665 | NHHHVDCL | 192 | 1.0636 | 1.0593 | 1.05 | 0.9 | 1.0594 | 0.0042
73657-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73657 | ENGLISH7 | 13.8 | 1.0537 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0037
73658-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73658 | ENGLISH8 | 13.8 | 1.0537 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0037
73665-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73665 | NHHHVDCL | 192 | 1.0561 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0061
73729-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73729 | ENGLISH | 13.8 | 1.0537 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0037
73657-SGTN1TSTK | ZONE 185 | RANGE | SGTN1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0534 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0034
73658-SGTN1TSTK | ZONE 185 | RANGE | SGTN1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0534 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0034
73665-SGTN1TSTK | ZONE 185 | RANGE | SGTN1TSTK | 73665 | NHHHVDCL | 192 | 1.0551 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0051
73729-SGTN1TSTK | ZONE 185 | RANGE | SGTN1TSTK | 73729 | ENGLISH | 13.8 | 1.0534 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0034
73388-SGTN3TSTK | ZONE 171 | RANGE | SGTN3TSTK | 73388 | SO.NAUG | 13.8 | 1.0505 | 1.0542 | 1.05 | 0.9 | #N/A | 0.0005
73657-SGTN3TSTK | ZONE 185 | RANGE | SGTN3TSTK | 73657 | ENGLISH7 | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73658-SGTN3TSTK | ZONE 185 | RANGE | SGTN3TSTK | 73658 | ENGLISH8 | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73665-SGTN3TSTK | ZONE 185 | RANGE | SGTN3TSTK | 73665 | NHHHVDCL | 192 | 1.0523 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0023
73729-SGTN3TSTK | ZONE 185 | RANGE | SGTN3TSTK | 73729 | ENGLISH | 13.8 | 1.0515 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0015
73657-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0512 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0012
73658-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0512 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0012
73665-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73665 | NHHHVDCL | 192 | 1.0506 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0006
73729-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73729 | ENGLISH | 13.8 | 1.0512 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0012
73657-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73657 | ENGLISH7 | 13.8 | 1.0512 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0012
73658-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73658 | ENGLISH8 | 13.8 | 1.0512 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0012
73665-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73665 | NHHHVDCL | 192 | 1.0533 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0033
73729-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73729 | ENGLISH | 13.8 | 1.0512 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0012
73657-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73657 | ENGLISH7 | 13.8 | 1.0527 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0027
73658-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73658 | ENGLISH8 | 13.8 | 1.0527 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0027
73665-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73665 | NHHHVDCL | 192 | 1.0536 | 1.0593 | 1.05 | 0.9 | 1.0519 | 0.0017
73729-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73729 | ENGLISH | 13.8 | 1.0527 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0027
73267-GLNBRKASTK | ZONE 171 | RANGE | GLNBRKASTK | 73267 | DARIEN | 115 | 1.0658 | 1.0375 | 1.05 | 0.9 | #N/A | 0.0158
73286-GLNBRKASTK | ZONE 171 | RANGE | GLNBRKASTK | 73286 | COMPO | 115 | 1.0559 | 1.0385 | 1.05 | 0.9 | #N/A | 0.0059
73300-GLNBRKASTK | ZONE 171 | RANGE | GLNBRKASTK | 73300 | ELYTAP | 115 | 1.0615 | 1.0378 | 1.05 | 0.9 | #N/A | 0.0115
73657-DC1-BES-NOR | ZONE 185 | RANGE | DC1-BES-NOR | 73657 | ENGLISH7 | 13.8 | 1.0525 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0025
73658-DC1-BES-NOR | ZONE 185 | RANGE | DC1-BES-NOR | 73658 | ENGLISH8 | 13.8 | 1.0525 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0025
73665-DC1-BES-NOR | ZONE 185 | RANGE | DC1-BES-NOR | 73665 | NHHHVDCL | 192 | 1.0552 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0052
73729-DC1-BES-NOR | ZONE 185 | RANGE | DC1-BES-NOR | 73729 | ENGLISH | 13.8 | 1.0525 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0025
73657-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73657 | ENGLISH7 | 13.8 | 1.0508 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0008
73658-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73658 | ENGLISH8 | 13.8 | 1.0508 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0008
73665-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73665 | NHHHVDCL | 192 | 1.0531 | 1.0593 | 1.05 | 0.9 | #N/A | 0.0031
73729-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73729 | ENGLISH | 13.8 | 1.0508 | 1.0566 | 1.05 | 0.9 | #N/A | 0.0008

## contingencies
CONTINGENCY LEGEND
LABEL EVENTS
100LINE : OPEN LINE FROM BUS 73344 [MONTVLLE69.000] TO BUS 73343 [GALESF A69.000] CKT 1
100+400LINES: OPEN LINE FROM BUS 73344 [MONTVLLE69.000] TO BUS 73343 [GALESF A69.000] CKT 1
OPEN LINE FROM BUS 73343 [GALESF A69.000] TO BUS 73345 [LEDYARDJ69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73615 [BUDDGTN 69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73617 [TUNNEL 69.000] CKT 1
400LINE : OPEN LINE FROM BUS 73343 [GALESF A69.000] TO BUS 73345 [LEDYARDJ69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73615 [BUDDGTN 69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73617 [TUNNEL 69.000] CKT 1
500LINE : OPEN LINE FROM BUS 73617 [TUNNEL 69.000] TO BUS 73616 [SCRRA PF69.000] CKT 1
667-690LINE : OPEN LINE FROM BUS 73336 [FALLS V 69.000] TO BUS 73337 [SALISBRY69.000] CKT 1
689LINE : OPEN LINE FROM BUS 73346 [TORRGTN 69.000] TO BUS 73336 [FALLS V 69.000] CKT 1
693LINE : OPEN LINE FROM BUS 73346 [TORRGTN 69.000] TO BUS 73336 [FALLS V 69.000] CKT 2
694LINE : OPEN LINE FROM BUS 73336 [FALLS V 69.000] TO BUS 73335 [N.CANAAN69.000] CKT 1
1000LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
OPEN LINE FROM BUS 73612 [BEAN HLL115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
1050LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1050+1766LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
OPEN LINE FROM BUS 73255 [WESTSIDE115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1060LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
1070LINE : OPEN LINE FROM BUS 73218 [STKHOUSE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1070+1490LNS: OPEN LINE FROM BUS 73291 [FORTHF 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73218 [STKHOUSE115.00] TO BUS 73215 [CARD 115.00] CKT 1
1080LINE : OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1090LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1100LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
1130LINE : OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1130+1416LNS: OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
1163LINE : OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
1163+1910LNS: OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
1165LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
1191LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
1200LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
1206LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73600 [CONN YAN115.00] CKT 1
1207LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
1208LINE : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1222LINE : OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 1
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 2
1235LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73151 [UNCASVLA115.00] CKT 1
1238LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
1238+1813LNS: OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
1250LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73152 [UNCASVLB115.00] CKT 1
1261LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73231 [BOKUM 115.00] CKT 1
1270LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
1272LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1272+1445LNS: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1280LINE : OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1300LINE : OPEN LINE FROM BUS 73220 [ENFIELD 115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
OPEN LINE FROM BUS 73222 [WNDSRLK 115.00] TO BUS 73539 [DEXTR PF13.800] CKT 1
1310LINE : OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73221 [S.WNDSRB115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73283 [SWINDT13115.00] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73221 [S.WNDSRB115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1337LINE : OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
1342LINE : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
1355LINE : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
ONE1385 : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
1385LN+AUTO : OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 2
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 3
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1389LINE : OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1394LINE : OPEN LINE FROM BUS 73266 [SCITICO 115.00] TO BUS 72978 [FRANCONA115.00] CKT 1
1410LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73613 [BUDDGTN2115.00] CKT 1
1416LINE : OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1430LINE : OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
1440LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
1443LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1443+1759LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1445LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1450LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
1460LINE : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
1466LINE : OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
1470LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
1490LINE : OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
1500LINE : OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73150 [FLNDRSA 115.00] CKT 1
OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73149 [WILIAMSA115.00] CKT 1
OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1505LINE : OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73223 [FRYBRT05115.00] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73236 [FRYBR05 115.00] CKT 1
OPEN LINE FROM BUS 73236 [FRYBR05 115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73476 [TRACY05 115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73270 [BROOKLYN115.00] TO BUS 73444 [BROOKLYN23.000] CKT 1
OPEN LINE FROM BUS 73475 [TRACY 23.000] TO BUS 73476 [TRACY05 115.00] CKT 1
1508LINE : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
1515LINE : OPEN LINE FROM BUS 72972 [LUDLOW 115.00] TO BUS 73266 [SCITICO 115.00] CKT 1
1537LINE : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
1545LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
1545+SPS : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73705 [IND.WELL115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
1550LINE : OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1550+1950LNS: OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1560LINE : OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
1565LINE : OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
1570LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
1572LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1572+1772LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
OPEN LINE FROM BUS 73600 [CONN YAN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1575LINE : OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
1580LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1585LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1588LINE : OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
1594LINE : OPEN LINE FROM BUS 73705 [IND.WELL115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
1605LINE : OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73238 [FLANDRSB115.00] CKT 1
OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73239 [WILIAMSB115.00] CKT 1
OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1607LINE : OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73226 [FRYBRT07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73229 [FRY BR07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73229 [FRY BR07115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73442 [TRACY 23.000] CKT 1
1610LINE : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1618LINE : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
1620NLINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73241 [MIDDLTWN115.00] CKT 1
1620SLINE : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
1622LINE : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
1625LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73161 [ROCKVILL115.00] CKT 1
1630LINE : OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
1637LINE : OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
1640LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1655LINE : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
1668LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1670LINE : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
1675LINE : OPEN LINE FROM BUS 73612 [BEAN HLL115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1685LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1690LINE : OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73197 [HANOVERA115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1704LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73248 [SW.HTFD 115.00] CKT 1
1710LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
1720LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
1721LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1722LINE : OPEN LINE FROM BUS 73248 [SW.HTFD 115.00] TO BUS 73279 [CDECCA 115.00] CKT 1
OPEN LINE FROM BUS 73261 [NW.HTFD 115.00] TO BUS 73279 [CDECCA 115.00] CKT 1
1726LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73247 [FARMNGTN115.00] CKT 1
1730ALINE : OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1730BLINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1730CLINE : OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1732LINE : OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73262 [CANTON 115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
1740LINE : OPEN LINE FROM BUS 73162 [WATERSDE115.00] TO BUS 73163 [COS COB 115.00] CKT 1
1750LINE : OPEN LINE FROM BUS 73167 [SO.END 115.00] TO BUS 73144 [TOMAC 115.00] CKT 1
OPEN LINE FROM BUS 73144 [TOMAC 115.00] TO BUS 73163 [COS COB 115.00] CKT 1
1751LINE : OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1752LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73257 [ROCKY HL115.00] CKT 1
1753LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
1756LINE : OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
1759LINE : OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1760LINE : OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
1760+1876LNS: OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
1763LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73284 [SWINDT17115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73131 [S.WNDSRA115.00] CKT 1
OPEN LINE FROM BUS 73131 [S.WNDSRA115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1765LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73255 [WESTSIDE115.00] CKT 1
1766LINE : OPEN LINE FROM BUS 73255 [WESTSIDE115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1767LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73259 [HOPEWELL115.00] CKT 1
1769LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73256 [E.NBRITN115.00] CKT 1
1770LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
1771LINE : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
1772LINE : OPEN LINE FROM BUS 73600 [CONN YAN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1773LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73257 [ROCKY HL115.00] CKT 1
1775LINE : OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73274 [RIVDRHIA115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 73274 [RIVDRHIA115.00] TO BUS 73537 [RVRSD PF23.000] CKT 1
1777LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1779LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1780LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
1783LINE : OPEN LINE FROM BUS 73254 [NEWINGTN115.00] TO BUS 73247 [FARMNGTN115.00] CKT 1
OPEN LINE FROM BUS 73254 [NEWINGTN115.00] TO BUS 73256 [E.NBRITN115.00] CKT 1
1784LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73288 [NESMBY 115.00] CKT 1
OPEN LINE FROM BUS 73288 [NESMBY 115.00] TO BUS 73262 [CANTON 115.00] CKT 1
1785LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73254 [NEWINGTN115.00] CKT 1
1786LINE : OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73275 [RIVDRHIB115.00] CKT 1
OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
1788LINE : OPEN LINE FROM BUS 73245 [TORR TER115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
1790LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
1792LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
1800-1860LNS: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
1810LINE : OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1813LINE : OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
1820LINE : OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1821LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 72991 [SAGAR 115.00] CKT 1
1825LINE : OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1830LINE : OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1835LINE : OPEN LINE FROM BUS 73235 [CHIP HIL115.00] TO BUS 73240 [THOMASTN115.00] CKT 1
1836LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 72992 [SAGBR 115.00] CKT 1
1867LINE : OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
1870LINE : OPEN LINE FROM BUS 73177 [MYSTICCT115.00] TO BUS 73285 [CTRI1870115.00] CKT 1
OPEN LINE FROM BUS 73285 [CTRI1870115.00] TO BUS 72581 [WOOD RIV115.00] CKT 1
1876LINE : OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
1880LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
1887LINE : OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
1890LINE : OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
1900LINE : OPEN LINE FROM BUS 73203 [CAMPV PH115.00] TO BUS 73245 [TORR TER115.00] CKT 1
1910LINE : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
1921LINE : OPEN LINE FROM BUS 73203 [CAMPV PH115.00] TO BUS 73240 [THOMASTN115.00] CKT 1
1950LINE : OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
1975LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
1977LINENEW : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
1990LINE : OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
8100LINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
8200LINE : OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
8300LINE : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
8400LINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
8500LINE : OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
8600LINE : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
8700LINE : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
8804ALINE : OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
8809ALINE-1 : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
8809ALINE-2 : OPEN LINE FROM BUS 73694 [BAIRD A 115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
8904BLINE : OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
8909BLINE-1 : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
8909BLINE-2 : OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
9500LINE : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
9502LINE : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
84004LINE : OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
88003ALINE : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
88003ALINE-1: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
88003ALINE-2: OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
88003ALINE-3: OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
88005ALINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
88005ALINE-1: OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
88005ALINE-2: OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
88006ALINE : OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73694 [BAIRD A 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
89003BLINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
89003BLINE-1: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
89003BLINE-2: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
89003BLINE-3: OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
89005BLINE : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
89005BLINE-1: OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
89005BLINE-2: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
89006BLINE : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
89006BLINE-1: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
91001LINE : OPEN LINE FROM BUS 73701 [CRRA JCT115.00] TO BUS 73702 [CRRA XFO115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
EDEVDEV1 : OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
EDEVDEV2 : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73129 [E.DEVONJ115.00] CKT 1
301-302LNS : OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72929 [BELCH301345.00] CKT 1
OPEN LINE FROM BUS 72929 [BELCH301345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
OPEN LINE FROM BUS 71796 [CARP HL 345.00] TO BUS 71797 [MILLBURY345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
310LINE : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
312LINE : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72926 [NRTHFLD 345.00] CKT 1
312+393LNS : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72926 [NRTHFLD 345.00] CKT 1
312+393REAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
318LINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
321LINE : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
329LINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
330LINE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
330+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73566 [LAKERD#221.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73567 [LAKERD#321.000] CKT 1
347LINE : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
347LREAC : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
347+LAKE : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73566 [LAKERD#221.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73567 [LAKERD#321.000] CKT 1
348LINE : OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
348NLINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
348N+AUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
352LINE : OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73105 [LONG MTN345.00] CKT 1
352+AUTO : OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73105 [LONG MTN345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73202 [FROST BR115.00] CKT 1
353LINE : OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
353+AUTO : OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
354LINE : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
362ELINE : OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
362WLINE : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
364+AUTO : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
368LINE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
371LINE : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
371+AUTO : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
376LINE : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
381LINE : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
381LREAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
383LINE : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
384LINE : OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
387+AUTOS : OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73664 [NHHHVDCL345.00] TO BUS 73665 [NHHHVDCL191.50] CKT 1
393LINE : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
395LINE : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
395+AUTO : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
398LINE : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
398LREAC : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
PLUMNOR : OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73133 [PLUMUG 345.00] CKT 2
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73134 [NORUG 345.00] CKT 3
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 2
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 3
OPEN LINE FROM BUS 73135 [NOROH 345.00] TO BUS 73293 [NORWALK 345.00] CKT 3
1000-1090DCT: OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
OPEN LINE FROM BUS 73611 [DUDLEY T115.00] TO BUS 73612 [BEAN HLL115.00] CKT 1
OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1060-1165DCT: OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
1060-1270DCT: OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
1070-1080DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
OPEN LINE FROM BUS 73291 [FORTHF 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
1080-1280DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1080-1490DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73214 [WAWECS J115.00] CKT 1
OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1100-1200DCT: OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
1100-1300DCT: OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
OPEN LINE FROM BUS 73220 [ENFIELD 115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
OPEN LINE FROM BUS 73222 [WNDSRLK 115.00] TO BUS 73539 [DEXTR PF13.800] CKT 1
1130-1430DCT: OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
113091001DCT: OPEN LINE FROM BUS 73701 [CRRA JCT115.00] TO BUS 73702 [CRRA XFO115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1163-1550D-2: OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1207-1775DCT: OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73253 [1775 TAP115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73274 [RIVDRHIA115.00] CKT 1
OPEN LINE FROM BUS 73274 [RIVDRHIA115.00] TO BUS 73537 [RVRSD PF23.000] CKT 1
1208-1640DCT: OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1222-1730ADC: OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 1
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1261-1620SDC: OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
1272-1721DCT: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1280-1870DCT: OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73177 [MYSTICCT115.00] TO BUS 73285 [CTRI1870115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73285 [CTRI1870115.00] TO BUS 72581 [WOOD RIV115.00] CKT 1
1310-1763DCT: OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73284 [SWINDT17115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73131 [S.WNDSRA115.00] CKT 1
OPEN LINE FROM BUS 73131 [S.WNDSRA115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73221 [S.WNDSRB115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73283 [SWINDT13115.00] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73221 [S.WNDSRB115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1355-1610DCT: OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1389-1880DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
1394-1515DCT: OPEN LINE FROM BUS 72978 [FRANCONA115.00] TO BUS 73266 [SCITICO 115.00] CKT 1
OPEN LINE FROM BUS 73266 [SCITICO 115.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
1416-1867DCT: OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1416-1880DCT: OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1416-1890DCT: OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1440-1450DCT: OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
1470-1565DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73155 [RDGFLD J115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
1470-1637DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
1470-1720DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1505-1607DCT: OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73223 [FRYBRT05115.00] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73236 [FRYBR05 115.00] CKT 1
OPEN LINE FROM BUS 73236 [FRYBR05 115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73476 [TRACY05 115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73270 [BROOKLYN115.00] TO BUS 73444 [BROOKLYN23.000] CKT 1
OPEN LINE FROM BUS 73475 [TRACY 23.000] TO BUS 73476 [TRACY05 115.00] CKT 1
OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73226 [FRYBRT07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73229 [FRY BR07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73229 [FRY BR07115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73442 [TRACY 23.000] CKT 1
1545-1570DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
1560-1570DCT: OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
1570-1575DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
1570-1580DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1575-1585DCT: OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
1575-1990DCT: OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73186 [BALDWINA115.00] TO BUS 73386 [BALDWINA13.800] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
1580-1585DCT: OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 2
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
1580-1730BDC: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1620N-1975DC: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
1622-1887DCT: OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
1637-1720DCT: OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1640-1690DCT: OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73197 [HANOVERA115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1668-1721DCT: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1670-1771DCT: OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
1670-1830DCT: OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1710-1730ADC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1710-1730BDC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1710-1730CDC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1720-1730ADC: OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1732-1788DCT: OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73262 [CANTON 115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
OPEN LINE FROM BUS 73245 [TORR TER115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
1751-1777DCT: OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1770-1887DCT: OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
1777-1779DCT: OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
1800-1810DCT: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1800-1825DCT: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1810-1825DCT: OPEN LINE FROM BUS 73154 [SGTN B 115.00] TO BUS 73234 [CHIPP TP115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1867-1880DCT: OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
1867-1890DCT: OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
1867-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1880-1890DCT: OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1880-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1890-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
8100-8200DCT: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
1466-362EDCT: OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
1460-387DCT : OPEN LINE FROM BUS 73107 [SCOVL RK345.00] TO BUS 73663 [E.SHORE 345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
1565-PLNRDCT: OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73133 [PLUMUG 345.00] CKT 2
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73134 [NORUG 345.00] CKT 3
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 2
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 3
OPEN LINE FROM BUS 73135 [NOROH 345.00] TO BUS 73293 [NORWALK 345.00] CKT 3
1610-BSKDVDC: OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1618-321DCT : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
1751-395DCT : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
1759-353DCT : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73114 [PORT JCT345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1767-353DCT : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73259 [HOPEWELL115.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73114 [PORT JCT345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1770-321DCT : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
1779-395DCT : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
1887-321DCT : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
1975-348DCT : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
1975-362WDCT: OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
310-348WDCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
310-368DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
310-383DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
329-352DCT : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73106 [SOUTHGTN345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73202 [FROST BR115.00] CKT 1
362W-376DCT : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
371-383DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73109 [MONTVILE345.00] CKT 1
MANCHAUTO1 : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
NORAUT : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73293 [NORWALK 345.00] CKT 1
PLUMAUT : OPEN LINE FROM BUS 73115 [PLUMTREE345.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
SOUTH1XAUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOUTH2XAUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
LOSSBPT3 : OPEN LINE FROM BUS 73648 [BPTHBR#322.000] TO BUS 73700 [PEQUONIC115.00] CKT 1
LOSSDEV7 : OPEN LINE FROM BUS 73553 [DEVON#7 13.800] TO BUS 73195 [DEVON 115.00] CKT 1
LOLAKERD : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
LOSSMID4 : OPEN LINE FROM BUS 73557 [MIDDTN#422.000] TO BUS 73116 [MIDDLTWN345.00] CKT 1
LOSSMP2 : OPEN LINE FROM BUS 73562 [MILL#2 24.000] TO BUS 73110 [MILLSTNE345.00] CKT 1
LOSSMP3 : OPEN LINE FROM BUS 73563 [MILL#3 24.000] TO BUS 73110 [MILLSTNE345.00] CKT 1
LOSSMON6 : OPEN LINE FROM BUS 73559 [MONTV#6 22.000] TO BUS 73210 [MONTVLLE115.00] CKT 1
LOSSNHAV : OPEN LINE FROM BUS 73651 [NH HARBR22.000] TO BUS 73668 [E.SHORE 115.00] CKT 1
LOSSNOR1 : OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
LOSSNOR2 : OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
ALLINGS1TSTK: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
ALLINGS2TSTK: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73685 [ALLINGSB115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
ASHCREEKBKR : OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73763 [ASHCREEK13.800] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73763 [ASHCREEK13.800] CKT 2
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73714 [ASHCREAC115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73714 [ASHCREAC115.00] CKT 2
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
BAIRDASTK : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73696 [CONGRESS115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73755 [CONGRES213.800] CKT 1
BAIRDBSTK : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73697 [CONGRESS115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73755 [CONGRES213.800] CKT 1
BATESROCK1T : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
BECONFLSTK : OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73228 [BALDWNJB115.00] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73387 [BEACON F13.800] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73387 [BEACON F13.800] CKT 2
BOKUM2T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
BOKUM3T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73231 [BOKUM 115.00] CKT 1
BRANFORD1T : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
BRANFORD2T : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
BRANFORD4T : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
BRANFRDRR1T : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
BROADWYST1 : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
BUNKERH1T : OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
BUNKERH2T : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
BUNKERH3T : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
COLONY1T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
DARIEN1T : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
DEVON1TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
DEVON2TSTK : OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73125 [MILFORD 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
DEVON3TSTK : OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73125 [MILFORD 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73570 [DEVGAS1113.800] CKT 1
DEVON6TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
DEVON7TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73573 [DEVGAS1413.800] CKT 1
DEVON8TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73573 [DEVGAS1413.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
DEVON10TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73571 [DEVGAS1213.800] CKT 1
DEVON11TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73571 [DEVGAS1213.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
DEVON12TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73570 [DEVGAS1113.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73572 [DEVGAS1313.800] CKT 1
DEVON23TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73553 [DEVON#7 13.800] CKT 1
DEVON24TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
DEVON25TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73554 [DEVON#8 13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
DEVON26TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73554 [DEVON#8 13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
DEVON27TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
DEVSWST1TSTK: OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
DEVSWST2TSTK: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
DEVSWST3TSTK: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
DEVSWST4TSTK: OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
EDEVSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73129 [E.DEVONJ115.00] CKT 1
OPEN LINE FROM BUS 73125 [MILFORD 115.00] TO BUS 73129 [E.DEVONJ115.00] CKT 1
OPEN LINE FROM BUS 73125 [MILFORD 115.00] TO BUS 73574 [MILFD#1 13.800] CKT 1
OPEN LINE FROM BUS 73125 [MILFORD 115.00] TO BUS 73575 [MILFD#2 13.800] CKT 1
EMERIDEN1T : OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
ESHORE12TSTK: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73651 [NH HARBR22.000] CKT 1
FLAXHILL2T : OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
FROSTBR15T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
FROSTBR21T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
FROSTBR27T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73186 [BALDWINA115.00] TO BUS 73386 [BALDWINA13.800] CKT 1
GLENBROOK3T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
GLENBROOK8T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GRNDAV1TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
GRNDAV2TSTK : OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
GRNDAV3TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
GRNDAV4TSTK : OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
GRNDAV5TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
GRNDAV6TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
GRNDAV7TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
GREENHLL2T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
HADDAM1T : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73600 [CONN YAN115.00] CKT 1
HAWTHORNST : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 2
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
JUNEST1 : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
MLLRVR1TSTK : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73737 [MILLRIV213.800] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73737 [MILLRIV213.800] TO BUS 73676 [MILL RVR115.00] CKT 2
MLLRVR2TSTK : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73736 [MILLRIV113.800] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73736 [MILLRIV113.800] TO BUS 73676 [MILL RVR115.00] CKT 2
MIXAVE1 : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
NOHAVN1TSTK : OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 2
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73670 [QUINNIP 115.00] CKT 1
NOHAVN2TSTK : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 1
NWALLING1T : OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
NORWALKST1 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73143 [RDGEFLDA115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
NORWALKST2 : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73292 [NRWLK RX115.00] CKT 2
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
NORWLKHAR1T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR2T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR3T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR4T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR7T : OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
OLDTOWNST : OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 2
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
PEACEABLE1T : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73155 [RDGFLD J115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
PEQUON22TSTK: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73696 [CONGRESS115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
PEQUON32TSTK: OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73647 [BPTHBR#220.000] CKT 1
PEQUON42TSTK: OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73697 [CONGRESS115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73648 [BPTHBR#322.000] CKT 1
PLUMTREE25T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
PLUMTREE28T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
PLUMTREE31T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
QUINIPACST1 : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
ROCKRIVER1T : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73147 [BULLS BR115.00] CKT 1
SACKETST1 : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
SASCOCR1T : OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
SHEPAUG13A : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
SOUTHEND5T : OPEN LINE FROM BUS 73167 [SO.END 115.00] TO BUS 73144 [TOMAC 115.00] CKT 1
OPEN LINE FROM BUS 73144 [TOMAC 115.00] TO BUS 73163 [COS COB 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
SOUTHEND6T : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
SNAUGA1T : OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 2
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
SOTHNGTN12T : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
SOTHNGTN13T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOTHNGTN14T : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
SOTHNGTN15T : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
SOTHNGTN16T : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOTHNGTN20T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
SOTHNGTN22T : OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SOTHNGTN23T : OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN24T : OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN25T : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN26T : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
SOTHNGTN28T : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
STEVENSNSTK : OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
STONYHILL1T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
TRPFALLST1 : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
TRIANGLE4T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
OPEN LINE FROM BUS 73377 [TRIANGLA13.800] TO BUS 73383 [TRIANGLB13.800] CKT 1
WALLING1TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73594 [WALL LV113.800] CKT 1
WALLING2TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73195 [DEVON 115.00] CKT 1
WALLING3TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73595 [WALL LV213.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73596 [WALL LV313.800] CKT 1
WALLING4TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73595 [WALL LV213.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73596 [WALL LV313.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
WALLING5TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73594 [WALL LV113.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
WATERST1TSTK: OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
WATERST2TSTK: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
WATERSIDE2T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73162 [WATERSDE115.00] TO BUS 73163 [COS COB 115.00] CKT 1
WBROOKFLD1T : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
WRIVER1TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
WRIVER2TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
WESTON1T : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73292 [NRWLK RX115.00] CKT 2
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73158 [WESTON 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
WOODMNT1TSTK: OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73746 [WOODMONT13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
WOODMNT2TSTK: OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73746 [WOODMONT13.800] CKT 1
OPEN LINE FROM BUS 73685 [ALLINGSB115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
318-362STKBR: OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73588 [MERIDEN121.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73589 [MERIDEN221.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73590 [MERIDEN321.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73106 [SOUTHGTN345.00] CKT 1
CARD1TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
CARD1T+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73565 [LAKERD#121.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73566 [LAKERD#221.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73567 [LAKERD#321.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
CARD2TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
CARD3TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
CARD3T+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73565 [LAKERD#121.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73566 [LAKERD#221.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73567 [LAKERD#321.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
HADNKSTBKR : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73109 [MONTVILE345.00] CKT 1
LONGMT5TSTK : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
LUDLOWSTBKR : OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72929 [BELCH301345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
OPEN LINE FROM BUS 72929 [BELCH301345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
OPEN LINE FROM BUS 71797 [MILLBURY345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
MANCH21TSTK : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73111 [NOBLMFLD345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
MONTVSTBKR : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 2
NOMNTSTBKR : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
NMSTBKREAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
SCOVRK4TSTK : OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK5TSTK : OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73664 [NHHHVDCL345.00] TO BUS 73665 [NHHHVDCL191.50] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK7TSTK : OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73114 [PORT JCT345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK8TSTK : OPEN LINE FROM BUS 73107 [SCOVL RK345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SGTN1TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SGTN3TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SGTN4TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
SGTN5TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
SGTN6TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
SGTN7TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
NORGLENLINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
NHBRGLENLINE: OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWALKST1 : OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWALKST2 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
NORWALKST3 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR1T : OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
NORWLKHAR2T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR3T : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 2
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 3
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR4T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR7T : OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHARBT : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 2
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 3
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
GLNBRKASTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
GLNBRKA1STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
GLNBRKA2STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
GLNBRKA3STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
GLNBRKA4STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
GLNBRKBSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
GLNBRKB1STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
GLNBRKB2STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GLNBRKB3STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
GLNBRKB4STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
GLNBRKCSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
GLNBRKDSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GLNBRKESTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
DC1-BES-NOR : REMOVE MACHINE 1 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 1 FROM BUS 73293 [NORWALK 345.00]
DC2-BES-SIN : REMOVE MACHINE 2 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 2 FROM BUS 73700 [PEQUONIC115.00]
DC3-BES-DEV : REMOVE MACHINE 3 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 3 FROM BUS 73129 [E.DEVONJ115.00]
DC4-SIN-NOR : REMOVE MACHINE 4 FROM BUS 73700 [PEQUONIC115.00]
REMOVE MACHINE 4 FROM BUS 73293 [NORWALK 345.00]
DC5-DEV-NOR : REMOVE MACHINE 5 FROM BUS 73129 [E.DEVONJ115.00]
REMOVE MACHINE 5 FROM BUS 73293 [NORWALK 345.00]

## nonconverged
ACCC NON-CONVERGED NETWORK REPORT:
BUS MISMATCH TOLERANCE= 2.5000 MVA
SYSTEM MISMATCH TOLERANCE= 20.0000 MVA
DISTRIBUTION FACTOR FILE: DC-ph2-alt2-ne-ny-091503-2-upg-redisp2.dfx
SUBSYSTEM DESCRIPTION FILE: swctnew.sub
MONITORED ELEMENT FILE: swct0802.mon
CONTINGENCY DESCRIPTION FILE: contigphase2-091503-newDC.con
X--MISMATCH (MVA)--X
CONTINGENCY BUS SYSTEM TERMINATION CONDITION
TRIANGLE2T 70.167 590.73 ITERATION LIMIT EXCEEDED
TRIANGLE3T 60.126 546.76 ITERATION LIMIT EXCEEDED
CONTINGENCY LEGEND
LABEL EVENTS
TRIANGLE2T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
TRIANGLE3T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2