## Sheet2
ACCC OVERLOAD REPORT: MONITORED ELEMENTS LOADED ABOVE 100.0 % OF RATING SET B
Sort This Column for Lookup | MONITORED ELEMENT | [8 empty] | CONTINGENCY | RATE | FLOW | % | Other Case | Diff
73166-73171-1-DEVON2TSTK | 73166 | * | NORHR138 | 138 | 73171 |  | NWLK HAR | 115 | 1 | DEVON2TSTK | 402 | 392.4 | 97.6 | #N/A | 2.6
73166-73171-1-DEVON3TSTK | 73166 | * | NORHR138 | 138 | 73171 |  | NWLK HAR | 115 | 1 | DEVON3TSTK | 402 | 388 | 96.5 | #N/A | 1.5
70521-70555-1-354LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 354LINE | 50 | 53.6 | 107.2 | 106.2 | 1
73210-73611-1-1080-1280DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080-1280DCT | 183 | 196.3 | 112.5 | 111.6 | 0.9
73210-73611-1-1070-1080DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1070-1080DCT | 183 | 196.4 | 112.5 | 111.7 | 0.8
73210-73611-1-1080-1490DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080-1490DCT | 183 | 196.4 | 112.5 | 111.7 | 0.8
73210-73611-1-1080LINE | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080LINE | 183 | 196.4 | 112.5 | 111.7 | 0.8
70557-70714-1-BASE CASE | 70557 | * | Q CITY | 115 | 70714 |  | Q CTY 34 | 34.5 | 1 | BASE CASE | 50 | 52.3 | 104.7 | 104 | 0.7
70521-70555-1-BASE CASE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | BASE CASE | 50 | 52.2 | 104.3 | 103.7 | 0.6
73339-73340-1-1625LINE | 73339 |  | BARBR HL | 69 | 73340 | * | ROCKVILL | 69 | 1 | 1625LINE | 84 | 90.3 | 113.1 | 112.6 | 0.5
70512-70719-1-LOSSMP3 | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | LOSSMP3 | 50 | 51.2 | 102.4 | 102.2 | 0.2
70712-70719-1-LOSSMP3 | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | LOSSMP3 | 50 | 49.6 | 98.1 | 97.9 | 0.2
70512-70719-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 50.2 | 100.4 | 100.3 | 0.1
73107-73116-1-310-348WDCT | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | 310-348WDCT | 436 | 428.4 | 95.1 | #N/A | 0.1
70490-70504-1-BASE CASE | 70490 | * | VERNONRD | 115 | 70504 |  | SBRAT 69 | 69 | 1 | BASE CASE | 24 | 25 | 104.2 | 104.2 | 0
70512-70735-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70735 |  | WILL #2 | 34.5 | 1 | BASE CASE | 50 | 48.8 | 97.5 | 97.5 | 0
70712-70719-1-BASE CASE | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 48.6 | 96.1 | 96.1 | 0
70721-70740-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70740 |  | 10-20 | 13.8 | 1 | BASE CASE | 20 | 26.1 | 130.5 | 130.5 | 0
73107-73116-1-1975-348DCT | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | 1975-348DCT | 436 | 428.4 | 95 | #N/A | 0
73144-73167-1-1440-1450DCT | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440-1450DCT | 252 | 255.3 | 99.2 | 99.2 | 0
73144-73167-1-1440LINE | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440LINE | 252 | 255.2 | 98.8 | 98.8 | 0
73144-73167-1-GLENBROOK3T | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLENBROOK3T | 252 | 255.2 | 98.8 | 98.8 | 0
73144-73167-1-GLNBRKCSTK | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLNBRKCSTK | 252 | 255.2 | 98.8 | 98.8 | 0
73162-73163-1-SOUTHEND6T | 73162 |  | WATERSDE | 115 | 73163 | * | COS COB | 115 | 1 | SOUTHEND6T | 239 | 298.7 | 124.7 | 124.7 | 0
73162-73168-1-SOUTHEND6T | 73162 | * | WATERSDE | 115 | 73168 |  | GLNBROOK | 115 | 1 | SOUTHEND6T | 352 | 367 | 102.4 | 102.4 | 0
73167-73294-1-1440-1450DCT | 73167 | * | SO.END | 115 | 73294 |  | GLNBRK J | 115 | 1 | 1440-1450DCT | 289 | 365.7 | 123.2 | 123.2 | 0
73144-73167-1-GLNBRKA2STK | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLNBRKA2STK | 252 | 255.3 | 99 | 99.2 | -0.2
70521-70555-1-312+393LNS | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 312+393LNS | 50 | 53.2 | 106.4 | 106.8 | -0.4
70521-70555-1-312+393REAC | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 312+393REAC | 50 | 53.2 | 106.4 | 106.8 | -0.4
70521-70555-1-312LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 312LINE | 50 | 53.2 | 106.4 | 106.8 | -0.4
73170-73176-1-1165LINE | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | 1165LINE | 138 | 144.6 | 103.7 | 104.3 | -0.6
73170-73176-1-PLUMTREE31T | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | PLUMTREE31T | 138 | 139.7 | 99.7 | 100.3 | -0.6
70721-70732-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70732 |  | MCNEIL T | 34.5 | 1 | BASE CASE | 30 | 29.8 | 102.1 | 102.7 | -0.6
73170-73176-2-1060-1270DCT | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 2 | 1060-1270DCT | 166 | 224.8 | 133.9 | 134.6 | -0.7
73176-73268-1-1060-1165DCT | 73176 | * | TRIANGLE | 115 | 73268 |  | MIDDLRIV | 115 | 1 | 1060-1165DCT | 134 | 146.8 | 110.4 | 111.1 | -0.7
73162-73163-1-GLNBRKA1STK | 73162 |  | WATERSDE | 115 | 73163 | * | COS COB | 115 | 1 | GLNBRKA1STK | 239 | 248.4 | 102.3 | 103 | -0.7
73170-73268-1-1060-1165DCT | 73170 |  | PLUMTREE | 115 | 73268 | * | MIDDLRIV | 115 | 1 | 1060-1165DCT | 126 | 226 | 179.5 | 180.5 | -1
73244-73258-1-1207-1775DCT | 73258 | * | BLOOMFLD | 115 | 73244 |  | N.BLMFLD | 115 | 1 | 1207-1775DCT | 193 | 220.6 | 117.2 | 120 | -2.8
73251-73261-1-1207-1775DCT | 73251 |  | BLM JCT | 115 | 73261 | * | NW.HTFD | 115 | 1 | 1207-1775DCT | 228 | 250 | 112.6 | 116.8 | -4.2
73188-73192-1-BUNKERH2T | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | BUNKERH2T | 112 | 109 | 101.6 | 107.6 | -6
73188-73192-1-1272-1721DCT | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | 1272-1721DCT | 112 | 130.4 | 124.4 | 131.9 | -7.5
73227-73633-1-SGTN7TSTK | 73227 | * | E.MERIDN | 115 | 73633 |  | NO.WALLF | 115 | 1 | SGTN7TSTK | 112 | 110.7 | 97.1 | 108.1 | -11
73230-73231-1-1620SLINE | 73230 |  | HADDAM | 115 | 73231 | * | BOKUM | 115 | 1 | 1620SLINE | 165 | 164.1 | 99.2 | 111.4 | -12.2
73106-73154-2-SGTN5TSTK | 73106 |  | SOUTHGTN | 345 | 73154 | * | SGTN B | 115 | 2 | SGTN5TSTK | 585 | 579.2 | 99 | 111.6 | -12.6

## thermal
ACCC OVERLOAD REPORT: MONITORED ELEMENTS LOADED ABOVE 100.0 % OF RATING SET B
Sort This Column for Lookup | MONITORED ELEMENT | [8 empty] | CONTINGENCY | RATE | FLOW | % | Other Case | Diff
70490-70504-1-BASE CASE | 70490 | * | VERNONRD | 115 | 70504 |  | SBRAT 69 | 69 | 1 | BASE CASE | 24 | 25 | 104.2 | 104.2 | 0
70512-70719-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 50.2 | 100.4 | 100.3 | 0.1
70512-70719-1-LOSSMP3 | 70512 | * | ESX B-2 | 115 | 70719 |  | WILL #1 | 34.5 | 1 | LOSSMP3 | 50 | 51.2 | 102.4 | 102.2 | 0.2
70512-70735-1-BASE CASE | 70512 | * | ESX B-2 | 115 | 70735 |  | WILL #2 | 34.5 | 1 | BASE CASE | 50 | 48.8 | 97.5 | 97.5 | 0
70521-70555-1-312+393LNS | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 312+393LNS | 50 | 53.2 | 106.4 | 106.8 | -0.4
70521-70555-1-312+393REAC | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 312+393REAC | 50 | 53.2 | 106.4 | 106.8 | -0.4
70521-70555-1-312LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 312LINE | 50 | 53.2 | 106.4 | 106.8 | -0.4
70521-70555-1-354LINE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | 354LINE | 50 | 53.6 | 107.2 | 106.2 | 1
70521-70555-1-BASE CASE | 70521 | * | RUTLAND | 115 | 70555 |  | N RUT 46 | 46 | 1 | BASE CASE | 50 | 52.2 | 104.3 | 103.7 | 0.6
70557-70714-1-BASE CASE | 70557 | * | Q CITY | 115 | 70714 |  | Q CTY 34 | 34.5 | 1 | BASE CASE | 50 | 52.3 | 104.7 | 104 | 0.7
70712-70719-1-BASE CASE | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | BASE CASE | 50 | 48.6 | 96.1 | 96.1 | 0
70712-70719-1-LOSSMP3 | 70712 | * | ESSEX 19 | 34.5 | 70719 |  | WILL #1 | 34.5 | 1 | LOSSMP3 | 50 | 49.6 | 98.1 | 97.9 | 0.2
70721-70732-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70732 |  | MCNEIL T | 34.5 | 1 | BASE CASE | 30 | 29.8 | 102.1 | 102.7 | -0.6
70721-70740-1-BASE CASE | 70721 | * | BURL34 | 34.5 | 70740 |  | 10-20 | 13.8 | 1 | BASE CASE | 20 | 26.1 | 130.5 | 130.5 | 0
73106-73154-2-SGTN5TSTK | 73106 |  | SOUTHGTN | 345 | 73154 | * | SGTN B | 115 | 2 | SGTN5TSTK | 585 | 579.2 | 99 | 111.6 | -12.6
73107-73116-1-1975-348DCT | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | 1975-348DCT | 436 | 428.4 | 95 | #N/A | 0
73107-73116-1-310-348WDCT | 73107 | * | SCOVL RK | 345 | 73116 |  | MIDDLTWN | 345 | 1 | 310-348WDCT | 436 | 428.4 | 95.1 | #N/A | 0.1
73144-73167-1-1440-1450DCT | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440-1450DCT | 252 | 255.3 | 99.2 | 99.2 | 0
73144-73167-1-1440LINE | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | 1440LINE | 252 | 255.2 | 98.8 | 98.8 | 0
73144-73167-1-GLENBROOK3T | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLENBROOK3T | 252 | 255.2 | 98.8 | 98.8 | 0
73144-73167-1-GLNBRKA2STK | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLNBRKA2STK | 252 | 255.3 | 99 | 99.2 | -0.2
73144-73167-1-GLNBRKCSTK | 73144 | * | TOMAC | 115 | 73167 |  | SO.END | 115 | 1 | GLNBRKCSTK | 252 | 255.2 | 98.8 | 98.8 | 0
73162-73163-1-GLNBRKA1STK | 73162 |  | WATERSDE | 115 | 73163 | * | COS COB | 115 | 1 | GLNBRKA1STK | 239 | 248.4 | 102.3 | 103 | -0.7
73162-73163-1-SOUTHEND6T | 73162 |  | WATERSDE | 115 | 73163 | * | COS COB | 115 | 1 | SOUTHEND6T | 239 | 298.7 | 124.7 | 124.7 | 0
73162-73168-1-SOUTHEND6T | 73162 | * | WATERSDE | 115 | 73168 |  | GLNBROOK | 115 | 1 | SOUTHEND6T | 352 | 367 | 102.4 | 102.4 | 0
73166-73171-1-DEVON2TSTK | 73166 | * | NORHR138 | 138 | 73171 |  | NWLK HAR | 115 | 1 | DEVON2TSTK | 402 | 392.4 | 97.6 | #N/A | 2.6
73166-73171-1-DEVON3TSTK | 73166 | * | NORHR138 | 138 | 73171 |  | NWLK HAR | 115 | 1 | DEVON3TSTK | 402 | 388 | 96.5 | #N/A | 1.5
73167-73294-1-1440-1450DCT | 73167 | * | SO.END | 115 | 73294 |  | GLNBRK J | 115 | 1 | 1440-1450DCT | 289 | 365.7 | 123.2 | 123.2 | 0
73170-73176-1-1165LINE | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | 1165LINE | 138 | 144.6 | 103.7 | 104.3 | -0.6
73170-73176-1-PLUMTREE31T | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 1 | PLUMTREE31T | 138 | 139.7 | 99.7 | 100.3 | -0.6
73170-73176-2-1060-1270DCT | 73170 |  | PLUMTREE | 115 | 73176 | * | TRIANGLE | 115 | 2 | 1060-1270DCT | 166 | 224.8 | 133.9 | 134.6 | -0.7
73170-73268-1-1060-1165DCT | 73170 |  | PLUMTREE | 115 | 73268 | * | MIDDLRIV | 115 | 1 | 1060-1165DCT | 126 | 226 | 179.5 | 180.5 | -1
73176-73268-1-1060-1165DCT | 73176 | * | TRIANGLE | 115 | 73268 |  | MIDDLRIV | 115 | 1 | 1060-1165DCT | 134 | 146.8 | 110.4 | 111.1 | -0.7
73188-73192-1-1272-1721DCT | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | 1272-1721DCT | 112 | 130.4 | 124.4 | 131.9 | -7.5
73188-73192-1-BUNKERH2T | 73188 | * | BCNFL PF | 115 | 73192 |  | DRBY J B | 115 | 1 | BUNKERH2T | 112 | 109 | 101.6 | 107.6 | -6
73210-73611-1-1070-1080DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1070-1080DCT | 183 | 196.4 | 112.5 | 111.7 | 0.8
73210-73611-1-1080-1280DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080-1280DCT | 183 | 196.3 | 112.5 | 111.6 | 0.9
73210-73611-1-1080-1490DCT | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080-1490DCT | 183 | 196.4 | 112.5 | 111.7 | 0.8
73210-73611-1-1080LINE | 73210 |  | MONTVLLE | 115 | 73611 | * | DUDLEY T | 115 | 1 | 1080LINE | 183 | 196.4 | 112.5 | 111.7 | 0.8
73227-73633-1-SGTN7TSTK | 73227 | * | E.MERIDN | 115 | 73633 |  | NO.WALLF | 115 | 1 | SGTN7TSTK | 112 | 110.7 | 97.1 | 108.1 | -11
73230-73231-1-1620SLINE | 73230 |  | HADDAM | 115 | 73231 | * | BOKUM | 115 | 1 | 1620SLINE | 165 | 164.1 | 99.2 | 111.4 | -12.2
73244-73258-1-1207-1775DCT | 73258 | * | BLOOMFLD | 115 | 73244 |  | N.BLMFLD | 115 | 1 | 1207-1775DCT | 193 | 220.6 | 117.2 | 120 | -2.8
73251-73261-1-1207-1775DCT | 73251 |  | BLM JCT | 115 | 73261 | * | NW.HTFD | 115 | 1 | 1207-1775DCT | 228 | 250 | 112.6 | 116.8 | -4.2
73339-73340-1-1625LINE | 73339 |  | BARBR HL | 69 | 73340 | * | ROCKVILL | 69 | 1 | 1625LINE | 84 | 90.3 | 113.1 | 112.6 | 0.5

## voltage
MONITORED VOLTAGE REPORT
Sort This Column for Lookup | SYSTEM |  | CONTINGENCY | BUS |  |  | V-CONT | V-INIT | V-MAX | V-MIN | Other Case | Diff
70622-354LINE | ZONE 41 | RANGE | 354LINE | 70622 | WHITE RV | 13.8 | 1.0515 | 1.0546 | 1.05 | 0.9 | #N/A | 0.0015
70622-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70622 | WHITE RV | 13.8 | 1.0546 | 1.0546 | 1.05 | 0.9 | 1.0546 | 0
70625-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70625 | WTRFORD | 34.5 | 1.0585 | 1.0585 | 1.05 | 0.9 | 1.0588 | -0.0003
70626-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70626 | GILMAN | 34.5 | 1.0599 | 1.0599 | 1.05 | 0.9 | 1.0604 | -0.0005
70639-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70639 | HGATE VL | 46 | 1.0554 | 1.0554 | 1.05 | 0.9 | 1.0554 | 0
70640-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70640 | MISSQ P | 48 | 1.0554 | 1.0554 | 1.05 | 0.9 | 1.0554 | 0
70693-1460-387DCT | ZONE 41 | RANGE | 1460-387DCT | 70693 | ESX-STAT | 3.2 | 1.0578 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0078
70693-312+393LNS | ZONE 41 | RANGE | 312+393LNS | 70693 | ESX-STAT | 3.2 | 1.0575 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0075
70693-312+393REAC | ZONE 41 | RANGE | 312+393REAC | 70693 | ESX-STAT | 3.2 | 1.0575 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0075
70693-312LINE | ZONE 41 | RANGE | 312LINE | 70693 | ESX-STAT | 3.2 | 1.0575 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0075
70693-318-362STKBR | ZONE 41 | RANGE | 318-362STKBR | 70693 | ESX-STAT | 3.2 | 1.0653 | 1.0606 | 1.05 | 0.9 | 1.065 | 0.0003
70693-330+LAKE | ZONE 41 | RANGE | 330+LAKE | 70693 | ESX-STAT | 3.2 | 1.068 | 1.0606 | 1.05 | 0.9 | 1.0665 | 0.0015
70693-330LINE | ZONE 41 | RANGE | 330LINE | 70693 | ESX-STAT | 3.2 | 1.0577 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0077
70693-347+LAKE | ZONE 41 | RANGE | 347+LAKE | 70693 | ESX-STAT | 3.2 | 1.068 | 1.0606 | 1.05 | 0.9 | 1.0665 | 0.0015
70693-384LINE | ZONE 41 | RANGE | 384LINE | 70693 | ESX-STAT | 3.2 | 1.064 | 1.0606 | 1.05 | 0.9 | 1.0639 | 0.0001
70693-387+AUTOS | ZONE 41 | RANGE | 387+AUTOS | 70693 | ESX-STAT | 3.2 | 1.0578 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0078
70693-393LINE | ZONE 41 | RANGE | 393LINE | 70693 | ESX-STAT | 3.2 | 1.0579 | 1.0606 | 1.05 | 0.9 | 1.0581 | -0.0002
70693-BASE CASE | ZONE 41 | RANGE | BASE CASE | 70693 | ESX-STAT | 3.2 | 1.0606 | 1.0606 | 1.05 | 0.9 | 1.061 | -0.0004
70693-CARD1T+LAKE | ZONE 41 | RANGE | CARD1T+LAKE | 70693 | ESX-STAT | 3.2 | 1.0682 | 1.0606 | 1.05 | 0.9 | 1.0667 | 0.0015
70693-CARD1TSTK | ZONE 41 | RANGE | CARD1TSTK | 70693 | ESX-STAT | 3.2 | 1.0578 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0078
70693-CARD3T+LAKE | ZONE 41 | RANGE | CARD3T+LAKE | 70693 | ESX-STAT | 3.2 | 1.0682 | 1.0606 | 1.05 | 0.9 | 1.0667 | 0.0015
70693-CARD3TSTK | ZONE 41 | RANGE | CARD3TSTK | 70693 | ESX-STAT | 3.2 | 1.0578 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0078
70693-DC4-SIN-NOR | ZONE 41 | RANGE | DC4-SIN-NOR | 70693 | ESX-STAT | 3.2 | 1.0571 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0071
70693-DC5-DEV-NOR | ZONE 41 | RANGE | DC5-DEV-NOR | 70693 | ESX-STAT | 3.2 | 1.0655 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0155
70693-DEVON2TSTK | ZONE 41 | RANGE | DEVON2TSTK | 70693 | ESX-STAT | 3.2 | 1.0662 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0162
70693-DEVON3TSTK | ZONE 41 | RANGE | DEVON3TSTK | 70693 | ESX-STAT | 3.2 | 1.0663 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0163
70693-LOLAKERD | ZONE 41 | RANGE | LOLAKERD | 70693 | ESX-STAT | 3.2 | 1.0635 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0135
70693-LOSSBPT3 | ZONE 41 | RANGE | LOSSBPT3 | 70693 | ESX-STAT | 3.2 | 1.0631 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0131
70693-LOSSMID4 | ZONE 41 | RANGE | LOSSMID4 | 70693 | ESX-STAT | 3.2 | 1.064 | 1.0606 | 1.05 | 0.9 | 1.0639 | 0.0001
70693-LOSSMON6 | ZONE 41 | RANGE | LOSSMON6 | 70693 | ESX-STAT | 3.2 | 1.0642 | 1.0606 | 1.05 | 0.9 | 1.0641 | 0.0001
70693-LOSSMP2 | ZONE 41 | RANGE | LOSSMP2 | 70693 | ESX-STAT | 3.2 | 1.0696 | 1.0606 | 1.05 | 0.9 | 1.0686 | 0.001
70693-LOSSMP3 | ZONE 41 | RANGE | LOSSMP3 | 70693 | ESX-STAT | 3.2 | 1.0736 | 1.0606 | 1.05 | 0.9 | 1.0721 | 0.0015
70693-NMSTBKREAC | ZONE 41 | RANGE | NMSTBKREAC | 70693 | ESX-STAT | 3.2 | 1.0577 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0077
70693-NOMNTSTBKR | ZONE 41 | RANGE | NOMNTSTBKR | 70693 | ESX-STAT | 3.2 | 1.0577 | 1.0606 | 1.05 | 0.9 | #N/A | 0.0077
73125-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73125 | MILFORD | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73129-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73129 | E.DEVONJ | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73151-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73151 | UNCASVLA | 115 | 1.0534 | 1.0122 | 1.05 | 0.9 | 1.0539 | -0.0005
73152-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73152 | UNCASVLB | 115 | 1.0536 | 1.0125 | 1.05 | 0.9 | 1.0541 | -0.0005
73153-1508LINE | ZONE 171 | RANGE | 1508LINE | 73153 | BRANFORD | 115 | 1.0508 | 1.0343 | 1.05 | 0.9 | #N/A | 0.0008
73153-BRANFORD1T | ZONE 171 | RANGE | BRANFORD1T | 73153 | BRANFORD | 115 | 1.0525 | 1.0343 | 1.05 | 0.9 | #N/A | 0.0025
73153-BRANFORD4T | ZONE 171 | RANGE | BRANFORD4T | 73153 | BRANFORD | 115 | 1.0549 | 1.0343 | 1.05 | 0.9 | #N/A | 0.0049
73153-GREENHLL2T | ZONE 171 | RANGE | GREENHLL2T | 73153 | BRANFORD | 115 | 1.0509 | 1.0343 | 1.05 | 0.9 | #N/A | 0.0009
73161-1625LINE | ZONE 171 | RANGE | 1625LINE | 73161 | ROCKVILL | 115 | 0.8415 | 0.9887 | 1.05 | 0.9 | 0.8455 | -0.004
73202-352+AUTO | ZONE 171 | RANGE | 352+AUTO | 73202 | FROST BR | 115 | 1.0501 | 1.029 | 1.05 | 0.9 | #N/A | 0.0001
73210-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73210 | MONTVLLE | 115 | 1.0538 | 1.0127 | 1.05 | 0.9 | 1.0543 | -0.0005
73216-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73216 | WHIP JCT | 115 | 1.0502 | 1.0114 | 1.05 | 0.9 | 1.0507 | -0.0005
73223-1070-1080DCT | ZONE 171 | RANGE | 1070-1080DCT | 73223 | FRYBRT05 | 115 | 0.8975 | 0.9623 | 1.05 | 0.9 | #N/A | -0.0025
73223-1080-1280DCT | ZONE 171 | RANGE | 1080-1280DCT | 73223 | FRYBRT05 | 115 | 0.8971 | 0.9623 | 1.05 | 0.9 | #N/A | -0.0029
73223-1080-1490DCT | ZONE 171 | RANGE | 1080-1490DCT | 73223 | FRYBRT05 | 115 | 0.8976 | 0.9623 | 1.05 | 0.9 | #N/A | -0.0024
73223-1080LINE | ZONE 171 | RANGE | 1080LINE | 73223 | FRYBRT05 | 115 | 0.8974 | 0.9623 | 1.05 | 0.9 | #N/A | -0.0026
73236-1070-1080DCT | ZONE 171 | RANGE | 1070-1080DCT | 73236 | FRYBR05 | 115 | 0.8971 | 0.962 | 1.05 | 0.9 | #N/A | -0.0029
73236-1080-1280DCT | ZONE 171 | RANGE | 1080-1280DCT | 73236 | FRYBR05 | 115 | 0.8967 | 0.962 | 1.05 | 0.9 | #N/A | -0.0033
73236-1080-1490DCT | ZONE 171 | RANGE | 1080-1490DCT | 73236 | FRYBR05 | 115 | 0.8972 | 0.962 | 1.05 | 0.9 | #N/A | -0.0028
73236-1080LINE | ZONE 171 | RANGE | 1080LINE | 73236 | FRYBR05 | 115 | 0.897 | 0.962 | 1.05 | 0.9 | #N/A | -0.003
73267-1867-1977DCT | ZONE 171 | RANGE | 1867-1977DCT | 73267 | DARIEN | 115 | 1.0658 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0158
73267-1880-1977DCT | ZONE 171 | RANGE | 1880-1977DCT | 73267 | DARIEN | 115 | 1.0658 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0158
73267-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73267 | DARIEN | 115 | 1.0658 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0158
73267-1977LINENEW | ZONE 171 | RANGE | 1977LINENEW | 73267 | DARIEN | 115 | 1.0658 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0158
73267-GLNBRKASTK | ZONE 171 | RANGE | GLNBRKASTK | 73267 | DARIEN | 115 | 1.0658 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0158
73267-SOUTHEND5T | ZONE 171 | RANGE | SOUTHEND5T | 73267 | DARIEN | 115 | 1.0658 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0158
73267-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73267 | DARIEN | 115 | 1.0658 | 1.0384 | 1.05 | 0.9 | #N/A | 0.0158
73270-1070-1080DCT | ZONE 171 | RANGE | 1070-1080DCT | 73270 | BROOKLYN | 115 | 0.8816 | 0.9485 | 1.05 | 0.9 | 0.8868 | -0.0052
73270-1080-1280DCT | ZONE 171 | RANGE | 1080-1280DCT | 73270 | BROOKLYN | 115 | 0.8812 | 0.9485 | 1.05 | 0.9 | 0.8875 | -0.0063
73270-1080-1490DCT | ZONE 171 | RANGE | 1080-1490DCT | 73270 | BROOKLYN | 115 | 0.8817 | 0.9485 | 1.05 | 0.9 | 0.8869 | -0.0052
73270-1080LINE | ZONE 171 | RANGE | 1080LINE | 73270 | BROOKLYN | 115 | 0.8815 | 0.9485 | 1.05 | 0.9 | 0.8867 | -0.0052
73278-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73278 | MONT DSL | 115 | 1.0538 | 1.0127 | 1.05 | 0.9 | 1.0543 | -0.0005
73286-1867-1977DCT | ZONE 171 | RANGE | 1867-1977DCT | 73286 | COMPO | 115 | 1.0559 | 1.0411 | 1.05 | 0.9 | #N/A | 0.0059
73286-1880-1977DCT | ZONE 171 | RANGE | 1880-1977DCT | 73286 | COMPO | 115 | 1.0559 | 1.0411 | 1.05 | 0.9 | #N/A | 0.0059
73286-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73286 | COMPO | 115 | 1.0559 | 1.0411 | 1.05 | 0.9 | #N/A | 0.0059
73286-1977LINENEW | ZONE 171 | RANGE | 1977LINENEW | 73286 | COMPO | 115 | 1.0559 | 1.0411 | 1.05 | 0.9 | #N/A | 0.0059
73286-GLNBRKASTK | ZONE 171 | RANGE | GLNBRKASTK | 73286 | COMPO | 115 | 1.0559 | 1.0411 | 1.05 | 0.9 | #N/A | 0.0059
73286-SOUTHEND5T | ZONE 171 | RANGE | SOUTHEND5T | 73286 | COMPO | 115 | 1.0559 | 1.0411 | 1.05 | 0.9 | #N/A | 0.0059
73286-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73286 | COMPO | 115 | 1.0559 | 1.0411 | 1.05 | 0.9 | #N/A | 0.0059
73293-1565-PLNRDCT | '345KV ' | RANGE | 1565-PLNRDCT | 73293 | NORWALK | 345 | 1.05 | 1.026 | 1.05 | 0.95 | #N/A | 0
73293-1565-PLNRDCT | ZONE 171 | RANGE | 1565-PLNRDCT | 73293 | NORWALK | 345 | 1.05 | 1.026 | 1.05 | 0.9 | #N/A | 0
73293-398LINE | '345KV ' | RANGE | 398LINE | 73293 | NORWALK | 345 | 1.05 | 1.026 | 1.05 | 0.95 | #N/A | 0
73293-398LINE | ZONE 171 | RANGE | 398LINE | 73293 | NORWALK | 345 | 1.05 | 1.026 | 1.05 | 0.9 | #N/A | 0
73293-398LREAC | '345KV ' | RANGE | 398LREAC | 73293 | NORWALK | 345 | 1.05 | 1.026 | 1.05 | 0.95 | #N/A | 0
73293-398LREAC | ZONE 171 | RANGE | 398LREAC | 73293 | NORWALK | 345 | 1.05 | 1.026 | 1.05 | 0.9 | #N/A | 0
73293-PLUMNOR | '345KV ' | RANGE | PLUMNOR | 73293 | NORWALK | 345 | 1.05 | 1.026 | 1.05 | 0.95 | #N/A | 0
73293-PLUMNOR | ZONE 171 | RANGE | PLUMNOR | 73293 | NORWALK | 345 | 1.05 | 1.026 | 1.05 | 0.9 | #N/A | 0
73300-1867-1977DCT | ZONE 171 | RANGE | 1867-1977DCT | 73300 | ELYTAP | 115 | 1.0615 | 1.0396 | 1.05 | 0.9 | #N/A | 0.0115
73300-1880-1977DCT | ZONE 171 | RANGE | 1880-1977DCT | 73300 | ELYTAP | 115 | 1.0615 | 1.0396 | 1.05 | 0.9 | #N/A | 0.0115
73300-1890-1977DCT | ZONE 171 | RANGE | 1890-1977DCT | 73300 | ELYTAP | 115 | 1.0615 | 1.0396 | 1.05 | 0.9 | #N/A | 0.0115
73300-1977LINENEW | ZONE 171 | RANGE | 1977LINENEW | 73300 | ELYTAP | 115 | 1.0615 | 1.0396 | 1.05 | 0.9 | #N/A | 0.0115
73300-GLNBRKASTK | ZONE 171 | RANGE | GLNBRKASTK | 73300 | ELYTAP | 115 | 1.0615 | 1.0396 | 1.05 | 0.9 | #N/A | 0.0115
73300-SOUTHEND5T | ZONE 171 | RANGE | SOUTHEND5T | 73300 | ELYTAP | 115 | 1.0615 | 1.0396 | 1.05 | 0.9 | #N/A | 0.0115
73300-SOUTHEND6T | ZONE 171 | RANGE | SOUTHEND6T | 73300 | ELYTAP | 115 | 1.0615 | 1.0396 | 1.05 | 0.9 | #N/A | 0.0115
73388-1460-387DCT | ZONE 171 | RANGE | 1460-387DCT | 73388 | SO.NAUG | 13.8 | 1.0542 | 1.057 | 1.05 | 0.9 | #N/A | 0.0042
73388-1545+SPS | ZONE 171 | RANGE | 1545+SPS | 73388 | SO.NAUG | 13.8 | 1.0536 | 1.057 | 1.05 | 0.9 | #N/A | 0.0036
73388-1545-1570DCT | ZONE 171 | RANGE | 1545-1570DCT | 73388 | SO.NAUG | 13.8 | 1.0519 | 1.057 | 1.05 | 0.9 | #N/A | 0.0019
73388-1545LINE | ZONE 171 | RANGE | 1545LINE | 73388 | SO.NAUG | 13.8 | 1.0544 | 1.057 | 1.05 | 0.9 | #N/A | 0.0044
73388-1560-1570DCT | ZONE 171 | RANGE | 1560-1570DCT | 73388 | SO.NAUG | 13.8 | 1.0536 | 1.057 | 1.05 | 0.9 | #N/A | 0.0036
73388-1565-PLNRDCT | ZONE 171 | RANGE | 1565-PLNRDCT | 73388 | SO.NAUG | 13.8 | 1.0541 | 1.057 | 1.05 | 0.9 | #N/A | 0.0041
73388-1570-1575DCT | ZONE 171 | RANGE | 1570-1575DCT | 73388 | SO.NAUG | 13.8 | 1.0609 | 1.057 | 1.05 | 0.9 | 1.0504 | 0.0105
73388-1570LINE | ZONE 171 | RANGE | 1570LINE | 73388 | SO.NAUG | 13.8 | 1.0527 | 1.057 | 1.05 | 0.9 | #N/A | 0.0027
73388-1575-1585DCT | ZONE 171 | RANGE | 1575-1585DCT | 73388 | SO.NAUG | 13.8 | 1.0528 | 1.057 | 1.05 | 0.9 | #N/A | 0.0028
73388-1575LINE | ZONE 171 | RANGE | 1575LINE | 73388 | SO.NAUG | 13.8 | 1.0608 | 1.057 | 1.05 | 0.9 | #N/A | 0.0108
73388-1585LINE | ZONE 171 | RANGE | 1585LINE | 73388 | SO.NAUG | 13.8 | 1.0533 | 1.057 | 1.05 | 0.9 | #N/A | 0.0033
73388-1721LINE | ZONE 171 | RANGE | 1721LINE | 73388 | SO.NAUG | 13.8 | 1.054 | 1.057 | 1.05 | 0.9 | #N/A | 0.004
73388-1770-321DCT | ZONE 171 | RANGE | 1770-321DCT | 73388 | SO.NAUG | 13.8 | 1.0541 | 1.057 | 1.05 | 0.9 | #N/A | 0.0041
73388-1770LINE | ZONE 171 | RANGE | 1770LINE | 73388 | SO.NAUG | 13.8 | 1.0541 | 1.057 | 1.05 | 0.9 | #N/A | 0.0041
73388-329-352DCT | ZONE 171 | RANGE | 329-352DCT | 73388 | SO.NAUG | 13.8 | 1.0694 | 1.057 | 1.05 | 0.9 | 1.0508 | 0.0186
73388-352+AUTO | ZONE 171 | RANGE | 352+AUTO | 73388 | SO.NAUG | 13.8 | 1.0696 | 1.057 | 1.05 | 0.9 | 1.0509 | 0.0187
73388-387+AUTOS | ZONE 171 | RANGE | 387+AUTOS | 73388 | SO.NAUG | 13.8 | 1.0544 | 1.057 | 1.05 | 0.9 | #N/A | 0.0044
73388-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73388 | SO.NAUG | 13.8 | 1.057 | 1.057 | 1.05 | 0.9 | #N/A | 0.007
73388-BUNKERH1T | ZONE 171 | RANGE | BUNKERH1T | 73388 | SO.NAUG | 13.8 | 1.0601 | 1.057 | 1.05 | 0.9 | #N/A | 0.0101
73388-BUNKERH3T | ZONE 171 | RANGE | BUNKERH3T | 73388 | SO.NAUG | 13.8 | 1.053 | 1.057 | 1.05 | 0.9 | #N/A | 0.003
73388-DC1-BES-NOR | ZONE 171 | RANGE | DC1-BES-NOR | 73388 | SO.NAUG | 13.8 | 1.0542 | 1.057 | 1.05 | 0.9 | #N/A | 0.0042
73388-DC3-BES-DEV | ZONE 171 | RANGE | DC3-BES-DEV | 73388 | SO.NAUG | 13.8 | 1.0534 | 1.057 | 1.05 | 0.9 | #N/A | 0.0034
73388-DC4-SIN-NOR | ZONE 171 | RANGE | DC4-SIN-NOR | 73388 | SO.NAUG | 13.8 | 1.0545 | 1.057 | 1.05 | 0.9 | #N/A | 0.0045
73388-DC5-DEV-NOR | ZONE 171 | RANGE | DC5-DEV-NOR | 73388 | SO.NAUG | 13.8 | 1.0526 | 1.057 | 1.05 | 0.9 | #N/A | 0.0026
73388-DEVON6TSTK | ZONE 171 | RANGE | DEVON6TSTK | 73388 | SO.NAUG | 13.8 | 1.0519 | 1.057 | 1.05 | 0.9 | #N/A | 0.0019
73388-DEVON7TSTK | ZONE 171 | RANGE | DEVON7TSTK | 73388 | SO.NAUG | 13.8 | 1.0527 | 1.057 | 1.05 | 0.9 | #N/A | 0.0027
73388-PLUMTREE25T | ZONE 171 | RANGE | PLUMTREE25T | 73388 | SO.NAUG | 13.8 | 1.0538 | 1.057 | 1.05 | 0.9 | #N/A | 0.0038
73399-329-352DCT | ZONE 171 | RANGE | 329-352DCT | 73399 | NOERA | 13.8 | 1.0579 | 1.0401 | 1.05 | 0.9 | #N/A | 0.0079
73399-352+AUTO | ZONE 171 | RANGE | 352+AUTO | 73399 | NOERA | 13.8 | 1.0581 | 1.0401 | 1.05 | 0.9 | #N/A | 0.0081
73448-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73448 | UNCASVIL | 27.6 | 1.0511 | 1.0099 | 1.05 | 0.9 | 1.0516 | -0.0005
73476-1070-1080DCT | ZONE 171 | RANGE | 1070-1080DCT | 73476 | TRACY05 | 115 | 0.8757 | 0.9433 | 1.05 | 0.9 | 0.881 | -0.0053
73476-1080-1280DCT | ZONE 171 | RANGE | 1080-1280DCT | 73476 | TRACY05 | 115 | 0.8753 | 0.9433 | 1.05 | 0.9 | 0.8817 | -0.0064
73476-1080-1490DCT | ZONE 171 | RANGE | 1080-1490DCT | 73476 | TRACY05 | 115 | 0.8757 | 0.9433 | 1.05 | 0.9 | 0.881 | -0.0053
73476-1080LINE | ZONE 171 | RANGE | 1080LINE | 73476 | TRACY05 | 115 | 0.8755 | 0.9433 | 1.05 | 0.9 | 0.8808 | -0.0053
73574-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73574 | MILFD#1 | 13.8 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73575-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73575 | MILFD#2 | 13.8 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73597-1100-1200DCT | ZONE 171 | RANGE | 1100-1200DCT | 73597 | KLEENCT1 | 18 | 1.1146 | 1.1189 | 1.05 | 0.9 | 1.1326 | -0.018
73597-1100-1300DCT | ZONE 171 | RANGE | 1100-1300DCT | 73597 | KLEENCT1 | 18 | 1.116 | 1.1189 | 1.05 | 0.9 | #N/A | 0.066
73597-1310-1763DCT | ZONE 171 | RANGE | 1310-1763DCT | 73597 | KLEENCT1 | 18 | 1.1089 | 1.1189 | 1.05 | 0.9 | 1.1288 | -0.0199
73597-1443LINE | ZONE 171 | RANGE | 1443LINE | 73597 | KLEENCT1 | 18 | 1.1218 | 1.1189 | 1.05 | 0.9 | 1.1385 | -0.0167
73597-1460-387DCT | ZONE 171 | RANGE | 1460-387DCT | 73597 | KLEENCT1 | 18 | 1.1159 | 1.1189 | 1.05 | 0.9 | 1.1256 | -0.0097
73597-1670-1771DCT | ZONE 171 | RANGE | 1670-1771DCT | 73597 | KLEENCT1 | 18 | 1.1219 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0719
73597-1722LINE | ZONE 171 | RANGE | 1722LINE | 73597 | KLEENCT1 | 18 | 1.1218 | 1.1189 | 1.05 | 0.9 | 1.1383 | -0.0165
73597-1751-395DCT | ZONE 171 | RANGE | 1751-395DCT | 73597 | KLEENCT1 | 18 | 1.1162 | 1.1189 | 1.05 | 0.9 | 1.1275 | -0.0113
73597-1759-353NDCT | ZONE 171 | RANGE | 1759-353NDCT | 73597 | KLEENCT1 | 18 | 1.103 | 1.1189 | 1.05 | 0.9 | 1.1133 | -0.0103
73597-1767-353NDCT | ZONE 171 | RANGE | 1767-353NDCT | 73597 | KLEENCT1 | 18 | 1.103 | 1.1189 | 1.05 | 0.9 | 1.1133 | -0.0103
73597-1779-395DCT | ZONE 171 | RANGE | 1779-395DCT | 73597 | KLEENCT1 | 18 | 1.1153 | 1.1189 | 1.05 | 0.9 | 1.1267 | -0.0114
73597-1975-348DCT | ZONE 171 | RANGE | 1975-348DCT | 73597 | KLEENCT1 | 18 | 1.1317 | 1.1189 | 1.05 | 0.9 | 1.1579 | -0.0262
73597-310-348WDCT | ZONE 171 | RANGE | 310-348WDCT | 73597 | KLEENCT1 | 18 | 1.138 | 1.1189 | 1.05 | 0.9 | 1.1552 | -0.0172
73597-310-383DCT | ZONE 171 | RANGE | 310-383DCT | 73597 | KLEENCT1 | 18 | 1.1249 | 1.1189 | 1.05 | 0.9 | 1.1452 | -0.0203
73597-310LINE | ZONE 171 | RANGE | 310LINE | 73597 | KLEENCT1 | 18 | 1.1215 | 1.1189 | 1.05 | 0.9 | 1.14 | -0.0185
73597-312+393LNS | ZONE 171 | RANGE | 312+393LNS | 73597 | KLEENCT1 | 18 | 1.1247 | 1.1189 | 1.05 | 0.9 | 1.1543 | -0.0296
73597-312+393REAC | ZONE 171 | RANGE | 312+393REAC | 73597 | KLEENCT1 | 18 | 1.1247 | 1.1189 | 1.05 | 0.9 | 1.1544 | -0.0297
73597-312LINE | ZONE 171 | RANGE | 312LINE | 73597 | KLEENCT1 | 18 | 1.1247 | 1.1189 | 1.05 | 0.9 | 1.1543 | -0.0296
73597-318-362STKBR | ZONE 171 | RANGE | 318-362STKBR | 73597 | KLEENCT1 | 18 | 1.1235 | 1.1189 | 1.05 | 0.9 | 1.1559 | -0.0324
73597-330LINE | ZONE 171 | RANGE | 330LINE | 73597 | KLEENCT1 | 18 | 1.1288 | 1.1189 | 1.05 | 0.9 | 1.1464 | -0.0176
73597-348LINE | ZONE 171 | RANGE | 348LINE | 73597 | KLEENCT1 | 18 | 1.1307 | 1.1189 | 1.05 | 0.9 | 1.1581 | -0.0274
73597-353N+AUTO | ZONE 171 | RANGE | 353N+AUTO | 73597 | KLEENCT1 | 18 | 1.103 | 1.1189 | 1.05 | 0.9 | 1.1131 | -0.0101
73597-353NLINE | ZONE 171 | RANGE | 353NLINE | 73597 | KLEENCT1 | 18 | 1.103 | 1.1189 | 1.05 | 0.9 | 1.1126 | -0.0096
73597-353SLINE | ZONE 171 | RANGE | 353SLINE | 73597 | KLEENCT1 | 18 | 1.0991 | 1.1189 | 1.05 | 0.9 | 1.1039 | -0.0048
73597-362W-376DCT | ZONE 171 | RANGE | 362W-376DCT | 73597 | KLEENCT1 | 18 | 1.1289 | 1.1189 | 1.05 | 0.9 | 1.139 | -0.0101
73597-364+AUTO | ZONE 171 | RANGE | 364+AUTO | 73597 | KLEENCT1 | 18 | 1.1314 | 1.1189 | 1.05 | 0.9 | 1.1489 | -0.0175
73597-368LINE | ZONE 171 | RANGE | 368LINE | 73597 | KLEENCT1 | 18 | 1.1164 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0664
73597-371+AUTO | ZONE 171 | RANGE | 371+AUTO | 73597 | KLEENCT1 | 18 | 1.1276 | 1.1189 | 1.05 | 0.9 | 1.1404 | -0.0128
73597-371-383DCT | ZONE 171 | RANGE | 371-383DCT | 73597 | KLEENCT1 | 18 | 1.1293 | 1.1189 | 1.05 | 0.9 | 1.143 | -0.0137
73597-371LINE | ZONE 171 | RANGE | 371LINE | 73597 | KLEENCT1 | 18 | 1.1272 | 1.1189 | 1.05 | 0.9 | 1.14 | -0.0128
73597-383LINE | ZONE 171 | RANGE | 383LINE | 73597 | KLEENCT1 | 18 | 1.1229 | 1.1189 | 1.05 | 0.9 | 1.1409 | -0.018
73597-384LINE | ZONE 171 | RANGE | 384LINE | 73597 | KLEENCT1 | 18 | 1.1288 | 1.1189 | 1.05 | 0.9 | 1.1583 | -0.0295
73597-387+AUTOS | ZONE 171 | RANGE | 387+AUTOS | 73597 | KLEENCT1 | 18 | 1.1159 | 1.1189 | 1.05 | 0.9 | 1.1252 | -0.0093
73597-393LINE | ZONE 171 | RANGE | 393LINE | 73597 | KLEENCT1 | 18 | 1.1229 | 1.1189 | 1.05 | 0.9 | 1.151 | -0.0281
73597-395+AUTO | ZONE 171 | RANGE | 395+AUTO | 73597 | KLEENCT1 | 18 | 1.1144 | 1.1189 | 1.05 | 0.9 | 1.1269 | -0.0125
73597-395LINE | ZONE 171 | RANGE | 395LINE | 73597 | KLEENCT1 | 18 | 1.1153 | 1.1189 | 1.05 | 0.9 | 1.1267 | -0.0114
73597-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73597 | KLEENCT1 | 18 | 1.1189 | 1.1189 | 1.05 | 0.9 | 1.1357 | -0.0168
73597-CARD1TSTK | ZONE 171 | RANGE | CARD1TSTK | 73597 | KLEENCT1 | 18 | 1.131 | 1.1189 | 1.05 | 0.9 | 1.1515 | -0.0205
73597-CARD3TSTK | ZONE 171 | RANGE | CARD3TSTK | 73597 | KLEENCT1 | 18 | 1.1297 | 1.1189 | 1.05 | 0.9 | 1.1494 | -0.0197
73597-DC4-SIN-NOR | ZONE 171 | RANGE | DC4-SIN-NOR | 73597 | KLEENCT1 | 18 | 1.1146 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0646
73597-DC5-DEV-NOR | ZONE 171 | RANGE | DC5-DEV-NOR | 73597 | KLEENCT1 | 18 | 1.1227 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0727
73597-DEVON2TSTK | ZONE 171 | RANGE | DEVON2TSTK | 73597 | KLEENCT1 | 18 | 1.1238 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0738
73597-DEVON3TSTK | ZONE 171 | RANGE | DEVON3TSTK | 73597 | KLEENCT1 | 18 | 1.1238 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0738
73597-HADNKSTBKR | ZONE 171 | RANGE | HADNKSTBKR | 73597 | KLEENCT1 | 18 | 1.1289 | 1.1189 | 1.05 | 0.9 | 1.1391 | -0.0102
73597-LOSSMID4 | ZONE 171 | RANGE | LOSSMID4 | 73597 | KLEENCT1 | 18 | 1.1285 | 1.1189 | 1.05 | 0.9 | 1.1583 | -0.0298
73597-LUDLOWSTBKR | ZONE 171 | RANGE | LUDLOWSTBKR | 73597 | KLEENCT1 | 18 | 1.1146 | 1.1189 | 1.05 | 0.9 | 1.1284 | -0.0138
73597-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73597 | KLEENCT1 | 18 | 1.1299 | 1.1189 | 1.05 | 0.9 | 1.1476 | -0.0177
73597-NMSTBKREAC | ZONE 171 | RANGE | NMSTBKREAC | 73597 | KLEENCT1 | 18 | 1.1254 | 1.1189 | 1.05 | 0.9 | 1.1548 | -0.0294
73597-NOMNTSTBKR | ZONE 171 | RANGE | NOMNTSTBKR | 73597 | KLEENCT1 | 18 | 1.1254 | 1.1189 | 1.05 | 0.9 | 1.1548 | -0.0294
73597-SCOVRK4TSTK | ZONE 171 | RANGE | SCOVRK4TSTK | 73597 | KLEENCT1 | 18 | 1.1007 | 1.1189 | 1.05 | 0.9 | 1.106 | -0.0053
73597-SCOVRK7TSTK | ZONE 171 | RANGE | SCOVRK7TSTK | 73597 | KLEENCT1 | 18 | 1.1009 | 1.1189 | 1.05 | 0.9 | 1.1065 | -0.0056
73597-SCOVRK8TSTK | ZONE 171 | RANGE | SCOVRK8TSTK | 73597 | KLEENCT1 | 18 | 1.1142 | 1.1189 | 1.05 | 0.9 | 1.1205 | -0.0063
73597-SOTHNGTN15T | ZONE 171 | RANGE | SOTHNGTN15T | 73597 | KLEENCT1 | 18 | 1.1219 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0719
73598-1100-1200DCT | ZONE 171 | RANGE | 1100-1200DCT | 73598 | KLEENCT2 | 18 | 1.1146 | 1.1189 | 1.05 | 0.9 | 1.1326 | -0.018
73598-1100-1300DCT | ZONE 171 | RANGE | 1100-1300DCT | 73598 | KLEENCT2 | 18 | 1.116 | 1.1189 | 1.05 | 0.9 | #N/A | 0.066
73598-1310-1763DCT | ZONE 171 | RANGE | 1310-1763DCT | 73598 | KLEENCT2 | 18 | 1.1089 | 1.1189 | 1.05 | 0.9 | 1.1288 | -0.0199
73598-1443LINE | ZONE 171 | RANGE | 1443LINE | 73598 | KLEENCT2 | 18 | 1.1218 | 1.1189 | 1.05 | 0.9 | 1.1385 | -0.0167
73598-1460-387DCT | ZONE 171 | RANGE | 1460-387DCT | 73598 | KLEENCT2 | 18 | 1.1159 | 1.1189 | 1.05 | 0.9 | 1.1256 | -0.0097
73598-1670-1771DCT | ZONE 171 | RANGE | 1670-1771DCT | 73598 | KLEENCT2 | 18 | 1.1219 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0719
73598-1722LINE | ZONE 171 | RANGE | 1722LINE | 73598 | KLEENCT2 | 18 | 1.1218 | 1.1189 | 1.05 | 0.9 | 1.1383 | -0.0165
73598-1751-395DCT | ZONE 171 | RANGE | 1751-395DCT | 73598 | KLEENCT2 | 18 | 1.1162 | 1.1189 | 1.05 | 0.9 | 1.1275 | -0.0113
73598-1759-353NDCT | ZONE 171 | RANGE | 1759-353NDCT | 73598 | KLEENCT2 | 18 | 1.103 | 1.1189 | 1.05 | 0.9 | 1.1133 | -0.0103
73598-1767-353NDCT | ZONE 171 | RANGE | 1767-353NDCT | 73598 | KLEENCT2 | 18 | 1.103 | 1.1189 | 1.05 | 0.9 | 1.1133 | -0.0103
73598-1779-395DCT | ZONE 171 | RANGE | 1779-395DCT | 73598 | KLEENCT2 | 18 | 1.1153 | 1.1189 | 1.05 | 0.9 | 1.1267 | -0.0114
73598-1975-348DCT | ZONE 171 | RANGE | 1975-348DCT | 73598 | KLEENCT2 | 18 | 1.1317 | 1.1189 | 1.05 | 0.9 | 1.1579 | -0.0262
73598-310-348WDCT | ZONE 171 | RANGE | 310-348WDCT | 73598 | KLEENCT2 | 18 | 1.138 | 1.1189 | 1.05 | 0.9 | 1.1552 | -0.0172
73598-310-383DCT | ZONE 171 | RANGE | 310-383DCT | 73598 | KLEENCT2 | 18 | 1.1249 | 1.1189 | 1.05 | 0.9 | 1.1452 | -0.0203
73598-310LINE | ZONE 171 | RANGE | 310LINE | 73598 | KLEENCT2 | 18 | 1.1215 | 1.1189 | 1.05 | 0.9 | 1.14 | -0.0185
73598-312+393LNS | ZONE 171 | RANGE | 312+393LNS | 73598 | KLEENCT2 | 18 | 1.1247 | 1.1189 | 1.05 | 0.9 | 1.1543 | -0.0296
73598-312+393REAC | ZONE 171 | RANGE | 312+393REAC | 73598 | KLEENCT2 | 18 | 1.1247 | 1.1189 | 1.05 | 0.9 | 1.1544 | -0.0297
73598-312LINE | ZONE 171 | RANGE | 312LINE | 73598 | KLEENCT2 | 18 | 1.1247 | 1.1189 | 1.05 | 0.9 | 1.1543 | -0.0296
73598-318-362STKBR | ZONE 171 | RANGE | 318-362STKBR | 73598 | KLEENCT2 | 18 | 1.1235 | 1.1189 | 1.05 | 0.9 | 1.1559 | -0.0324
73598-330LINE | ZONE 171 | RANGE | 330LINE | 73598 | KLEENCT2 | 18 | 1.1288 | 1.1189 | 1.05 | 0.9 | 1.1464 | -0.0176
73598-348LINE | ZONE 171 | RANGE | 348LINE | 73598 | KLEENCT2 | 18 | 1.1307 | 1.1189 | 1.05 | 0.9 | 1.1581 | -0.0274
73598-353N+AUTO | ZONE 171 | RANGE | 353N+AUTO | 73598 | KLEENCT2 | 18 | 1.103 | 1.1189 | 1.05 | 0.9 | 1.1131 | -0.0101
73598-353NLINE | ZONE 171 | RANGE | 353NLINE | 73598 | KLEENCT2 | 18 | 1.103 | 1.1189 | 1.05 | 0.9 | 1.1126 | -0.0096
73598-353SLINE | ZONE 171 | RANGE | 353SLINE | 73598 | KLEENCT2 | 18 | 1.0991 | 1.1189 | 1.05 | 0.9 | 1.1039 | -0.0048
73598-362W-376DCT | ZONE 171 | RANGE | 362W-376DCT | 73598 | KLEENCT2 | 18 | 1.1289 | 1.1189 | 1.05 | 0.9 | 1.139 | -0.0101
73598-364+AUTO | ZONE 171 | RANGE | 364+AUTO | 73598 | KLEENCT2 | 18 | 1.1314 | 1.1189 | 1.05 | 0.9 | 1.1489 | -0.0175
73598-368LINE | ZONE 171 | RANGE | 368LINE | 73598 | KLEENCT2 | 18 | 1.1164 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0664
73598-371+AUTO | ZONE 171 | RANGE | 371+AUTO | 73598 | KLEENCT2 | 18 | 1.1276 | 1.1189 | 1.05 | 0.9 | 1.1404 | -0.0128
73598-371-383DCT | ZONE 171 | RANGE | 371-383DCT | 73598 | KLEENCT2 | 18 | 1.1293 | 1.1189 | 1.05 | 0.9 | 1.143 | -0.0137
73598-371LINE | ZONE 171 | RANGE | 371LINE | 73598 | KLEENCT2 | 18 | 1.1272 | 1.1189 | 1.05 | 0.9 | 1.14 | -0.0128
73598-383LINE | ZONE 171 | RANGE | 383LINE | 73598 | KLEENCT2 | 18 | 1.1229 | 1.1189 | 1.05 | 0.9 | 1.1409 | -0.018
73598-384LINE | ZONE 171 | RANGE | 384LINE | 73598 | KLEENCT2 | 18 | 1.1288 | 1.1189 | 1.05 | 0.9 | 1.1583 | -0.0295
73598-387+AUTOS | ZONE 171 | RANGE | 387+AUTOS | 73598 | KLEENCT2 | 18 | 1.1159 | 1.1189 | 1.05 | 0.9 | 1.1252 | -0.0093
73598-393LINE | ZONE 171 | RANGE | 393LINE | 73598 | KLEENCT2 | 18 | 1.1229 | 1.1189 | 1.05 | 0.9 | 1.151 | -0.0281
73598-395+AUTO | ZONE 171 | RANGE | 395+AUTO | 73598 | KLEENCT2 | 18 | 1.1144 | 1.1189 | 1.05 | 0.9 | 1.1269 | -0.0125
73598-395LINE | ZONE 171 | RANGE | 395LINE | 73598 | KLEENCT2 | 18 | 1.1153 | 1.1189 | 1.05 | 0.9 | 1.1267 | -0.0114
73598-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73598 | KLEENCT2 | 18 | 1.1189 | 1.1189 | 1.05 | 0.9 | 1.1357 | -0.0168
73598-CARD1TSTK | ZONE 171 | RANGE | CARD1TSTK | 73598 | KLEENCT2 | 18 | 1.131 | 1.1189 | 1.05 | 0.9 | 1.1515 | -0.0205
73598-CARD3TSTK | ZONE 171 | RANGE | CARD3TSTK | 73598 | KLEENCT2 | 18 | 1.1297 | 1.1189 | 1.05 | 0.9 | 1.1494 | -0.0197
73598-DC4-SIN-NOR | ZONE 171 | RANGE | DC4-SIN-NOR | 73598 | KLEENCT2 | 18 | 1.1146 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0646
73598-DC5-DEV-NOR | ZONE 171 | RANGE | DC5-DEV-NOR | 73598 | KLEENCT2 | 18 | 1.1227 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0727
73598-DEVON2TSTK | ZONE 171 | RANGE | DEVON2TSTK | 73598 | KLEENCT2 | 18 | 1.1238 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0738
73598-DEVON3TSTK | ZONE 171 | RANGE | DEVON3TSTK | 73598 | KLEENCT2 | 18 | 1.1238 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0738
73598-HADNKSTBKR | ZONE 171 | RANGE | HADNKSTBKR | 73598 | KLEENCT2 | 18 | 1.1289 | 1.1189 | 1.05 | 0.9 | 1.1391 | -0.0102
73598-LOSSMID4 | ZONE 171 | RANGE | LOSSMID4 | 73598 | KLEENCT2 | 18 | 1.1285 | 1.1189 | 1.05 | 0.9 | 1.1583 | -0.0298
73598-LUDLOWSTBKR | ZONE 171 | RANGE | LUDLOWSTBKR | 73598 | KLEENCT2 | 18 | 1.1146 | 1.1189 | 1.05 | 0.9 | 1.1284 | -0.0138
73598-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73598 | KLEENCT2 | 18 | 1.1299 | 1.1189 | 1.05 | 0.9 | 1.1476 | -0.0177
73598-NMSTBKREAC | ZONE 171 | RANGE | NMSTBKREAC | 73598 | KLEENCT2 | 18 | 1.1254 | 1.1189 | 1.05 | 0.9 | 1.1548 | -0.0294
73598-NOMNTSTBKR | ZONE 171 | RANGE | NOMNTSTBKR | 73598 | KLEENCT2 | 18 | 1.1254 | 1.1189 | 1.05 | 0.9 | 1.1548 | -0.0294
73598-SCOVRK4TSTK | ZONE 171 | RANGE | SCOVRK4TSTK | 73598 | KLEENCT2 | 18 | 1.1007 | 1.1189 | 1.05 | 0.9 | 1.106 | -0.0053
73598-SCOVRK7TSTK | ZONE 171 | RANGE | SCOVRK7TSTK | 73598 | KLEENCT2 | 18 | 1.1009 | 1.1189 | 1.05 | 0.9 | 1.1065 | -0.0056
73598-SCOVRK8TSTK | ZONE 171 | RANGE | SCOVRK8TSTK | 73598 | KLEENCT2 | 18 | 1.1142 | 1.1189 | 1.05 | 0.9 | 1.1205 | -0.0063
73598-SOTHNGTN15T | ZONE 171 | RANGE | SOTHNGTN15T | 73598 | KLEENCT2 | 18 | 1.1219 | 1.1189 | 1.05 | 0.9 | #N/A | 0.0719
73599-1310-1763DCT | ZONE 171 | RANGE | 1310-1763DCT | 73599 | KLEENST1 | 18 | 1.0983 | 1.1036 | 1.05 | 0.9 | 1.1089 | -0.0106
73599-1759-353NDCT | ZONE 171 | RANGE | 1759-353NDCT | 73599 | KLEENST1 | 18 | 1.0951 | 1.1036 | 1.05 | 0.9 | 1.1006 | -0.0055
73599-1767-353NDCT | ZONE 171 | RANGE | 1767-353NDCT | 73599 | KLEENST1 | 18 | 1.0951 | 1.1036 | 1.05 | 0.9 | 1.1006 | -0.0055
73599-1975-348DCT | ZONE 171 | RANGE | 1975-348DCT | 73599 | KLEENST1 | 18 | 1.1106 | 1.1036 | 1.05 | 0.9 | 1.1317 | -0.0211
73599-310-348WDCT | ZONE 171 | RANGE | 310-348WDCT | 73599 | KLEENST1 | 18 | 1.114 | 1.1036 | 1.05 | 0.9 | 1.1289 | -0.0149
73599-310-383DCT | ZONE 171 | RANGE | 310-383DCT | 73599 | KLEENST1 | 18 | 1.1068 | 1.1036 | 1.05 | 0.9 | 1.1179 | -0.0111
73599-312+393LNS | ZONE 171 | RANGE | 312+393LNS | 73599 | KLEENST1 | 18 | 1.1067 | 1.1036 | 1.05 | 0.9 | 1.1229 | -0.0162
73599-312+393REAC | ZONE 171 | RANGE | 312+393REAC | 73599 | KLEENST1 | 18 | 1.1067 | 1.1036 | 1.05 | 0.9 | 1.123 | -0.0163
73599-312LINE | ZONE 171 | RANGE | 312LINE | 73599 | KLEENST1 | 18 | 1.1067 | 1.1036 | 1.05 | 0.9 | 1.1229 | -0.0162
73599-330LINE | ZONE 171 | RANGE | 330LINE | 73599 | KLEENST1 | 18 | 1.109 | 1.1036 | 1.05 | 0.9 | 1.1186 | -0.0096
73599-348LINE | ZONE 171 | RANGE | 348LINE | 73599 | KLEENST1 | 18 | 1.11 | 1.1036 | 1.05 | 0.9 | 1.1319 | -0.0219
73599-353N+AUTO | ZONE 171 | RANGE | 353N+AUTO | 73599 | KLEENST1 | 18 | 1.0951 | 1.1036 | 1.05 | 0.9 | 1.1005 | -0.0054
73599-353NLINE | ZONE 171 | RANGE | 353NLINE | 73599 | KLEENST1 | 18 | 1.0951 | 1.1036 | 1.05 | 0.9 | 1.1002 | -0.0051
73599-353SLINE | ZONE 171 | RANGE | 353SLINE | 73599 | KLEENST1 | 18 | 1.0931 | 1.1036 | 1.05 | 0.9 | 1.0956 | -0.0025
73599-362W-376DCT | ZONE 171 | RANGE | 362W-376DCT | 73599 | KLEENST1 | 18 | 1.109 | 1.1036 | 1.05 | 0.9 | #N/A | 0.059
73599-364+AUTO | ZONE 171 | RANGE | 364+AUTO | 73599 | KLEENST1 | 18 | 1.1104 | 1.1036 | 1.05 | 0.9 | 1.12 | -0.0096
73599-371+AUTO | ZONE 171 | RANGE | 371+AUTO | 73599 | KLEENST1 | 18 | 1.1083 | 1.1036 | 1.05 | 0.9 | 1.1153 | -0.007
73599-371-383DCT | ZONE 171 | RANGE | 371-383DCT | 73599 | KLEENST1 | 18 | 1.1093 | 1.1036 | 1.05 | 0.9 | 1.1167 | -0.0074
73599-371LINE | ZONE 171 | RANGE | 371LINE | 73599 | KLEENST1 | 18 | 1.1081 | 1.1036 | 1.05 | 0.9 | #N/A | 0.0581
73599-384LINE | ZONE 171 | RANGE | 384LINE | 73599 | KLEENST1 | 18 | 1.109 | 1.1036 | 1.05 | 0.9 | 1.1261 | -0.0171
73599-BASE CASE | ZONE 171 | RANGE | BASE CASE | 73599 | KLEENST1 | 18 | 1.1036 | 1.1036 | 1.05 | 0.9 | 1.1127 | -0.0091
73599-CARD1TSTK | ZONE 171 | RANGE | CARD1TSTK | 73599 | KLEENST1 | 18 | 1.1102 | 1.1036 | 1.05 | 0.9 | 1.1214 | -0.0112
73599-CARD3TSTK | ZONE 171 | RANGE | CARD3TSTK | 73599 | KLEENST1 | 18 | 1.1094 | 1.1036 | 1.05 | 0.9 | 1.1202 | -0.0108
73599-DEVON2TSTK | ZONE 171 | RANGE | DEVON2TSTK | 73599 | KLEENST1 | 18 | 1.1063 | 1.1036 | 1.05 | 0.9 | #N/A | 0.0563
73599-DEVON3TSTK | ZONE 171 | RANGE | DEVON3TSTK | 73599 | KLEENST1 | 18 | 1.1063 | 1.1036 | 1.05 | 0.9 | #N/A | 0.0563
73599-HADNKSTBKR | ZONE 171 | RANGE | HADNKSTBKR | 73599 | KLEENST1 | 18 | 1.109 | 1.1036 | 1.05 | 0.9 | #N/A | 0.059
73599-LOSSMID4 | ZONE 171 | RANGE | LOSSMID4 | 73599 | KLEENST1 | 18 | 1.1088 | 1.1036 | 1.05 | 0.9 | 1.1256 | -0.0168
73599-MONTVSTBKR | ZONE 171 | RANGE | MONTVSTBKR | 73599 | KLEENST1 | 18 | 1.1096 | 1.1036 | 1.05 | 0.9 | 1.1192 | -0.0096
73599-NMSTBKREAC | ZONE 171 | RANGE | NMSTBKREAC | 73599 | KLEENST1 | 18 | 1.1071 | 1.1036 | 1.05 | 0.9 | 1.1232 | -0.0161
73599-NOMNTSTBKR | ZONE 171 | RANGE | NOMNTSTBKR | 73599 | KLEENST1 | 18 | 1.1071 | 1.1036 | 1.05 | 0.9 | 1.1232 | -0.0161
73599-SCOVRK4TSTK | ZONE 171 | RANGE | SCOVRK4TSTK | 73599 | KLEENST1 | 18 | 1.0939 | 1.1036 | 1.05 | 0.9 | 1.0967 | -0.0028
73599-SCOVRK7TSTK | ZONE 171 | RANGE | SCOVRK7TSTK | 73599 | KLEENST1 | 18 | 1.094 | 1.1036 | 1.05 | 0.9 | 1.097 | -0.003
73599-SCOVRK8TSTK | ZONE 171 | RANGE | SCOVRK8TSTK | 73599 | KLEENST1 | 18 | 1.1011 | 1.1036 | 1.05 | 0.9 | 1.1045 | -0.0034
73620-MONTVSTBKR | ZONE 178 | RANGE | MONTVSTBKR | 73620 | BUDDGTNB | 34.5 | 1.0802 | 1.0376 | 1.05 | 0.9 | 1.0808 | -0.0006
73657-1460-387DCT | ZONE 185 | RANGE | 1460-387DCT | 73657 | ENGLISH7 | 13.8 | 1.0531 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0031
73657-1508LINE | ZONE 185 | RANGE | 1508LINE | 73657 | ENGLISH7 | 13.8 | 1.0634 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0134
73657-348N+AUTO | ZONE 185 | RANGE | 348N+AUTO | 73657 | ENGLISH7 | 13.8 | 1.0568 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0068
73657-84004LINE | ZONE 185 | RANGE | 84004LINE | 73657 | ENGLISH7 | 13.8 | 1.0626 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0126
73657-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73657 | ENGLISH7 | 13.8 | 1.0554 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0054
73657-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73657 | ENGLISH7 | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73657-88005ALINE-1 | ZONE 185 | RANGE | 88005ALINE-1 | 73657 | ENGLISH7 | 13.8 | 1.0559 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0059
73657-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73657-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73657 | ENGLISH7 | 13.8 | 1.0553 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0053
73657-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73657 | ENGLISH7 | 13.8 | 1.0551 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0051
73657-89005BLINE-1 | ZONE 185 | RANGE | 89005BLINE-1 | 73657 | ENGLISH7 | 13.8 | 1.0559 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0059
73657-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73657 | ENGLISH7 | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73657-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73657 | ENGLISH7 | 13.8 | 1.0538 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0038
73657-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0523 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0023
73657-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0522 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0022
73657-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73657 | ENGLISH7 | 13.8 | 1.0536 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0036
73657-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73657 | ENGLISH7 | 13.8 | 1.0594 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0094
73657-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73657 | ENGLISH7 | 13.8 | 1.0634 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0134
73657-BRANFORD2T | ZONE 185 | RANGE | BRANFORD2T | 73657 | ENGLISH7 | 13.8 | 1.0628 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0128
73657-BRANFORD4T | ZONE 185 | RANGE | BRANFORD4T | 73657 | ENGLISH7 | 13.8 | 1.0626 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0126
73657-DC2-BES-SIN | ZONE 185 | RANGE | DC2-BES-SIN | 73657 | ENGLISH7 | 13.8 | 1.0551 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0051
73657-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73657 | ENGLISH7 | 13.8 | 1.0528 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0028
73657-DC5-DEV-NOR | ZONE 185 | RANGE | DC5-DEV-NOR | 73657 | ENGLISH7 | 13.8 | 1.055 | 1.0594 | 1.05 | 0.9 | #N/A | 0.005
73657-DEVON24TSTK | ZONE 185 | RANGE | DEVON24TSTK | 73657 | ENGLISH7 | 13.8 | 1.0567 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0067
73657-DEVON27TSTK | ZONE 185 | RANGE | DEVON27TSTK | 73657 | ENGLISH7 | 13.8 | 1.0565 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0065
73657-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73657-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0542 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0042
73657-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73657 | ENGLISH7 | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73657-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73657-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73657 | ENGLISH7 | 13.8 | 1.0531 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0031
73657-GREENHLL2T | ZONE 185 | RANGE | GREENHLL2T | 73657 | ENGLISH7 | 13.8 | 1.0634 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0134
73657-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0543 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0043
73657-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73657 | ENGLISH7 | 13.8 | 1.0543 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0043
73657-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73657 | ENGLISH7 | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73657-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73657 | ENGLISH7 | 13.8 | 1.0568 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0068
73657-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73657 | ENGLISH7 | 13.8 | 1.0635 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0135
73657-MLLRVR1TSTK | ZONE 185 | RANGE | MLLRVR1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0623 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0123
73657-MLLRVR2TSTK | ZONE 185 | RANGE | MLLRVR2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0624 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0124
73657-NOHAVN1TSTK | ZONE 185 | RANGE | NOHAVN1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0561 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0061
73657-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73657 | ENGLISH7 | 13.8 | 1.056 | 1.0594 | 1.05 | 0.9 | #N/A | 0.006
73657-QUINIPACST1 | ZONE 185 | RANGE | QUINIPACST1 | 73657 | ENGLISH7 | 13.8 | 1.0622 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0122
73657-SCOVRK4TSTK | ZONE 185 | RANGE | SCOVRK4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0555 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0055
73657-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73657 | ENGLISH7 | 13.8 | 1.0553 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0053
73657-SGTN1TSTK | ZONE 185 | RANGE | SGTN1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0566 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0066
73657-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73657 | ENGLISH7 | 13.8 | 1.0564 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0064
73657-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73657 | ENGLISH7 | 13.8 | 1.056 | 1.0594 | 1.05 | 0.9 | #N/A | 0.006
73657-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73657 | ENGLISH7 | 13.8 | 1.0564 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0064
73657-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73657 | ENGLISH7 | 13.8 | 1.0544 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0044
73657-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73657 | ENGLISH7 | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73658-1460-387DCT | ZONE 185 | RANGE | 1460-387DCT | 73658 | ENGLISH8 | 13.8 | 1.0531 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0031
73658-1508LINE | ZONE 185 | RANGE | 1508LINE | 73658 | ENGLISH8 | 13.8 | 1.0634 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0134
73658-348N+AUTO | ZONE 185 | RANGE | 348N+AUTO | 73658 | ENGLISH8 | 13.8 | 1.0568 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0068
73658-84004LINE | ZONE 185 | RANGE | 84004LINE | 73658 | ENGLISH8 | 13.8 | 1.0626 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0126
73658-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73658 | ENGLISH8 | 13.8 | 1.0554 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0054
73658-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73658 | ENGLISH8 | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73658-88005ALINE-1 | ZONE 185 | RANGE | 88005ALINE-1 | 73658 | ENGLISH8 | 13.8 | 1.0559 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0059
73658-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73658-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73658 | ENGLISH8 | 13.8 | 1.0553 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0053
73658-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73658 | ENGLISH8 | 13.8 | 1.0551 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0051
73658-89005BLINE-1 | ZONE 185 | RANGE | 89005BLINE-1 | 73658 | ENGLISH8 | 13.8 | 1.0559 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0059
73658-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73658 | ENGLISH8 | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73658-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73658 | ENGLISH8 | 13.8 | 1.0538 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0038
73658-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0523 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0023
73658-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0522 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0022
73658-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73658 | ENGLISH8 | 13.8 | 1.0536 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0036
73658-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73658 | ENGLISH8 | 13.8 | 1.0594 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0094
73658-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73658 | ENGLISH8 | 13.8 | 1.0634 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0134
73658-BRANFORD2T | ZONE 185 | RANGE | BRANFORD2T | 73658 | ENGLISH8 | 13.8 | 1.0628 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0128
73658-BRANFORD4T | ZONE 185 | RANGE | BRANFORD4T | 73658 | ENGLISH8 | 13.8 | 1.0626 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0126
73658-DC2-BES-SIN | ZONE 185 | RANGE | DC2-BES-SIN | 73658 | ENGLISH8 | 13.8 | 1.0551 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0051
73658-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73658 | ENGLISH8 | 13.8 | 1.0528 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0028
73658-DC5-DEV-NOR | ZONE 185 | RANGE | DC5-DEV-NOR | 73658 | ENGLISH8 | 13.8 | 1.055 | 1.0594 | 1.05 | 0.9 | #N/A | 0.005
73658-DEVON24TSTK | ZONE 185 | RANGE | DEVON24TSTK | 73658 | ENGLISH8 | 13.8 | 1.0567 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0067
73658-DEVON27TSTK | ZONE 185 | RANGE | DEVON27TSTK | 73658 | ENGLISH8 | 13.8 | 1.0565 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0065
73658-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73658-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0542 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0042
73658-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73658 | ENGLISH8 | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73658-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73658-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73658 | ENGLISH8 | 13.8 | 1.0531 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0031
73658-GREENHLL2T | ZONE 185 | RANGE | GREENHLL2T | 73658 | ENGLISH8 | 13.8 | 1.0634 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0134
73658-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0543 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0043
73658-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73658 | ENGLISH8 | 13.8 | 1.0543 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0043
73658-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73658 | ENGLISH8 | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73658-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73658 | ENGLISH8 | 13.8 | 1.0568 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0068
73658-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73658 | ENGLISH8 | 13.8 | 1.0635 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0135
73658-MLLRVR1TSTK | ZONE 185 | RANGE | MLLRVR1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0623 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0123
73658-MLLRVR2TSTK | ZONE 185 | RANGE | MLLRVR2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0624 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0124
73658-NOHAVN1TSTK | ZONE 185 | RANGE | NOHAVN1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0561 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0061
73658-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73658 | ENGLISH8 | 13.8 | 1.056 | 1.0594 | 1.05 | 0.9 | #N/A | 0.006
73658-QUINIPACST1 | ZONE 185 | RANGE | QUINIPACST1 | 73658 | ENGLISH8 | 13.8 | 1.0622 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0122
73658-SCOVRK4TSTK | ZONE 185 | RANGE | SCOVRK4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0555 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0055
73658-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73658 | ENGLISH8 | 13.8 | 1.0553 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0053
73658-SGTN1TSTK | ZONE 185 | RANGE | SGTN1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0566 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0066
73658-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73658 | ENGLISH8 | 13.8 | 1.0564 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0064
73658-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73658 | ENGLISH8 | 13.8 | 1.056 | 1.0594 | 1.05 | 0.9 | #N/A | 0.006
73658-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73658 | ENGLISH8 | 13.8 | 1.0564 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0064
73658-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73658 | ENGLISH8 | 13.8 | 1.0544 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0044
73658-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73658 | ENGLISH8 | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73665-1261-1620SDC | ZONE 185 | RANGE | 1261-1620SDC | 73665 | NHHHVDCL | 192 | 1.0502 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0002
73665-1342LINE | ZONE 185 | RANGE | 1342LINE | 73665 | NHHHVDCL | 192 | 1.0567 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0067
73665-329-352DCT | ZONE 185 | RANGE | 329-352DCT | 73665 | NHHHVDCL | 192 | 1.0567 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0067
73665-329LINE | ZONE 185 | RANGE | 329LINE | 73665 | NHHHVDCL | 192 | 1.0563 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0063
73665-348N+AUTO | ZONE 185 | RANGE | 348N+AUTO | 73665 | NHHHVDCL | 192 | 1.0553 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0053
73665-348NLINE | ZONE 185 | RANGE | 348NLINE | 73665 | NHHHVDCL | 192 | 1.0558 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0058
73665-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73665 | NHHHVDCL | 192 | 1.0562 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0062
73665-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73665 | NHHHVDCL | 192 | 1.056 | 1.0592 | 1.05 | 0.9 | #N/A | 0.006
73665-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73665 | NHHHVDCL | 192 | 1.0562 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0062
73665-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73665 | NHHHVDCL | 192 | 1.056 | 1.0592 | 1.05 | 0.9 | #N/A | 0.006
73665-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73665 | NHHHVDCL | 192 | 1.0554 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0054
73665-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73665 | NHHHVDCL | 192 | 1.055 | 1.0592 | 1.05 | 0.9 | #N/A | 0.005
73665-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73665 | NHHHVDCL | 192 | 1.0549 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0049
73665-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73665 | NHHHVDCL | 192 | 1.0553 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0053
73665-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73665 | NHHHVDCL | 192 | 1.0592 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0092
73665-BOKUM2T | ZONE 185 | RANGE | BOKUM2T | 73665 | NHHHVDCL | 192 | 1.0566 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0066
73665-BOKUM3T | ZONE 185 | RANGE | BOKUM3T | 73665 | NHHHVDCL | 192 | 1.0566 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0066
73665-BRANFORD2T | ZONE 185 | RANGE | BRANFORD2T | 73665 | NHHHVDCL | 192 | 1.0619 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0119
73665-DC2-BES-SIN | ZONE 185 | RANGE | DC2-BES-SIN | 73665 | NHHHVDCL | 192 | 1.054 | 1.0592 | 1.05 | 0.9 | #N/A | 0.004
73665-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73665 | NHHHVDCL | 192 | 1.0525 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0025
73665-DC5-DEV-NOR | ZONE 185 | RANGE | DC5-DEV-NOR | 73665 | NHHHVDCL | 192 | 1.055 | 1.0592 | 1.05 | 0.9 | #N/A | 0.005
73665-DEVON2TSTK | ZONE 185 | RANGE | DEVON2TSTK | 73665 | NHHHVDCL | 192 | 1.0504 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0004
73665-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73665 | NHHHVDCL | 192 | 1.0559 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0059
73665-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73665 | NHHHVDCL | 192 | 1.0557 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0057
73665-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73665 | NHHHVDCL | 192 | 1.0559 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0059
73665-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73665 | NHHHVDCL | 192 | 1.0562 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0062
73665-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73665 | NHHHVDCL | 192 | 1.0544 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0044
73665-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73665 | NHHHVDCL | 192 | 1.0562 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0062
73665-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73665 | NHHHVDCL | 192 | 1.0617 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0117
73665-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73665 | NHHHVDCL | 192 | 1.0557 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0057
73665-SCOVRK4TSTK | ZONE 185 | RANGE | SCOVRK4TSTK | 73665 | NHHHVDCL | 192 | 1.0558 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0058
73665-SCOVRK7TSTK | ZONE 185 | RANGE | SCOVRK7TSTK | 73665 | NHHHVDCL | 192 | 1.0625 | 1.0592 | 1.05 | 0.9 | 1.0521 | 0.0104
73665-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73665 | NHHHVDCL | 192 | 1.0533 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0033
73665-SGTN1TSTK | ZONE 185 | RANGE | SGTN1TSTK | 73665 | NHHHVDCL | 192 | 1.0551 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0051
73665-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73665 | NHHHVDCL | 192 | 1.0554 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0054
73665-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73665 | NHHHVDCL | 192 | 1.0553 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0053
73665-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73665 | NHHHVDCL | 192 | 1.0539 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0039
73665-SOTHNGTN12T | ZONE 185 | RANGE | SOTHNGTN12T | 73665 | NHHHVDCL | 192 | 1.0558 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0058
73665-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73665 | NHHHVDCL | 192 | 1.0563 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0063
73665-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73665 | NHHHVDCL | 192 | 1.0564 | 1.0592 | 1.05 | 0.9 | #N/A | 0.0064
73671-1630LINE | ZONE 185 | RANGE | 1630LINE | 73671 | NO.HAVEN | 115 | 1.0511 | 1.0419 | 1.05 | 0.9 | #N/A | 0.0011
73671-NOHAVN2TSTK | ZONE 185 | RANGE | NOHAVN2TSTK | 73671 | NO.HAVEN | 115 | 1.0589 | 1.0419 | 1.05 | 0.9 | #N/A | 0.0089
73671-WALLING1TSTK | ZONE 185 | RANGE | WALLING1TSTK | 73671 | NO.HAVEN | 115 | 1.0511 | 1.0419 | 1.05 | 0.9 | #N/A | 0.0011
73671-WALLING2TSTK | ZONE 185 | RANGE | WALLING2TSTK | 73671 | NO.HAVEN | 115 | 1.0512 | 1.0419 | 1.05 | 0.9 | #N/A | 0.0012
73672-84004LINE | ZONE 185 | RANGE | 84004LINE | 73672 | SACKETT | 115 | 1.0528 | 1.0443 | 1.05 | 0.9 | #N/A | 0.0028
73672-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73672 | SACKETT | 115 | 1.0538 | 1.0443 | 1.05 | 0.9 | #N/A | 0.0038
73700-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73700 | PEQUONIC | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73702-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73702 | CRRA XFO | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73716-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73716 | PEQBETAP | 115 | 1.05 | 1.05 | 1.05 | 0.9 | #N/A | 0
73729-1460-387DCT | ZONE 185 | RANGE | 1460-387DCT | 73729 | ENGLISH | 13.8 | 1.0531 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0031
73729-1508LINE | ZONE 185 | RANGE | 1508LINE | 73729 | ENGLISH | 13.8 | 1.0634 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0134
73729-348N+AUTO | ZONE 185 | RANGE | 348N+AUTO | 73729 | ENGLISH | 13.8 | 1.0568 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0068
73729-84004LINE | ZONE 185 | RANGE | 84004LINE | 73729 | ENGLISH | 13.8 | 1.0626 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0126
73729-88003ALINE | ZONE 185 | RANGE | 88003ALINE | 73729 | ENGLISH | 13.8 | 1.0554 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0054
73729-88005ALINE | ZONE 185 | RANGE | 88005ALINE | 73729 | ENGLISH | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73729-88005ALINE-1 | ZONE 185 | RANGE | 88005ALINE-1 | 73729 | ENGLISH | 13.8 | 1.0559 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0059
73729-88005ALINE-2 | ZONE 185 | RANGE | 88005ALINE-2 | 73729 | ENGLISH | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73729-89003BLINE | ZONE 185 | RANGE | 89003BLINE | 73729 | ENGLISH | 13.8 | 1.0553 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0053
73729-89005BLINE | ZONE 185 | RANGE | 89005BLINE | 73729 | ENGLISH | 13.8 | 1.0551 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0051
73729-89005BLINE-1 | ZONE 185 | RANGE | 89005BLINE-1 | 73729 | ENGLISH | 13.8 | 1.0559 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0059
73729-89005BLINE-2 | ZONE 185 | RANGE | 89005BLINE-2 | 73729 | ENGLISH | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73729-89006BLINE | ZONE 185 | RANGE | 89006BLINE | 73729 | ENGLISH | 13.8 | 1.0538 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0038
73729-ALLINGS1TSTK | ZONE 185 | RANGE | ALLINGS1TSTK | 73729 | ENGLISH | 13.8 | 1.0523 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0023
73729-ALLINGS2TSTK | ZONE 185 | RANGE | ALLINGS2TSTK | 73729 | ENGLISH | 13.8 | 1.0522 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0022
73729-BAIRDBSTK | ZONE 185 | RANGE | BAIRDBSTK | 73729 | ENGLISH | 13.8 | 1.0536 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0036
73729-BASE CASE | ZONE 185 | RANGE | BASE CASE | 73729 | ENGLISH | 13.8 | 1.0594 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0094
73729-BRANFORD1T | ZONE 185 | RANGE | BRANFORD1T | 73729 | ENGLISH | 13.8 | 1.0634 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0134
73729-BRANFORD2T | ZONE 185 | RANGE | BRANFORD2T | 73729 | ENGLISH | 13.8 | 1.0628 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0128
73729-BRANFORD4T | ZONE 185 | RANGE | BRANFORD4T | 73729 | ENGLISH | 13.8 | 1.0626 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0126
73729-DC2-BES-SIN | ZONE 185 | RANGE | DC2-BES-SIN | 73729 | ENGLISH | 13.8 | 1.0551 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0051
73729-DC3-BES-DEV | ZONE 185 | RANGE | DC3-BES-DEV | 73729 | ENGLISH | 13.8 | 1.0528 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0028
73729-DC5-DEV-NOR | ZONE 185 | RANGE | DC5-DEV-NOR | 73729 | ENGLISH | 13.8 | 1.055 | 1.0594 | 1.05 | 0.9 | #N/A | 0.005
73729-DEVON24TSTK | ZONE 185 | RANGE | DEVON24TSTK | 73729 | ENGLISH | 13.8 | 1.0567 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0067
73729-DEVON27TSTK | ZONE 185 | RANGE | DEVON27TSTK | 73729 | ENGLISH | 13.8 | 1.0565 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0065
73729-DEVSWST1TSTK | ZONE 185 | RANGE | DEVSWST1TSTK | 73729 | ENGLISH | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73729-DEVSWST2TSTK | ZONE 185 | RANGE | DEVSWST2TSTK | 73729 | ENGLISH | 13.8 | 1.0542 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0042
73729-DEVSWST3TSTK | ZONE 185 | RANGE | DEVSWST3TSTK | 73729 | ENGLISH | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73729-DEVSWST4TSTK | ZONE 185 | RANGE | DEVSWST4TSTK | 73729 | ENGLISH | 13.8 | 1.0548 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0048
73729-EDEVDEV1 | ZONE 185 | RANGE | EDEVDEV1 | 73729 | ENGLISH | 13.8 | 1.0531 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0031
73729-GREENHLL2T | ZONE 185 | RANGE | GREENHLL2T | 73729 | ENGLISH | 13.8 | 1.0634 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0134
73729-GRNDAV4TSTK | ZONE 185 | RANGE | GRNDAV4TSTK | 73729 | ENGLISH | 13.8 | 1.0543 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0043
73729-GRNDAV5TSTK | ZONE 185 | RANGE | GRNDAV5TSTK | 73729 | ENGLISH | 13.8 | 1.0543 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0043
73729-GRNDAV6TSTK | ZONE 185 | RANGE | GRNDAV6TSTK | 73729 | ENGLISH | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045
73729-LOSSBPT3 | ZONE 185 | RANGE | LOSSBPT3 | 73729 | ENGLISH | 13.8 | 1.0568 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0068
73729-MIXAVE1 | ZONE 185 | RANGE | MIXAVE1 | 73729 | ENGLISH | 13.8 | 1.0635 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0135
73729-MLLRVR1TSTK | ZONE 185 | RANGE | MLLRVR1TSTK | 73729 | ENGLISH | 13.8 | 1.0623 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0123
73729-MLLRVR2TSTK | ZONE 185 | RANGE | MLLRVR2TSTK | 73729 | ENGLISH | 13.8 | 1.0624 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0124
73729-NOHAVN1TSTK | ZONE 185 | RANGE | NOHAVN1TSTK | 73729 | ENGLISH | 13.8 | 1.0561 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0061
73729-PEQUON42TSTK | ZONE 185 | RANGE | PEQUON42TSTK | 73729 | ENGLISH | 13.8 | 1.056 | 1.0594 | 1.05 | 0.9 | #N/A | 0.006
73729-QUINIPACST1 | ZONE 185 | RANGE | QUINIPACST1 | 73729 | ENGLISH | 13.8 | 1.0622 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0122
73729-SCOVRK4TSTK | ZONE 185 | RANGE | SCOVRK4TSTK | 73729 | ENGLISH | 13.8 | 1.0555 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0055
73729-SCOVRK8TSTK | ZONE 185 | RANGE | SCOVRK8TSTK | 73729 | ENGLISH | 13.8 | 1.0553 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0053
73729-SGTN1TSTK | ZONE 185 | RANGE | SGTN1TSTK | 73729 | ENGLISH | 13.8 | 1.0566 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0066
73729-SGTN4TSTK | ZONE 185 | RANGE | SGTN4TSTK | 73729 | ENGLISH | 13.8 | 1.0564 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0064
73729-SGTN5TSTK | ZONE 185 | RANGE | SGTN5TSTK | 73729 | ENGLISH | 13.8 | 1.056 | 1.0594 | 1.05 | 0.9 | #N/A | 0.006
73729-SGTN7TSTK | ZONE 185 | RANGE | SGTN7TSTK | 73729 | ENGLISH | 13.8 | 1.0564 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0064
73729-WRIVER1TSTK | ZONE 185 | RANGE | WRIVER1TSTK | 73729 | ENGLISH | 13.8 | 1.0544 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0044
73729-WRIVER2TSTK | ZONE 185 | RANGE | WRIVER2TSTK | 73729 | ENGLISH | 13.8 | 1.0545 | 1.0594 | 1.05 | 0.9 | #N/A | 0.0045

## contingencies
CONTINGENCY LEGEND
LABEL EVENTS
100LINE : OPEN LINE FROM BUS 73344 [MONTVLLE69.000] TO BUS 73343 [GALESF A69.000] CKT 1
100+400LINES: OPEN LINE FROM BUS 73344 [MONTVLLE69.000] TO BUS 73343 [GALESF A69.000] CKT 1
OPEN LINE FROM BUS 73343 [GALESF A69.000] TO BUS 73345 [LEDYARDJ69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73615 [BUDDGTN 69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73617 [TUNNEL 69.000] CKT 1
400LINE : OPEN LINE FROM BUS 73343 [GALESF A69.000] TO BUS 73345 [LEDYARDJ69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73615 [BUDDGTN 69.000] CKT 1
OPEN LINE FROM BUS 73345 [LEDYARDJ69.000] TO BUS 73617 [TUNNEL 69.000] CKT 1
500LINE : OPEN LINE FROM BUS 73617 [TUNNEL 69.000] TO BUS 73616 [SCRRA PF69.000] CKT 1
667-690LINE : OPEN LINE FROM BUS 73336 [FALLS V 69.000] TO BUS 73337 [SALISBRY69.000] CKT 1
689LINE : OPEN LINE FROM BUS 73346 [TORRGTN 69.000] TO BUS 73336 [FALLS V 69.000] CKT 1
693LINE : OPEN LINE FROM BUS 73346 [TORRGTN 69.000] TO BUS 73336 [FALLS V 69.000] CKT 2
694LINE : OPEN LINE FROM BUS 73336 [FALLS V 69.000] TO BUS 73335 [N.CANAAN69.000] CKT 1
1000LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
OPEN LINE FROM BUS 73612 [BEAN HLL115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
1050LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1050+1766LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
OPEN LINE FROM BUS 73255 [WESTSIDE115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1060LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
1070LINE : OPEN LINE FROM BUS 73218 [STKHOUSE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1070+1490LNS: OPEN LINE FROM BUS 73291 [FORTHF 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73218 [STKHOUSE115.00] TO BUS 73215 [CARD 115.00] CKT 1
1080LINE : OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1090LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1100LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
1130LINE : OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1130+1416LNS: OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
1163LINE : OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
1163+1910LNS: OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
1165LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
1191LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
1200LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
1206LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73600 [CONN YAN115.00] CKT 1
1207LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
1208LINE : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1222LINE : OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 1
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 2
1235LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73151 [UNCASVLA115.00] CKT 1
1238LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
1238+1813LNS: OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
1250LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73152 [UNCASVLB115.00] CKT 1
1261LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73231 [BOKUM 115.00] CKT 1
1270LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
1272LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1272+1445LNS: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1280LINE : OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1300LINE : OPEN LINE FROM BUS 73220 [ENFIELD 115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
OPEN LINE FROM BUS 73222 [WNDSRLK 115.00] TO BUS 73539 [DEXTR PF13.800] CKT 1
1310LINE : OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73221 [S.WNDSRB115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73283 [SWINDT13115.00] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73221 [S.WNDSRB115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1337LINE : OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
1342LINE : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
1355LINE : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
ONE1385 : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
1385LN+AUTO : OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 2
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 3
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1389LINE : OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1394LINE : OPEN LINE FROM BUS 73266 [SCITICO 115.00] TO BUS 72978 [FRANCONA115.00] CKT 1
1410LINE : OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73613 [BUDDGTN2115.00] CKT 1
1416LINE : OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1430LINE : OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
1440LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
1443LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1443+1759LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1445LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
1450LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
1460LINE : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
1466LINE : OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
1470LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
1490LINE : OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
1500LINE : OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73150 [FLNDRSA 115.00] CKT 1
OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73149 [WILIAMSA115.00] CKT 1
OPEN LINE FROM BUS 73156 [COHNZ JA115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1505LINE : OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73223 [FRYBRT05115.00] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73236 [FRYBR05 115.00] CKT 1
OPEN LINE FROM BUS 73236 [FRYBR05 115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73476 [TRACY05 115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73270 [BROOKLYN115.00] TO BUS 73444 [BROOKLYN23.000] CKT 1
OPEN LINE FROM BUS 73475 [TRACY 23.000] TO BUS 73476 [TRACY05 115.00] CKT 1
1508LINE : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
1515LINE : OPEN LINE FROM BUS 72972 [LUDLOW 115.00] TO BUS 73266 [SCITICO 115.00] CKT 1
1537LINE : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
1545LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
1545+SPS : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73705 [IND.WELL115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
1550LINE : OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1550+1950LNS: OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1560LINE : OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
1565LINE : OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
1570LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
1572LINE : OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1572+1772LNS: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
OPEN LINE FROM BUS 73600 [CONN YAN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1575LINE : OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
1580LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1585LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1588LINE : OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
1594LINE : OPEN LINE FROM BUS 73705 [IND.WELL115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
1605LINE : OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73238 [FLANDRSB115.00] CKT 1
OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73239 [WILIAMSB115.00] CKT 1
OPEN LINE FROM BUS 73157 [COHNZ JB115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1607LINE : OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73226 [FRYBRT07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73229 [FRY BR07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73229 [FRY BR07115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73442 [TRACY 23.000] CKT 1
1610LINE : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1618LINE : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
1620NLINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73241 [MIDDLTWN115.00] CKT 1
1620SLINE : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
1622LINE : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
1625LINE : OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73161 [ROCKVILL115.00] CKT 1
1630LINE : OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
1637LINE : OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
1640LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1655LINE : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
1668LINE : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1670LINE : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
1675LINE : OPEN LINE FROM BUS 73612 [BEAN HLL115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1685LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1690LINE : OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73197 [HANOVERA115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1704LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73248 [SW.HTFD 115.00] CKT 1
1710LINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
1720LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
1721LINE : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1722LINE : OPEN LINE FROM BUS 73248 [SW.HTFD 115.00] TO BUS 73279 [CDECCA 115.00] CKT 1
OPEN LINE FROM BUS 73261 [NW.HTFD 115.00] TO BUS 73279 [CDECCA 115.00] CKT 1
1726LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73247 [FARMNGTN115.00] CKT 1
1730ALINE : OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1730BLINE : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1730CLINE : OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1732LINE : OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73262 [CANTON 115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
1740LINE : OPEN LINE FROM BUS 73162 [WATERSDE115.00] TO BUS 73163 [COS COB 115.00] CKT 1
1750LINE : OPEN LINE FROM BUS 73167 [SO.END 115.00] TO BUS 73144 [TOMAC 115.00] CKT 1
OPEN LINE FROM BUS 73144 [TOMAC 115.00] TO BUS 73163 [COS COB 115.00] CKT 1
1751LINE : OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1752LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73257 [ROCKY HL115.00] CKT 1
1753LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
1756LINE : OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
1759LINE : OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
1760LINE : OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
1760+1876LNS: OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
1763LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73284 [SWINDT17115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73131 [S.WNDSRA115.00] CKT 1
OPEN LINE FROM BUS 73131 [S.WNDSRA115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1765LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73255 [WESTSIDE115.00] CKT 1
1766LINE : OPEN LINE FROM BUS 73255 [WESTSIDE115.00] TO BUS 73269 [DOOLEY 115.00] CKT 1
1767LINE : OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73259 [HOPEWELL115.00] CKT 1
1769LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73256 [E.NBRITN115.00] CKT 1
1770LINE : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
1771LINE : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
1772LINE : OPEN LINE FROM BUS 73600 [CONN YAN115.00] TO BUS 73249 [P+W MIDD115.00] CKT 1
1773LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73257 [ROCKY HL115.00] CKT 1
1775LINE : OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73274 [RIVDRHIA115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 73274 [RIVDRHIA115.00] TO BUS 73537 [RVRSD PF23.000] CKT 1
1777LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1779LINE : OPEN LINE FROM BUS 73246 [S.MEADOW115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1780LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
1783LINE : OPEN LINE FROM BUS 73254 [NEWINGTN115.00] TO BUS 73247 [FARMNGTN115.00] CKT 1
OPEN LINE FROM BUS 73254 [NEWINGTN115.00] TO BUS 73256 [E.NBRITN115.00] CKT 1
1784LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73288 [NESMBY 115.00] CKT 1
OPEN LINE FROM BUS 73288 [NESMBY 115.00] TO BUS 73262 [CANTON 115.00] CKT 1
1785LINE : OPEN LINE FROM BUS 73243 [BERLIN 115.00] TO BUS 73254 [NEWINGTN115.00] CKT 1
1786LINE : OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73275 [RIVDRHIB115.00] CKT 1
OPEN LINE FROM BUS 73252 [1786 TAP115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
1788LINE : OPEN LINE FROM BUS 73245 [TORR TER115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
1790LINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
1792LINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
1800-1860LNS: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
1810LINE : OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1813LINE : OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
1820LINE : OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1821LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 72991 [SAGAR 115.00] CKT 1
1825LINE : OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1830LINE : OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1835LINE : OPEN LINE FROM BUS 73235 [CHIP HIL115.00] TO BUS 73240 [THOMASTN115.00] CKT 1
1836LINE : OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 72992 [SAGBR 115.00] CKT 1
1867LINE : OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
1870LINE : OPEN LINE FROM BUS 73177 [MYSTICCT115.00] TO BUS 73285 [CTRI1870115.00] CKT 1
OPEN LINE FROM BUS 73285 [CTRI1870115.00] TO BUS 72581 [WOOD RIV115.00] CKT 1
1876LINE : OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
1880LINE : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
1887LINE : OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
1890LINE : OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
1900LINE : OPEN LINE FROM BUS 73203 [CAMPV PH115.00] TO BUS 73245 [TORR TER115.00] CKT 1
1910LINE : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
1921LINE : OPEN LINE FROM BUS 73203 [CAMPV PH115.00] TO BUS 73240 [THOMASTN115.00] CKT 1
1950LINE : OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
1975LINE : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
1977LINENEW : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
1990LINE : OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
8100LINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
8200LINE : OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
8300LINE : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
8400LINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
8500LINE : OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
8600LINE : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
8700LINE : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
8804ALINE : OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
8809ALINE-1 : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
8809ALINE-2 : OPEN LINE FROM BUS 73694 [BAIRD A 115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
8904BLINE : OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
8909BLINE-1 : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
8909BLINE-2 : OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
9500LINE : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
9502LINE : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
84004LINE : OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
88003ALINE : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
88003ALINE-1: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
88003ALINE-2: OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
88003ALINE-3: OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
88005ALINE : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
88005ALINE-1: OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
88005ALINE-2: OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
88006ALINE : OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73694 [BAIRD A 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
89003BLINE : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
89003BLINE-1: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
89003BLINE-2: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
89003BLINE-3: OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
89005BLINE : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
89005BLINE-1: OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
89005BLINE-2: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
89006BLINE : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
89006BLINE-1: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73752 [BARNUM 13.800] CKT 1
OPEN LINE FROM BUS 73695 [BAIRD B 115.00] TO BUS 73754 [BAIRD 13.800] CKT 1
91001LINE : OPEN LINE FROM BUS 73701 [CRRA JCT115.00] TO BUS 73702 [CRRA XFO115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
EDEVDEV1 : OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
EDEVDEV2 : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73129 [E.DEVONJ115.00] CKT 1
301-302LNS : OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72929 [BELCH301345.00] CKT 1
OPEN LINE FROM BUS 72929 [BELCH301345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
OPEN LINE FROM BUS 71796 [CARP HL 345.00] TO BUS 71797 [MILLBURY345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
310LINE : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
312LINE : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72926 [NRTHFLD 345.00] CKT 1
312+393LNS : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72926 [NRTHFLD 345.00] CKT 1
312+393REAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
318LINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
321LINE : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
329LINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
330LINE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
330+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73566 [LAKERD#221.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73567 [LAKERD#321.000] CKT 1
347LINE : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
347LREAC : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
347+LAKE : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73118 [CTRI347 345.00] CKT 1
OPEN LINE FROM BUS 73118 [CTRI347 345.00] TO BUS 71336 [SHERMAN 345.00] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73566 [LAKERD#221.000] CKT 1
OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73567 [LAKERD#321.000] CKT 1
348LINE : OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
348NLINE : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
348N+AUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
352LINE : OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73105 [LONG MTN345.00] CKT 1
352+AUTO : OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73105 [LONG MTN345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73202 [FROST BR115.00] CKT 1
353NLINE : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73120 [KLEEN 345.00] CKT 1
353SLINE : OPEN LINE FROM BUS 73107 [SCOVL RK345.00] TO BUS 73120 [KLEEN 345.00] CKT 1
353N+AUTO : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73120 [KLEEN 345.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
354LINE : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
362ELINE : OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
362WLINE : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
364+AUTO : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
368LINE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
371LINE : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
371+AUTO : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
376LINE : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
381LINE : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
381LREAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
383LINE : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
384LINE : OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
387+AUTOS : OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73664 [NHHHVDCL345.00] TO BUS 73665 [NHHHVDCL191.50] CKT 1
393LINE : OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
395LINE : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
395+AUTO : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
398LINE : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
398LREAC : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
PLUMNOR : OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73133 [PLUMUG 345.00] CKT 2
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73134 [NORUG 345.00] CKT 3
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 2
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 3
OPEN LINE FROM BUS 73135 [NOROH 345.00] TO BUS 73293 [NORWALK 345.00] CKT 3
1000-1090DCT: OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73611 [DUDLEY T115.00] CKT 1
OPEN LINE FROM BUS 73611 [DUDLEY T115.00] TO BUS 73612 [BEAN HLL115.00] CKT 1
OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73291 [FORTHF 115.00] CKT 1
1060-1165DCT: OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
1060-1270DCT: OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
1070-1080DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
OPEN LINE FROM BUS 73291 [FORTHF 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
1080-1280DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
1080-1490DCT: OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73210 [MONTVLLE115.00] TO BUS 73214 [WAWECS J115.00] CKT 1
OPEN LINE FROM BUS 73215 [CARD 115.00] TO BUS 73218 [STKHOUSE115.00] CKT 1
OPEN LINE FROM BUS 73214 [WAWECS J115.00] TO BUS 73276 [LISBN PF115.00] CKT 1
OPEN LINE FROM BUS 73276 [LISBN PF115.00] TO BUS 73213 [TUNNEL 115.00] CKT 1
1100-1200DCT: OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
1100-1300DCT: OPEN LINE FROM BUS 73219 [BARBR HL115.00] TO BUS 73220 [ENFIELD 115.00] CKT 1
OPEN LINE FROM BUS 73220 [ENFIELD 115.00] TO BUS 73222 [WNDSRLK 115.00] CKT 1
OPEN LINE FROM BUS 73222 [WNDSRLK 115.00] TO BUS 73539 [DEXTR PF13.800] CKT 1
1130-1430DCT: OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
113091001DCT: OPEN LINE FROM BUS 73701 [CRRA JCT115.00] TO BUS 73702 [CRRA XFO115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1163-1550D-2: OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
1207-1775DCT: OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73250 [E.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73253 [1775 TAP115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
OPEN LINE FROM BUS 73253 [1775 TAP115.00] TO BUS 73274 [RIVDRHIA115.00] CKT 1
OPEN LINE FROM BUS 73274 [RIVDRHIA115.00] TO BUS 73537 [RVRSD PF23.000] CKT 1
1208-1640DCT: OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
1222-1730ADC: OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 1
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1261-1620SDC: OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
1272-1721DCT: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1280-1870DCT: OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73177 [MYSTICCT115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73177 [MYSTICCT115.00] TO BUS 73285 [CTRI1870115.00] CKT 1
OPEN LINE FROM BUS 73216 [WHIP JCT115.00] TO BUS 73217 [BUDDGTN 115.00] CKT 1
OPEN LINE FROM BUS 73285 [CTRI1870115.00] TO BUS 72581 [WOOD RIV115.00] CKT 1
1310-1763DCT: OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73284 [SWINDT17115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73284 [SWINDT17115.00] TO BUS 73131 [S.WNDSRA115.00] CKT 1
OPEN LINE FROM BUS 73131 [S.WNDSRA115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73221 [S.WNDSRB115.00] CKT 1
OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73283 [SWINDT13115.00] CKT 1
OPEN LINE FROM BUS 73283 [SWINDT13115.00] TO BUS 73219 [BARBR HL115.00] CKT 1
OPEN LINE FROM BUS 73221 [S.WNDSRB115.00] TO BUS 73458 [SO.WNDSR13.800] CKT 1
1355-1610DCT: OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1389-1880DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
1394-1515DCT: OPEN LINE FROM BUS 72978 [FRANCONA115.00] TO BUS 73266 [SCITICO 115.00] CKT 1
OPEN LINE FROM BUS 73266 [SCITICO 115.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
1416-1867DCT: OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1416-1880DCT: OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1416-1890DCT: OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73267 [DARIEN 115.00] TO BUS 73300 [ELYTAP 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
1440-1450DCT: OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
1470-1565DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73155 [RDGFLD J115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
1470-1637DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
1470-1720DCT: OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73143 [RDGEFLDA115.00] CKT 1
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1505-1607DCT: OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73223 [FRYBRT05115.00] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73236 [FRYBR05 115.00] CKT 1
OPEN LINE FROM BUS 73236 [FRYBR05 115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73223 [FRYBRT05115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73476 [TRACY05 115.00] TO BUS 73270 [BROOKLYN115.00] CKT 1
OPEN LINE FROM BUS 73270 [BROOKLYN115.00] TO BUS 73444 [BROOKLYN23.000] CKT 1
OPEN LINE FROM BUS 73475 [TRACY 23.000] TO BUS 73476 [TRACY05 115.00] CKT 1
OPEN LINE FROM BUS 73213 [TUNNEL 115.00] TO BUS 73226 [FRYBRT07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73229 [FRY BR07115.00] CKT 1
OPEN LINE FROM BUS 73226 [FRYBRT07115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73281 [EXETR PF115.00] CKT 1
OPEN LINE FROM BUS 73229 [FRY BR07115.00] TO BUS 73443 [FRY BRK 23.000] CKT 1
OPEN LINE FROM BUS 73212 [TRACY07 115.00] TO BUS 73442 [TRACY 23.000] CKT 1
1545-1570DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
1560-1570DCT: OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
1570-1575DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
1570-1580DCT: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
1575-1585DCT: OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
1575-1990DCT: OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73186 [BALDWINA115.00] TO BUS 73386 [BALDWINA13.800] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
1580-1585DCT: OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 2
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
1580-1730BDC: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1620N-1975DC: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73230 [HADDAM 115.00] CKT 1
1622-1887DCT: OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
1637-1720DCT: OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
1640-1690DCT: OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73197 [HANOVERA115.00] CKT 1
OPEN LINE FROM BUS 73193 [LUCHJA90115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1668-1721DCT: OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
1670-1771DCT: OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
1670-1830DCT: OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
1710-1730ADC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1710-1730BDC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
1710-1730CDC: OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
1720-1730ADC: OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73158 [WESTON 115.00] CKT 1
1732-1788DCT: OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73262 [CANTON 115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
OPEN LINE FROM BUS 73263 [WEINGART115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
OPEN LINE FROM BUS 73245 [TORR TER115.00] TO BUS 73260 [FRKLN DR115.00] CKT 1
1751-1777DCT: OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
1770-1887DCT: OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
1777-1779DCT: OPEN LINE FROM BUS 73244 [N.BLMFLD115.00] TO BUS 73258 [BLOOMFLD115.00] CKT 1
OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
1800-1810DCT: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
1800-1825DCT: OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1810-1825DCT: OPEN LINE FROM BUS 73154 [SGTN B 115.00] TO BUS 73234 [CHIPP TP115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73232 [FORESTVL115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
1867-1880DCT: OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
1867-1890DCT: OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
1867-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1880-1890DCT: OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1880-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
1890-1977DCT: OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
8100-8200DCT: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
1466-362EDCT: OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
1460-387DCT : OPEN LINE FROM BUS 73107 [SCOVL RK345.00] TO BUS 73663 [E.SHORE 345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
1565-PLNRDCT: OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73372 [RDGEFLD 13.800] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73132 [PLUMREAC345.00] TO BUS 73133 [PLUMUG 345.00] CKT 2
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73134 [NORUG 345.00] CKT 3
OPEN LINE FROM BUS 73133 [PLUMUG 345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 2
OPEN LINE FROM BUS 73134 [NORUG 345.00] TO BUS 73135 [NOROH 345.00] CKT 3
OPEN LINE FROM BUS 73135 [NOROH 345.00] TO BUS 73293 [NORWALK 345.00] CKT 3
1610-BSKDVDC: OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
1618-321DCT : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
1751-395DCT : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73261 [NW.HTFD 115.00] CKT 1
OPEN LINE FROM BUS 73251 [BLM JCT 115.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
1759-353NDCT: OPEN LINE FROM BUS 73241 [MIDDLTWN115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73259 [HOPEWELL115.00] TO BUS 73264 [PORTLAND115.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73120 [KLEEN 345.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1767-353NDCT: OPEN LINE FROM BUS 73242 [MANCHSTR115.00] TO BUS 73259 [HOPEWELL115.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73120 [KLEEN 345.00] CKT 1
OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
1770-321DCT : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
1779-395DCT : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 73258 [BLOOMFLD115.00] TO BUS 73246 [S.MEADOW115.00] CKT 1
1887-321DCT : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
1975-348DCT : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
1975-362WDCT: OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
310-348WDCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73230 [HADDAM 115.00] CKT 1
OPEN LINE FROM BUS 73121 [HADAUTO 345.00] TO BUS 73295 [BESECK 345.00] CKT 1
310-368DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
310-383DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
329-352DCT : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73106 [SOUTHGTN345.00] CKT 1
OPEN LINE FROM BUS 73104 [FRSTBDGE345.00] TO BUS 73202 [FROST BR115.00] CKT 1
362W-376DCT : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
371-383DCT : OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73108 [CARD 345.00] CKT 1
OPEN LINE FROM BUS 73110 [MILLSTNE345.00] TO BUS 73109 [MONTVILE345.00] CKT 1
MANCHAUTO1 : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73242 [MANCHSTR115.00] CKT 1
NORAUT : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73293 [NORWALK 345.00] CKT 1
PLUMAUT : OPEN LINE FROM BUS 73115 [PLUMTREE345.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
SOUTH1XAUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOUTH2XAUTO : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
LOSSBPT3 : OPEN LINE FROM BUS 73648 [BPTHBR#322.000] TO BUS 73700 [PEQUONIC115.00] CKT 1
LOSSDEV7 : OPEN LINE FROM BUS 73553 [DEVON#7 13.800] TO BUS 73195 [DEVON 115.00] CKT 1
LOLAKERD : OPEN LINE FROM BUS 73119 [LAKEROAD345.00] TO BUS 73565 [LAKERD#121.000] CKT 1
LOSSMID4 : OPEN LINE FROM BUS 73557 [MIDDTN#422.000] TO BUS 73116 [MIDDLTWN345.00] CKT 1
LOSSMP2 : OPEN LINE FROM BUS 73562 [MILL#2 24.000] TO BUS 73110 [MILLSTNE345.00] CKT 1
LOSSMP3 : OPEN LINE FROM BUS 73563 [MILL#3 24.000] TO BUS 73110 [MILLSTNE345.00] CKT 1
LOSSMON6 : OPEN LINE FROM BUS 73559 [MONTV#6 22.000] TO BUS 73210 [MONTVLLE115.00] CKT 1
LOSSNHAV : OPEN LINE FROM BUS 73651 [NH HARBR22.000] TO BUS 73668 [E.SHORE 115.00] CKT 1
LOSSNOR1 : OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
LOSSNOR2 : OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
ALLINGS1TSTK: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
ALLINGS2TSTK: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73742 [ELMWEST 13.800] CKT 1
OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73685 [ALLINGSB115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
ASHCREEKBKR : OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73763 [ASHCREEK13.800] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73763 [ASHCREEK13.800] CKT 2
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73714 [ASHCREAC115.00] CKT 1
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73714 [ASHCREAC115.00] CKT 2
OPEN LINE FROM BUS 73703 [ASHCREEK115.00] TO BUS 73701 [CRRA JCT115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
BAIRDASTK : OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73696 [CONGRESS115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73755 [CONGRES213.800] CKT 1
BAIRDBSTK : OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73697 [CONGRESS115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73755 [CONGRES213.800] CKT 1
BATESROCK1T : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
BECONFLSTK : OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73228 [BALDWNJB115.00] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73387 [BEACON F13.800] CKT 1
OPEN LINE FROM BUS 73188 [BCNFL PF115.00] TO BUS 73387 [BEACON F13.800] CKT 2
BOKUM2T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73230 [HADDAM 115.00] CKT 2
OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
BOKUM3T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73231 [BOKUM 115.00] CKT 1
BRANFORD1T : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
BRANFORD2T : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
BRANFORD4T : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
BRANFRDRR1T : OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73287 [BRANF RR115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
BROADWYST1 : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
BUNKERH1T : OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73160 [BALDWINB115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
OPEN LINE FROM BUS 73228 [BALDWNJB115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73160 [BALDWINB115.00] TO BUS 73382 [BALDWINB13.800] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
BUNKERH2T : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
BUNKERH3T : OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73185 [BUNKER H115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73183 [SHAWSHIL115.00] CKT 1
COLONY1T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
DARIEN1T : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73300 [ELYTAP 115.00] TO BUS 73286 [COMPO 115.00] CKT 1
OPEN LINE FROM BUS 73286 [COMPO 115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
DEVON1TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
DEVON2TSTK : OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73125 [MILFORD 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
DEVON3TSTK : OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73125 [MILFORD 115.00] CKT 1
OPEN LINE FROM BUS 73129 [E.DEVONJ115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73570 [DEVGAS1113.800] CKT 1
DEVON6TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
DEVON7TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73192 [DRBY J B115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73188 [BCNFL PF115.00] CKT 1
OPEN LINE FROM BUS 73192 [DRBY J B115.00] TO BUS 73705 [IND.WELL115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73573 [DEVGAS1413.800] CKT 1
DEVON8TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73573 [DEVGAS1413.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
DEVON10TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73571 [DEVGAS1213.800] CKT 1
DEVON11TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73571 [DEVGAS1213.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73199 [SO.NAUG 115.00] CKT 1
DEVON12TSTK : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73570 [DEVGAS1113.800] CKT 1
OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73572 [DEVGAS1313.800] CKT 1
DEVON23TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73553 [DEVON#7 13.800] CKT 1
DEVON24TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
DEVON25TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73554 [DEVON#8 13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
DEVON26TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73554 [DEVON#8 13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
DEVON27TSTK : OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
DEVSWST1TSTK: OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73692 [BARNUM A115.00] CKT 1
OPEN LINE FROM BUS 73692 [BARNUM A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
DEVSWST2TSTK: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
DEVSWST3TSTK: OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73693 [BARNUM B115.00] CKT 1
OPEN LINE FROM BUS 73693 [BARNUM B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73691 [DEVON179115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1
DEVSWST4TSTK: OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
EMERIDEN1T : OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
ESHORE12TSTK: OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73651 [NH HARBR22.000] CKT 1
FLAXHILL2T : OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73207 [FLAX HIL115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
FROSTBR15T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73203 [CAMPV PH115.00] CKT 1
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
FROSTBR21T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73180 [CARMHILL115.00] CKT 1
OPEN LINE FROM BUS 73180 [CARMHILL115.00] TO BUS 73190 [ROCK RIV115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
FROSTBR27T : OPEN LINE FROM BUS 73202 [FROST BR115.00] TO BUS 73189 [FREIGHT 115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73186 [BALDWINA115.00] TO BUS 73386 [BALDWINA13.800] CKT 1
GLENBROOK3T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73169 [RYTN J A115.00] CKT 1
GLENBROOK8T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GRNDAV1TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
GRNDAV2TSTK : OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
GRNDAV3TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
GRNDAV4TSTK : OPEN LINE FROM BUS 73668 [E.SHORE 115.00] TO BUS 73669 [GRAND AV115.00] CKT 2
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
GRNDAV5TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
GRNDAV6TSTK : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
GRNDAV7TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73679 [ENG STA 115.00] CKT 1
OPEN LINE FROM BUS 73679 [ENG STA 115.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
GREENHLL2T : OPEN LINE FROM BUS 73231 [BOKUM 115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73265 [GREEN HL115.00] CKT 1
HADDAM1T : OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73227 [E.MERIDN115.00] CKT 1
OPEN LINE FROM BUS 73230 [HADDAM 115.00] TO BUS 73600 [CONN YAN115.00] CKT 1
HAWTHORNST : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 2
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
JUNEST1 : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
MLLRVR1TSTK : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73737 [MILLRIV213.800] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73737 [MILLRIV213.800] TO BUS 73676 [MILL RVR115.00] CKT 2
MLLRVR2TSTK : OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73736 [MILLRIV113.800] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73736 [MILLRIV113.800] TO BUS 73676 [MILL RVR115.00] CKT 2
MIXAVE1 : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
NOHAVN1TSTK : OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 2
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73153 [BRANFORD115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73670 [QUINNIP 115.00] CKT 1
NOHAVN2TSTK : OPEN LINE FROM BUS 73153 [BRANFORD115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73671 [NO.HAVEN115.00] TO BUS 73731 [NO.HAVEN13.800] CKT 1
NWALLING1T : OPEN LINE FROM BUS 73633 [NO.WALLF115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73227 [E.MERIDN115.00] TO BUS 73633 [NO.WALLF115.00] CKT 1
NORWALKST1 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73143 [RDGEFLDA115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
NORWALKST2 : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73292 [NRWLK RX115.00] CKT 2
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
NORWLKHAR1T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR2T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR3T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 75051 [NRTHPRT1138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 75053 [NRTHPT P138.00] TO BUS 73166 [NORHR138138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR4T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR7T : OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
OLDTOWNST : OPEN LINE FROM BUS 73710 [HAWTHORN115.00] TO BUS 73711 [HAWTH R 115.00] CKT 2
OPEN LINE FROM BUS 73711 [HAWTH R 115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73709 [OLD TOWN115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
PEACEABLE1T : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73155 [RDGFLD J115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
OPEN LINE FROM BUS 73174 [PEACEABL115.00] TO BUS 73143 [RDGEFLDA115.00] CKT 1
PEQUON22TSTK: OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73225 [TRMB J B115.00] CKT 1
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73700 [PEQUONIC115.00] CKT 2
OPEN LINE FROM BUS 73225 [TRMB J B115.00] TO BUS 73709 [OLD TOWN115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73696 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73696 [CONGRESS115.00] TO BUS 73712 [CNGRES2A115.00] CKT 1
OPEN LINE FROM BUS 73712 [CNGRES2A115.00] TO BUS 73694 [BAIRD A 115.00] CKT 1
PEQUON32TSTK: OPEN LINE FROM BUS 73224 [TRMB J A115.00] TO BUS 73700 [PEQUONIC115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73647 [BPTHBR#220.000] CKT 1
PEQUON42TSTK: OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73697 [CONGRESS115.00] CKT 1
OPEN LINE FROM BUS 73697 [CONGRESS115.00] TO BUS 73713 [CNGRES2B115.00] CKT 1
OPEN LINE FROM BUS 73713 [CNGRES2B115.00] TO BUS 73695 [BAIRD B 115.00] CKT 1
OPEN LINE FROM BUS 73700 [PEQUONIC115.00] TO BUS 73648 [BPTHBR#322.000] CKT 1
PLUMTREE25T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
PLUMTREE28T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
PLUMTREE31T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73155 [RDGFLD J115.00] TO BUS 73146 [RDGEFLDB115.00] CKT 1
QUINIPACST1 : OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73676 [MILL RVR115.00] CKT 1
OPEN LINE FROM BUS 73670 [QUINNIP 115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
ROCKRIVER1T : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73147 [BULLS BR115.00] CKT 1
SACKETST1 : OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73672 [SACKETT 115.00] CKT 1
OPEN LINE FROM BUS 73672 [SACKETT 115.00] TO BUS 73673 [SACKPHS 115.00] CKT 1
OPEN LINE FROM BUS 73673 [SACKPHS 115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
SASCOCR1T : OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 1
OPEN LINE FROM BUS 73714 [ASHCREAC115.00] TO BUS 73703 [ASHCREEK115.00] CKT 2
OPEN LINE FROM BUS 73171 [NWLK HAR115.00] TO BUS 73237 [ELYAVE 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
SHEPAUG13A : OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73178 [SHEPAUG 115.00] TO BUS 73341 [SHEPAUG 69.000] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
SOUTHEND5T : OPEN LINE FROM BUS 73167 [SO.END 115.00] TO BUS 73144 [TOMAC 115.00] CKT 1
OPEN LINE FROM BUS 73144 [TOMAC 115.00] TO BUS 73163 [COS COB 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
SOUTHEND6T : OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
SNAUGA1T : OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73388 [SO.NAUG 13.800] CKT 2
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73126 [DEVON#2 115.00] CKT 1
OPEN LINE FROM BUS 73199 [SO.NAUG 115.00] TO BUS 73185 [BUNKER H115.00] CKT 1
SOTHNGTN12T : OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73631 [WLNGF PF115.00] CKT 1
SOTHNGTN13T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73707 [JUNE ST 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73675 [MIX AVE 115.00] CKT 1
OPEN LINE FROM BUS 73196 [GLEN JCT115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOTHNGTN14T : OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
SOTHNGTN15T : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73198 [SOUTHGTN115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
SOTHNGTN16T : OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73243 [BERLIN 115.00] CKT 1
OPEN LINE FROM BUS 73206 [RES RD J115.00] TO BUS 73273 [BLRKHIB 115.00] CKT 1
OPEN LINE FROM BUS 73272 [BLRKHIA 115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
SOTHNGTN20T : OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73634 [COLONY 115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73182 [HANOVERB115.00] CKT 1
OPEN LINE FROM BUS 73184 [LUCHJB55115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
SOTHNGTN22T : OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SOTHNGTN23T : OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73175 [BLACK RK115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN24T : OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73148 [U.A.C. 115.00] CKT 1
OPEN LINE FROM BUS 73208 [U.A.C.TP115.00] TO BUS 73232 [FORESTVL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN25T : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73233 [BRISTOL 115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73235 [CHIP HIL115.00] CKT 1
OPEN LINE FROM BUS 73234 [CHIPP TP115.00] TO BUS 73154 [SGTN B 115.00] CKT 1
SOTHNGTN26T : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
SOTHNGTN28T : OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73127 [SGTNB RX115.00] TO BUS 73204 [TODD 115.00] CKT 1
OPEN LINE FROM BUS 73204 [TODD 115.00] TO BUS 73205 [NOERA JB115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73201 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73205 [NOERA JB115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73154 [SGTN B 115.00] CKT 2
OPEN LINE FROM BUS 73128 [SGTNB2 R115.00] TO BUS 73211 [CANAL 115.00] CKT 1
OPEN LINE FROM BUS 73211 [CANAL 115.00] TO BUS 73200 [NOERA JA115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73181 [NOERA 115.00] CKT 1
OPEN LINE FROM BUS 73200 [NOERA JA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
STEVENSNSTK : OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73282 [SNDYHK 115.00] CKT 1
OPEN LINE FROM BUS 73282 [SNDYHK 115.00] TO BUS 73194 [NEWTOWN 115.00] CKT 1
OPEN LINE FROM BUS 73194 [NEWTOWN 115.00] TO BUS 73170 [PLUMTREE115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73186 [BALDWINA115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73202 [FROST BR115.00] CKT 1
OPEN LINE FROM BUS 73164 [BALDWNJA115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73706 [ANSONIA 115.00] CKT 1
OPEN LINE FROM BUS 73191 [DRBY J A115.00] TO BUS 73187 [STEVENSN115.00] CKT 1
STONYHILL1T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73159 [BATES RK115.00] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
TRPFALLST1 : OPEN LINE FROM BUS 73126 [DEVON#2 115.00] TO BUS 73704 [TRAP FLS115.00] CKT 1
OPEN LINE FROM BUS 73704 [TRAP FLS115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73187 [STEVENSN115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
OPEN LINE FROM BUS 73706 [ANSONIA 115.00] TO BUS 73191 [DRBY J A115.00] CKT 1
TRIANGLE4T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
OPEN LINE FROM BUS 73377 [TRIANGLA13.800] TO BUS 73383 [TRIANGLB13.800] CKT 1
WALLING1TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73594 [WALL LV113.800] CKT 1
WALLING2TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73632 [WALLFRDJ115.00] CKT 1
OPEN LINE FROM BUS 73632 [WALLFRDJ115.00] TO BUS 73671 [NO.HAVEN115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73195 [DEVON 115.00] CKT 1
WALLING3TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73195 [DEVON 115.00] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73595 [WALL LV213.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73596 [WALL LV313.800] CKT 1
WALLING4TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73595 [WALL LV213.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73596 [WALL LV313.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
WALLING5TSTK: OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73594 [WALL LV113.800] CKT 1
OPEN LINE FROM BUS 73631 [WLNGF PF115.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
WATERST1TSTK: OPEN LINE FROM BUS 73680 [WATER ST115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
WATERST2TSTK: OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73678 [BROADWAY115.00] TO BUS 73680 [WATER ST115.00] CKT 1
WATERSIDE2T : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73162 [WATERSDE115.00] TO BUS 73163 [COS COB 115.00] CKT 1
WBROOKFLD1T : OPEN LINE FROM BUS 73190 [ROCK RIV115.00] TO BUS 73179 [W.BRKFLD115.00] CKT 1
OPEN LINE FROM BUS 73179 [W.BRKFLD115.00] TO BUS 73165 [STONY HL115.00] CKT 1
OPEN LINE FROM BUS 73165 [STONY HL115.00] TO BUS 73178 [SHEPAUG 115.00] CKT 1
WRIVER1TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73669 [GRAND AV115.00] CKT 1
OPEN LINE FROM BUS 73682 [ELMWST A115.00] TO BUS 73681 [WEST RIV115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73682 [ELMWST A115.00] CKT 1
WRIVER2TSTK : OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73680 [WATER ST115.00] CKT 1
OPEN LINE FROM BUS 73669 [GRAND AV115.00] TO BUS 73681 [WEST RIV115.00] CKT 2
OPEN LINE FROM BUS 73681 [WEST RIV115.00] TO BUS 73683 [ELMWST B115.00] CKT 1
OPEN LINE FROM BUS 73683 [ELMWST B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
WESTON1T : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73292 [NRWLK RX115.00] CKT 2
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73158 [WESTON 115.00] TO BUS 73224 [TRMB J A115.00] CKT 1
318-362STKBR: OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73588 [MERIDEN121.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73589 [MERIDEN221.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73590 [MERIDEN321.000] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73122 [MERID362345.00] TO BUS 73106 [SOUTHGTN345.00] CKT 1
CARD1TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
CARD1T+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73565 [LAKERD#121.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73566 [LAKERD#221.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73567 [LAKERD#321.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
CARD2TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
CARD3TSTK : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
CARD3T+LAKE : OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73108 [CARD 345.00] TO BUS 73215 [CARD 115.00] CKT 1
OPEN LINE FROM BUS 73565 [LAKERD#121.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73566 [LAKERD#221.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
OPEN LINE FROM BUS 73567 [LAKERD#321.000] TO BUS 73119 [LAKEROAD345.00] CKT 1
HADNKSTBKR : OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73295 [BESECK 345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73109 [MONTVILE345.00] CKT 1
LONGMT5TSTK : OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73117 [CTNY398 345.00] CKT 1
OPEN LINE FROM BUS 73117 [CTNY398 345.00] TO BUS 74344 [PLTVLLEY345.00] CKT 1
OPEN LINE FROM BUS 73105 [LONG MTN345.00] TO BUS 73115 [PLUMTREE345.00] CKT 1
LUDLOWSTBKR : OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72929 [BELCH301345.00] CKT 1
OPEN LINE FROM BUS 72925 [LUDLOW 345.00] TO BUS 72972 [LUDLOW 115.00] CKT 1
OPEN LINE FROM BUS 72929 [BELCH301345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
OPEN LINE FROM BUS 71797 [MILLBURY345.00] TO BUS 71796 [CARP HL 345.00] CKT 1
MANCH21TSTK : OPEN LINE FROM BUS 73112 [MANCHSTR345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73244 [N.BLMFLD115.00] CKT 1
OPEN LINE FROM BUS 73111 [NOBLMFLD345.00] TO BUS 73103 [MEEKVL J345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 73112 [MANCHSTR345.00] CKT 1
OPEN LINE FROM BUS 73103 [MEEKVL J345.00] TO BUS 72925 [LUDLOW 345.00] CKT 1
MONTVSTBKR : OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73110 [MILLSTNE345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 1
OPEN LINE FROM BUS 73109 [MONTVILE345.00] TO BUS 73210 [MONTVLLE115.00] CKT 2
NOMNTSTBKR : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
NMSTBKREAC : OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72924 [BERKSHRE345.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72952 [BERKSHIR115.00] CKT 1
OPEN LINE FROM BUS 72924 [BERKSHRE345.00] TO BUS 72928 [MANY393 345.00] CKT 1
OPEN LINE FROM BUS 72928 [MANY393 345.00] TO BUS 78700 [ALPS345 345.00] CKT 1
OPEN LINE FROM BUS 72926 [NRTHFLD 345.00] TO BUS 72927 [MANH381 345.00] CKT 1
OPEN LINE FROM BUS 72927 [MANH381 345.00] TO BUS 70486 [VTYNK345345.00] CKT 1
OPEN LINE FROM BUS 70508 [SANDB115115.00] TO BUS 70509 [SB RCTOR115.00] CKT 2
SCOVRK4TSTK : OPEN LINE FROM BUS 73120 [KLEEN 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK5TSTK : OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73668 [E.SHORE 115.00] CKT 2
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73664 [NHHHVDCL345.00] CKT 1
OPEN LINE FROM BUS 73663 [E.SHORE 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73664 [NHHHVDCL345.00] TO BUS 73665 [NHHHVDCL191.50] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73557 [MIDDTN#422.000] CKT 1
OPEN LINE FROM BUS 73116 [MIDDLTWN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK7TSTK : OPEN LINE FROM BUS 73120 [KLEEN 345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73113 [HADDM NK345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SCOVRK8TSTK : OPEN LINE FROM BUS 73107 [SCOVL RK345.00] TO BUS 73113 [HADDM NK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
SGTN1TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SGTN3TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 2
SGTN4TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73122 [MERID362345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
SGTN5TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73104 [FRSTBDGE345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
SGTN6TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73154 [SGTN B 115.00] CKT 3
SGTN7TSTK : OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73107 [SCOVL RK345.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 1
OPEN LINE FROM BUS 73106 [SOUTHGTN345.00] TO BUS 73198 [SOUTHGTN115.00] CKT 4
NORGLENLINE : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
NHBRGLENLINE: OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWALKST1 : OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73158 [WESTON 115.00] CKT 1
OPEN LINE FROM BUS 73292 [NRWLK RX115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWALKST2 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73710 [HAWTHORN115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
NORWALKST3 : OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73174 [PEACEABL115.00] CKT 1
OPEN LINE FROM BUS 73172 [NORWALK 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR1T : OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
NORWLKHAR2T : OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR3T : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 2
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 3
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
NORWLKHAR4T : OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73552 [NORHAR#220.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHAR7T : OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
OPEN LINE FROM BUS 73551 [NORHAR#118.000] TO BUS 73171 [NWLK HAR115.00] CKT 1
NORWLKHARBT : OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 1
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 2
OPEN LINE FROM BUS 73166 [NORHR138138.00] TO BUS 75053 [NRTHPT P138.00] CKT 3
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
GLNBRKASTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73294 [GLNBRK J115.00] TO BUS 73267 [DARIEN 115.00] CKT 1
GLNBRKA1STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
GLNBRKA2STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
GLNBRKA3STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
GLNBRKA4STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73294 [GLNBRK J115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
GLNBRKBSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73271 [RYTN J B115.00] TO BUS 73207 [FLAX HIL115.00] CKT 1
GLNBRKB1STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
GLNBRKB2STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GLNBRKB3STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
GLNBRKB4STK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73145 [CDR HGTS115.00] CKT 2
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73271 [RYTN J B115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 2
GLNBRKCSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73162 [WATERSDE115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73169 [RYTN J A115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
GLNBRKDSTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73167 [SO.END 115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73168 [GLNBROOK115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
OPEN LINE FROM BUS 73237 [ELYAVE 115.00] TO BUS 73173 [SASCO CR115.00] CKT 1
GLNBRKESTK : OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73172 [NORWALK 115.00] CKT 1
OPEN LINE FROM BUS 73168 [GLNBROOK115.00] TO BUS 73171 [NWLK HAR115.00] CKT 1
DC1-BES-NOR : REMOVE MACHINE 1 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 1 FROM BUS 73293 [NORWALK 345.00]
DC2-BES-SIN : REMOVE MACHINE 2 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 2 FROM BUS 73700 [PEQUONIC115.00]
DC3-BES-DEV : REMOVE MACHINE 3 FROM BUS 73295 [BESECK 345.00]
REMOVE MACHINE 3 FROM BUS 73129 [E.DEVONJ115.00]
DC4-SIN-NOR : REMOVE MACHINE 4 FROM BUS 73700 [PEQUONIC115.00]
REMOVE MACHINE 4 FROM BUS 73293 [NORWALK 345.00]
DC5-DEV-NOR : REMOVE MACHINE 5 FROM BUS 73129 [E.DEVONJ115.00]
REMOVE MACHINE 5 FROM BUS 73293 [NORWALK 345.00]

## nonconverged
ACCC NON-CONVERGED NETWORK REPORT:
BUS MISMATCH TOLERANCE= 2.5000 MVA
SYSTEM MISMATCH TOLERANCE= 20.0000 MVA
DISTRIBUTION FACTOR FILE: C:\Projects\10934 NE Utilities DC\DC Light\PSSE Files\Case 2.dfx
SUBSYSTEM DESCRIPTION FILE: C:\Projects\10934 NE Utilities DC\DC Light\PSSE Files\swctnew.sub
MONITORED ELEMENT FILE: C:\Projects\10934 NE Utilities DC\DC Light\PSSE Files\swct0802.mon
CONTINGENCY DESCRIPTION FILE: C:\Projects\10934 NE Utilities DC\DC Light\PSSE Files\contigphase2-091503-kleen-newDC.con
X--MISMATCH (MVA)--X
CONTINGENCY BUS SYSTEM TERMINATION CONDITION
TRIANGLE2T 77.432 627.59 ITERATION LIMIT EXCEEDED
TRIANGLE3T 55.374 498.51 ITERATION LIMIT EXCEEDED
WOODMNT1TSTK 0.89031 35.026 MET CONVERGENCE TOLERANCE
WOODMNT2TSTK 0.92499 37.872 MET CONVERGENCE TOLERANCE
CONTINGENCY LEGEND
LABEL EVENTS
TRIANGLE2T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 1
TRIANGLE3T : OPEN LINE FROM BUS 73170 [PLUMTREE115.00] TO BUS 73176 [TRIANGLE115.00] CKT 2
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73383 [TRIANGLB13.800] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73268 [MIDDLRIV115.00] CKT 1
OPEN LINE FROM BUS 73176 [TRIANGLE115.00] TO BUS 73377 [TRIANGLA13.800] CKT 2
WOODMNT1TSTK: OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73684 [ALLINGSA115.00] CKT 1
OPEN LINE FROM BUS 73684 [ALLINGSA115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
OPEN LINE FROM BUS 73686 [WDMONT A115.00] TO BUS 73746 [WOODMONT13.800] CKT 1
OPEN LINE FROM BUS 73195 [DEVON 115.00] TO BUS 73690 [DEVON178115.00] CKT 1
OPEN LINE FROM BUS 73690 [DEVON178115.00] TO BUS 73688 [MILVON A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73686 [WDMONT A115.00] CKT 1
OPEN LINE FROM BUS 73688 [MILVON A115.00] TO BUS 73748 [MILVON 13.800] CKT 1
WOODMNT2TSTK: OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73685 [ALLINGSB115.00] CKT 1
OPEN LINE FROM BUS 73687 [WDMONT B115.00] TO BUS 73746 [WOODMONT13.800] CKT 1
OPEN LINE FROM BUS 73685 [ALLINGSB115.00] TO BUS 73744 [ALLINGS 13.800] CKT 1
OPEN LINE FROM BUS 73691 [DEVON179115.00] TO BUS 73689 [MILVON B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73687 [WDMONT B115.00] CKT 1
OPEN LINE FROM BUS 73689 [MILVON B115.00] TO BUS 73748 [MILVON 13.800] CKT 1