STATE OF CONNECTICUT

CONNECTICUT SITING COUNCIL

## Northeast Utilities Service Company Application		   	          Docket No. 272

to the Connecticut Siting Council for a

Certificate of Environmental Compatibility and

Public Need (“Certificate”) For The Construction

of a New 345-Kv Electric Transmission Line

Facility and Associated Facilities Between Scovill

Rock Switching Station in Middletown and

Norwalk Substation In Norwalk, Including the

Reconstruction of Portions of Existing 115-kV and

345-kV Electric Transmission Lines, the Construction

of Beseck Switching Station in Wallingford, East

Devon Substation in Milford, and Singer Substation

in Bridgeport, Modifications at Scovill Rock

Switching Station and Norwalk Substation, and the

Reconfiguration of Certain Interconnections 			      												 November 30, 2004

## KEMA RESPONSES TO OFFICE OF CONSUMER COUNSEL’S

# FOURTH SET OF INTERROGATORIES

INTERROGATORIES:

OCC-32	Please refer to the KEMA Report, p. 9, stating that KEMA developed “a new 368-bus model” for its studies. Does KEMA believe that its model is fully equivalent to and consistent with the model used by the Applicant’s consultant for its studies reported in this docket? Please explain any answer in specific detail.

A:  The 368-bus system model was supplied to KEMA by the Applicant in ASPEN format. This model was also originally supplied to the Applicant’s Consultant to build their EMTP model.  KEMA built from this original ASPEN model the PowerFactory model used in its studies.  KEMA has not had the opportunity to review the model used by the Applicant’s consultant.  Therefore, we cannot comment on the relative equivalence or consistency of the two models.

- Harmonic performance. Refer to the KEMA Report, pp. 29-30.

- Did those aspects of the KEMA analysis implicating the Phase One transmission project assume or test any configurations for that project that differ from what actually is planned for its construction? Please explain any answer in specific detail.

A:	No. Phase I was used only for comparison purposes. One HPFF cable for Phase I with Phase II in operation, is also one of the operational cases studied by the Applicant and their consultants.

- How does KEMA rank the relative importance of harmonic, transient, thermal and voltage, stability and short circuit performance when evaluating the reliability of various configurations for the Phase Two transmission project? Please explain any answer in specific detail.

A:	All of these design criteria should be considered for a system to be reliable. Harmonic impedance calculations were used by KEMA, similar to the Applicant, as a screening tool for the different network configurations.  KEMA has not established any ranking for these various performance criteria.

- Refer to the KEMA Report, p. 69, Recommendation 3, stating that transient analyses should be performed.

- Does KEMA intend to do such transient analyses? If yes, when does KEMA expect the results of such studies to be available? If no, why not, and whom does KEMA propose could or should do such studies?

A:	KEMA has not done any transient calculations on the specific configuration.  We believe that the Applicant’s consultant has performed some of these transient calculations since the summer, but no results have been made available. KEMA, as an independent consultant, will gladly contribute to these transient calculations in close cooperation with the Applicant, if and when required.

- Does KEMA believe that transient studies are required before a valid answer can be given to the question of how many miles of underground construction for the Phase Two project are compatible with electric system reliability?

A: Yes, if the transient analyses yield results that are not satisfactory, acceptable mitigation should also be evaluated before a final decision is made on the maximum length of undergrounding that is feasible.

- Transient performance. Refer to the ROC Group Report, filed in this docket on August 16, 2004, and the studies conducted in connection with that report.

- Does KEMA believe that the transient performance of the SW CT electrical system must be acceptable for that system to be considered reliable?

A: Yes, but acceptable mitigation options should also be evaluated if the transient analyses do not yield satisfactory results.

- If no, why not? If yes, what does KEMA believe is the minimum acceptable level of transient performance for the SW CT electrical system, and what does KEMA believe is the preferable level of transient performance for the SW CT electrical system? Please explain any answers in specific detail.

A: KEMA has not established either “minimum acceptable” or “preferable” levels of transient performance.

- Thermal and voltage performance. Refer to the Application, 10/9/03, Vol. 1, p. F-28 and the ROC Group Report, filed in this docket on August 16, 2004, and the studies conducted in connection with that report.

- Does KEMA believe that the thermal and voltage performance of the SW CT electrical system must be acceptable for that system to be considered reliable?

A: Yes.

- If no, why not? If yes, what does KEMA believe is the minimum acceptable level of thermal and voltage performance for the SW CT electrical system, and what does KEMA believe is the preferable level of thermal and voltage performance for the SW CT electrical system? Please explain any answers in specific detail.

A: The minimum acceptable levels of thermal and voltage performance for the SW CT electrical system are those that exactly meet the reliability standards established by the Applicant and NEPOOL.   KEMA has not defined a “preferable” level of thermal and voltage performance for the SW CT electrical system.

- Stability performance. Refer to the ROC Group Report, filed in this docket on August 16, 2004, and the studies conducted in connection with that report.

- Does KEMA believe that the stability performance of the SW CT electrical system must be acceptable for that system to be considered reliable?

A: Yes.

- If no, why not? If yes, what does KEMA believe is the minimum acceptable level of stability performance for the SW CT electrical system, and what does KEMA believe is the preferable level of stability performance for the SW CT electrical system? Please explain any answers in specific detail.

A: The minimum acceptable level of stability performance for the SW CT electrical system is that which exactly meets the stability standards established by the Applicant and NEPOOL.   KEMA has not defined a “preferable” level of stability performance for the SW CT electrical system.

- Short circuit performance. Refer to the Application, 10/9/03, Vol. 1, pp. F-29-30 and the ROC Group Report, filed in this docket on August 16, 2004, and the studies conducted in connection with that report.

- Does KEMA believe that the short circuit performance of the SW CT electrical system must be acceptable for that system to be considered reliable?

A: Yes.

- If no, why not? If yes, what does KEMA believe is the minimum acceptable level of short circuit performance for the SW CT electrical system, and what does KEMA believe is the preferable level of short circuit performance for the SW CT electrical system? Please explain any answers in specific detail.

A: The minimum acceptable level of short circuit performance for the SW CT electrical system is that which exactly meets the standards established by the Applicant and NEPOOL.  KEMA has not defined a “preferable” level of short circuit performance for the SW CT electrical system.

- Refer to the Application, 10/9/03, Vol. 1, pp. F-24-31, where the SW CT electrical system is described as inadequate to meet national and regional reliability performance standards.

- Does KEMA agree with this assessment of the present SW CT electrical system?

A: KEMA has made no independent evaluation of the Applicant’s system assessment, as summarized in Volume 1 of the Application.

- How is such electrical system weakness measured and evaluated? How should it be measured and evaluated?  Please explain any answer in specific detail.

A:  To our knowledge there is no universally accepted definition of “electrical system weakness.” In some instances “system weakness” is used to describe a system that is less “strong” than another system.  In this context, system “strength” is a measure of the ability of a system to deliver power at a given location.

- Would construction of the transmission system configuration that KEMA recommends for further study (i.e., 10-20 miles of additional undergrounding) strengthen the SW CT electrical system?

A: From the KEMA report it is clear that with extended undergrounding both the system strength and system damping are increased over that for the SW CT system with Phase I improvements only.

- Would the construction of such a project (i.e., with 34-44 miles of undergrounding) fully resolve the present electrical system weaknesses found in SW CT?

A: A detailed analysis of all system weaknesses was not part of KEMA’s harmonic analysis. With this amount of network extension a more reliable and interconnected system will result.

- If this transmission project were built with 34-44 miles of undergrounding, as KEMA has stated may be possible, would the SW CT electrical system still be relatively weak? Would it be measurably strengthened? Would it be decisively strengthened?

A: A detailed analysis of system weaknesses was not part of KEMA’s harmonic analysis. However, it is clear from the harmonic impedance results that the proposed system will be significantly strengthened over the system with only the Phase I improvements.

- Refer to the ROC Group Report filed in this docket on October 8, 2004, and specifically its analysis of “Case 7.” Does KEMA agree with the ROC Group conclusion concerning STATCOM units, namely that no further consideration should be given to utilization of multiple STATCOM units as a mitigation measure? Please explain any answer in specific detail.

A: KEMA agrees that the use of multiple STATCOMS alone does not appear to be a feasible mitigation alternative due to the limited ability of a small number of STATCOMs to keep the system’s 1st harmonic resonance point above 3.0.  However, the use of an additional 1 or 2 STATCOMs in conjunction with other mitigation, such as C-type filters, is worthy of further study.

- Refer to the KEMA Report, p. 60, Key Conclusions 4 and 7, for the 10 Mile Underground Results.

- On what basis were Southington and Southington Ring 1 excluded from these conclusions?

A: In the tables, summarizing the results, Southington 345 kV and 115 kV substations are listed to have maximum impedance values below the 3rd harmonic. From the detailed plotted results it is clear that these are not resonance peaks, as such.  These maximum values, indicated around or below the 3rd harmonic, are the result of the system characteristics and the filtering properties of the C-Type filter. These maximum values are also damped to levels that they do not pose any problems in terms of over-voltages or resonances. Therefore the results from these substations are excluded from the conclusions.

- Would these key conclusions be the same if Southington and Southington Ring 1 had been included here?

A: Yes.

- Refer to the KEMA Report, p. 62, Key Conclusions 4 and 7, for the 20 Mile Underground Results.

- On what basis were Southington and Southington Ring 1 excluded from these conclusions?

A: See answer to question 41.

- Would these key conclusions be the same if Southington and Southington Ring 1 had been included here?

A: Yes.

- Refer to the KEMA Report, p. 64, reporting the results of KEMA’s analysis of underground construction for all of Segments 1 and 2 of the proposed project. Has KEMA concluded that it is definitely not possible to construct all 69 miles of this proposed project underground, based on system reliability considerations? Please explain any answer in specific detail.

A: Based on harmonic performance alone, KEMA has concluded this is not technically feasible.  For undergrounding beyond 44 miles, first harmonic resonance points are approaching 3.0 even with mitigation from C-Type filters.  ISO-NE has identified a first harmonic resonance point above 3.0 as a prerequisite for acceptability because of the potential for distortion and overvoltage due to harmonic amplification near the 2nd harmonic point.

- Refer to the KEMA Report, p. 69, Conclusion 5, mentioning the difficulty of system operations when certain equipment is installed.

- Does KEMA believe that the difficulty of system operations is a factor that should be taken into account when evaluating whether an electrical system is reliable? Please explain any answer in specific detail.

A:  Yes, system design and operability are inseparable factors in determining whether a given system alternative is reliable.

- Does KEMA believe that the SW CT electrical system will be more difficult to operate if the proposed project is constructed with 34-44 miles of undergrounding, with the additional filtering recommended, and with further mitigation measures included as appropriate?

A: KEMA has not made any studies to assess operational difficulties.  KEMA does not believe these will be significantly greater than with 24 miles of underground cable.

- Refer to the KEMA Report, p. 9, stating that SW CT has inadequate local generation, and to the Application, 10/9/03, Vol. 1, p. F-30, referring to existing restrictions on the operation of generation resources in SW CT.

- Please state whether KEMA believes that it is possible to make the most efficient use of generation resources within SW CT, under each of three different system configurations, namely, (i) the existing transmission system in this area, (ii) the facility that the Applicants have applied to build [i.e., with 45 miles overhead and 24 miles underground], and (c) the Applicants’ proposal as modified through the addition of 10-20 miles of underground construction that KEMA states may be possible.

A: KEMA does not know what is meant by “make the most efficient use of generation resources.”  KEMA has not investigated the relative merits of alternative uses of generation resources in SWCT.

- Does KEMA believe that the possibility for such efficient use of generation resources is a standard that should be addressed when determining the reliability of a transmission system?

A: KEMA cannot answer this question without a clear definition of what is meant by “efficient use of generation resources.”

- Did KEMA use the possibility for such efficient use of generation resources as a standard to evaluate the various transmission line configurations considered in the KEMA Report?

A: No.

- Refer to the KEMA Report, p. 9, stating that SW CT has inadequate local generation.

- Please state whether KEMA believes that it is possible to take any existing generation units within SW CT off-line for re-powering, under each of three different system configurations, namely, (i) the existing transmission system in this area, (ii) the facility that the Applicants have applied to build [i.e., with 45 miles overhead and 24 miles underground], and (c) the Applicants’ proposal as modified through the addition of 10-20 miles of underground construction that KEMA states may be possible.

A: KEMA has made no evaluation as to whether it is possible to “. . .take any existing generation units within SW CT off-line for re-powering . . .”  Therefore, KEMA has not formed an opinion on this matter.

- Does KEMA believe that the possibility for such re-powering is a standard that should be addressed when determining the reliability of a transmission system?

A:  Power supply adequacy is a standard that should be addressed when determining the reliability of a transmission system.  Generating unit repowering should be evaluated in that context.

- Did KEMA use the possibility for such re-powering as a standard to evaluate the various transmission line configurations considered in the KEMA Report?

A:  No.

- Refer to the KEMA Report, p. 9, stating that SW CT has inadequate local generation, and to the Application, 10/9/03, Vol. 1, p. F-31, referring to allowance for the addition of new generation resources in SW CT.

- Please state whether KEMA believes that it is possible to add new generation resources within SW CT, under each of three different system configurations, namely, (i) the existing transmission system in this area, (ii) the facility that the Applicants have applied to build [i.e., with 45 miles overhead and 24 miles underground], and (c) the Applicants’ proposal as modified through the addition of 10-20 miles of underground construction as KEMA states may be possible.

A:  KEMA’s answer is “yes” for all three system configurations.

- Does KEMA believe that the possibility for such addition of new generation resources is a standard that should addressed when determining the reliability of a transmission system?

A:  KEMA agrees that the possibility of adding new generation resources should be considered when evaluating the current and future reliability of a power supply system with expected load growth.

- Did KEMA use the possibility for such addition of new generation resources as a standard to evaluate the various transmission line configurations considered in the KEMA Report?

A:  No, KEMA’s studies examined only system harmonic performance under two assumed dispatches of existing generation.

- Refer to the ROC Group Report filed in this docket on August 16, 2004, and the statement (p. 4) that it was a significant challenge to “track new risks to system operability and reliability that are introduced when seeking to develop an atypical transmission design.”

  - Does KEMA believe that adding more undergrounding to the proposed project (beyond the 24 miles the Applicants have proposed) would represent an atypical transmission design for the specific area where the line is to be sited?

A:  KEMA does not know precisely what the referenced report means by the term “atypical transmission design.”  However, we presume that the Applicant’s Phase II proposal to underground 24 miles of additional transmission is not judged to be “atypical.”  Therefore, we do not believe that undergrounding 10 – 20 miles further would be considered “atypical.”

  - Does KEMA agree that such tracking of new risks is a significant challenge?

A:  Yes.

  - Do the system configurations that KEMA studied introduce new risks to system operability and reliability? If no, why not? If yes, please describe those new risks in specific detail.

A:  With regard to additional undergrounding, please see the previous answer to OCC-48 (a).  With regard to mitigation, KEMA examined STATCOMs and C-Type filters.  KEMA’s report (p. 32) mentions the “operational issues associated with operating numerous STATCOMs,” and these issues are discussed further in response to OCC-68.  We do not believe that C-Type filters would introduce new risks associated with an  atypical transmission design.  These are passive devices that contribute in the same way that regular capacitor banks do to provide voltage support at the fundamental frequency, and they are switched on and off in much the same way.

  - Does the KEMA Report track new risks to system operability and reliability that the system configurations it studied may introduce? Does the KEMA Report specifically address those risks, through analysis of mitigation measures or otherwise? Please explain any answers in specific detail.

A:  No, the KEMA report does not track new risks to system operability and reliability.  Neither does the report specifically address these risks through mitigation measures or otherwise.

- Refer to the ROC Group Report filed in this docket on October 8, 2004, and its statement (on p. 9-13 and otherwise) of 13 system criteria that the proposed facility must meet.

  - Does KEMA agree that any facility approved by the Siting Council must meet each of these 13 system criteria? Please explain any answer in specific detail.

A:  KEMA has not been asked to review the criteria used by the Siting Council in approving new facilities.  Therefore, KEMA is not in a position to comment on whether the criteria adopted by the ROC Group are appropriate for use by the Siting Council.

  - Please provide a summary chart stating whether, for each of the 11 key study cases that KEMA analyzed, the case meets each of the 13 system criteria specified in the ROC Group Report. Please provide additional explanatory details as appropriate.

A: Criterion 1:  KEMA cannot comment on whether its study cases meet this criterion.  We have not explicitly evaluated moving 1,200 MW of power into SWCT.

Criterion 2:  KEMA cannot comment on whether its study cases meet this criterion.  We have not evaluated short circuit issues at the referenced locations.

Criterion 3:  KEMA cannot comment on whether its study cases meet this criterion.  We have not evaluated generation interdependencies at Pequonnock, Devon, and Norwalk Harbor.

Criterion 4:  This criterion was the subject of KEMA’s Harmonic Impedance Study Report.  The results for the 11 referenced study cases do not lend themselves to a simple yes or no answer, as requested.  To answer the question that has been raised, please see the referenced Report Tables for the following study cases:

Case I-1 - Table 7, page 43

Case II-1 – Table 8, page 46

Case II-2 – Table 8, page 46

Case II-3 – No results were obtained, load flow did not converge

Case II-4 – See graphical results pages 87-90

Case II-5 – Table12, page 56

Case II-6 – Table 12, page 56

Case II-7 – Table 14, page59

Case II-8 – Table 15, page61

Case II-9 – Table 16, page 63

Case II-10 – See graphical results pages 126-129

Criterion 5:  KEMA believes this is satisfied for all study cases.

Criterion 6:  KEMA believes this is satisfied for all study cases.

Criterion 7:  KEMA cannot comment on whether its study cases meet this criterion.  KEMA did not explicitly evaluate different load cycles or varying dispatches.  Line outages were examined only in load-flow studies that will be made available in the near future.

Criterion 8:  KEMA cannot comment on whether its study cases meet this criterion.  KEMA did not address line overloads in this report.  KEMA’s load-flow analysis may indicate some additional overloads, especially at 115 kV and below.

Criterion 9:  KEMA cannot comment on whether its study cases meet this criterion.  KEMA has not explicitly evaluated physical limitations.

Criterion 10:  KEMA cannot comment on whether its study cases meet this criterion.  KEMA has not evaluated system stability effects.

Criterion 11:  KEMA cannot comment on whether its harmonic impedance study cases meet this criterion.  This report does not address adequate voltage on the system.  KEMA’s load-flow report to be released in the near future will show voltage violations for some configurations.  KEMA believes these can be satisfactorily mitigated.

Criterion 12:  KEMA cannot comment on whether its study cases meet this criterion.  KEMA has not evaluated the effect on existing contracts and system capabilities.

Criterion 13:  KEMA cannot comment on whether its study cases meet this criterion.  KEMA has not evaluated Sub-synchronous Torsional Interaction effects.

- Refer to the Supplemental Pre-Filed Testimony of ISO New England, Inc., (Stephen G. Whitley), filed in this docket on June 7, 2004, and its discussion (at pp. 2-4, etc.) of Good Utility Practice.

  - Does KEMA agree that any facility approved by the Siting Council must meet the Good Utility Practice standard?

A:  KEMA has not been asked to review the criteria used by the Siting Council in approving new facilities.  Therefore, KEMA is not in a position to comment on whether the criteria adopted by the ROC Group are appropriate for use by the Siting Council.

  - Would construction of the transmission system configuration that KEMA recommends for further study (i.e., 10-20 miles of additional undergrounding) meet the Good Utility Practice standard? Please explain any answer in specific detail.

A: KEMA has not attempted to evaluate the conformance of the referenced system configuration to what Mr. Whitley’s testimony defines as “Good Utility Practice.”  We have cited the need for additional studies to confirm the reliability of such a configuration.  Some parties might disagree as to whether additional undergrounding would result in a “reasonable cost,” but KEMA was not asked to evaluate this aspect of the referenced system configuration.  Finally, we have made no evaluation of the effects of such a configuration on “expedition.”

  - Refer to the KEMA Report, p. 9, stating that SW CT has inadequate local generation.

- Please provide a comparison of the transmission import capability into SW CT and the Norwalk-Stamford area under each of the three different system configurations, namely, (i) the existing transmission system in this area, (ii) the facility that the Applicants have applied to build [i.e., with 45 miles overhead and 24 miles underground], and (iii) the Applicants’ proposal as modified through the addition of 10-20 miles of underground construction as KEMA states may be possible.

A:  KEMA has not evaluated the transmission import capabilities of these three system configurations.

- Does KEMA consider the transmission import capability into SW CT and the Norwalk-Stamford area as a standard that should addressed when determining the reliability of a transmission system?

A:  Transmission import capability is not a reliability “standard.”  Rather, it is a system attribute that should be considered, together with system load and local generation capability in assessing the reliability of the overall power supply system.

- Did KEMA use the transmission import capability into SW CT and the Norwalk-Stamford area as a standard to evaluate the various transmission line configurations considered in the KEMA Report?

A:  No, KEMA did not explicitly consider transmission import capability in evaluating the referenced transmission line configurations.

  - Please provide estimates of the costs (unit costs and overall costs) of using C-type filters to mitigate harmonic problems, as recommended in the KEMA Report.

A:  The price per bank can only be determined in cooperation with manufacturers, after a specification is finalized. It is however important to note that the components in the existing capacitor banks may be used in the converted C-Type design.  Budget prices for new installations, based on previous installations may be in the range of $12 - 18 per kVAr for a 150 MVAr, 115 kV design.

- Refer to the KEMA Report, p. 6. Please provide a copy of any qualifications that KEMA submitted to the Siting Council describing KEMA’s expertise in harmonic impedance studies.  If none was submitted, please provide KEMA’s qualifications and experience in harmonic studies.

A: KEMA is a company of 1500 consultants in the different areas of power engineering and numerous similar studies have been performed. The resumes of the principal investigators for this study were made available to all parties concerned, indicating the key projects and qualifications. In the proposal for this project the key qualifications and projects were listed. Relevant qualification sections of the proposal are included in a separate file.

- Please provide a detailed list of all other Harmonic Impedance studies or similar analyses performed by KEMA.  Include the name of the client, the date completed, a description of the system being analyzed, the type of transmission alternatives being studied, the analytical tools or software used, a summary of the results, and any recommendations.  If possible, provide copies of those reports.

A: See answer to question 53. Some recent key projects by the principal consultants include harmonic impedance studies for Nuon, Eneco, TenneT and BritNed.  In some of these studies C-Type filters were also studied, designed and commissioned for the Dutch HV grid.

- Please describe the history and experience with passive C-type filters.  How many of these devices are in service in the US?  Where are they located and what are their specifications?  What has been their performance track record to date?  Please provide all reports that describe actual C-type filter performance.

A: These filters have been in operation since the early 1980’s on HV systems in the 115 kV to 400 kV voltage levels. The exact number of banks installed in the USA and the world cannot be determined on short notice. From previous work in this area KEMA has knowledge of several 150 – 225 MVAr banks on the 132 kV, 275 kV and 400 kV system of National Grid (UK). These filters have already been in operation more than 5 years. In some cases, existing mechanically-controlled banks were converted to C-Type filter designs on the 132 kV system. The relocatable SVCs on NGC’s grid are also equipped with C-type designs. TenneT, the Dutch 150 – 380 kV Transmission System Operator, has installed 2 years ago, ten 150 MVAr C-Type capacitor banks on most of the 380 kV and 220 kV substations for reactive power control. A more complete list and references can be compiled in cooperation with several US and European manufacturers.

- Refer to the KEMA Report, p. 9. Where are the 368 busses located?  Are all in SW CT, within the NU transmission system, or do they extend to all of the ISO-NE control area?  How are ties to other areas modeled?

A: In the 368-bus system supplied by the Applicant, the buses are mainly located in SW CT with buses extended to most parts of Northern CT and to parts of Eastern CT. Systems beyond the modeled area were modeled using equivalents.

- Other than the Phase I assets, how many miles of underground transmission lines are included in the 368-bus model?  What type of cable is each of these, how long is each line, how are they modeled, and where are they located?

A: Data supplied to KEMA for lines of the 368-bus system other than Phase I contained information on positive and zero sequence impedance values only. The OCC could check with the Applicant for additional information about these lines.

- Refer to the KEMA Report, p. 10. Please describe the PowerFactory computer program, its inputs and outputs, and how it functions.

A: The DIgSILENT PowerFactory software is an integrated power system analysis tool that combines reliable and flexible system modeling capabilities, with state-of-the-art solution algorithms and a unique database management concept. The company's web site, http://www.digsilent.de/, provides a wealth of information about the capabilities of the software. Please visit company's web site and/or contact the company directly for detailed information.

- Refer to the KEMA Report, p. 13. Please identify all known power converters within the 368-bus model, provide their location, and describe how they were modeled.

A: Data received by KEMA did not indicate there were any converters with the modeled system. None were modeled.

- Refer to the KEMA Report, pp. 23-24.

  - How were the light and minimum generator dispatch conditions contained in Table 2 determined?

A: In Table 2, the light dispatch conditions are identical to the light dispatch conditions assumed by the Applicants consultant, GE, in its harmonic impedance studies.  The “minimum dispatch” conditions in Table 2 are identical to the “light post project dispatch” used by GE.

  - Were any other dispatch scenarios considered or utilized?  How sensitive are the results to changes in this dispatch?

A: No other dispatch scenarios were utilized.  A peak generator dispatch was considered but was not used because it would not stress the system as much as either the light or minimum generator dispatches.

  - Would placing generation at Norwalk in-service affect the results?

A:  We do not know because KEMA did not study this possibility.  KEMA expects that such generation would be beneficial to harmonic performance.

- Refer to the KEMA Report, p. 24. Would capacitors to perform voltage support be required more during heavy load periods or during light / medium periods?

A: Such capacitors would be required more during heavy load periods.

- Refer to the KEMA Report, p. 25.

  - Please describe the physical and electrical characteristics of XLPE and HPFF cables, as modeled in Powerfactory.  

A: Detailed information about XLPE and HPFF cables could be found in many references. One of them is the EPRI’s “Underground Transmission Systems Reference Book”. In short, differences in the insulation material, the construction and the installation of cables would result in differences in their electrical parameters such as positive and zero sequence impedance including the charging capacitance, etc. In PowerFactory, a line is modeled using the positive and zero sequence line impedance values, regardless whether it is a cable or an overhead line.

  - Explain why charging capacitance for XLPE is 60% of HPFF.

A: A XLPE cable generally has less charging capacitance than that of a HPFF cable, because it uses the insulation material and construction that is very different from that of a HPFF cable. The actual charging capacitance difference between cables depends upon the exact cables used for comparison. The data supplied by the Applicant indicate that a 3000 kcmil XLPE cable has approximately 60% of the charging capacitance of that of a 3000 kcmil HPFF cable.

  - Explain how any differences in the physical and electrical characteristics (e.g., charging capacitance) of XLPE and HPFF cables affects the harmonic performance of the KEMA undergrounding proposal.  

A: Assuming other conditions are the same (system short circuit level, line length, etc.), the higher the per-mile charging capacitance of a cable is, the lower the first resonance frequency of the system will be.

  - How did KEMA treat such differences in its study?  

A: KEMA used XLPE cable in its simulation cases, because it has lower per-mile charging capacitance which would allow for longer undergrounding than using a HPFF cable.

- How did any differences in physical and electrical characteristics of XLPE and HPFF cables affect KEMA’s recommendations addressing each of three configurations, namely, (i) the existing transmission system in this area, (ii) the facility that the Applicants have applied to build [i.e., with 45 miles overhead and 24 miles underground], and (iii) the Applicants’ proposal as modified through the addition of 10-20 miles of underground construction as KEMA states may be possible?

A: KEMA only used the parameters of XLPE cables in its harmonic impedance studies, mainly due to the lower charging capacitance of these cables. No HPFF cables were considered in KEMA’s studies.

- Refer to the KEMA Report, p. 27.

  - Please explain why “a load in the range of 70-100% of full load with all capacitors in service is expected to be a worst case.”

A: This is the approximate load range for which KEMA believes it is reasonable to expect all fixed capacitors to be in service.  At lower load levels, either some or all of these capacitors would likely be switched “off.”  As the report states, “. . . (this) is expected to be a worst case from the harmonic impedance perspective,” because increased amounts of capacitance tend to lower the first harmonic resonance point to frequencies that approach the 2nd and 3rd harmonics.  System resonant frequencies at these levels can result in significant overvoltages during transformer energization and should be avoided, if possible, or be mitigated.

  - If a 100% full load scenario was studied, what generator dispatch was assumed?

A: Both “light” and “minimum” local generator dispatch scenarios were assumed, as specified in KEMA’s Report, Table 2, pp. 23-24

- Refer to the KEMA Report. p. 27. Do any of the capacitors listed in Table 3 have the ability to operate at levels between “all on” and “all off”?  Are any of these dispatchable remotely, manually operated, or are they fixed?

A: The third column of Table 3 lists the number of capacitor banks at each substation.  KEMA assumes that each bank may be switched on and off independently, but this needs to be confirmed with the Applicant.  We do not know if any or all of the capacitor banks are remotely dispatchable.  We assume that each bank is “fixed” (in terms of the amount of capacitance) and that each bank can be manually switched on or off.

- Refer to the KEMA Report, p. 28, section 3.6.7. Please explain why the Glenbrook STATCOM was not included in the model. How are these devices normally modeled in PowerFactory?

A: The Glenbrook STATCOM was included in the harmonic impedance calculation model. The details of a STATCOM model, in PowerFactory or any other modeling tool, depends on the required type of study (Load flow, harmonic, transient, transient stability, etc.).  For frequency scans, because the capacitance of a STATCOM is “electrically” removed from the system, it is appropriate to exclude that amount of capacitance from the system model.  For dynamic studies, a more detailed STATCOM model, including its control system, is required.  Please refer to the KEMA Report, p. 32, Section 5.1 for a more detailed discussion of STATCOM characteristics.

- Refer to the KEMA Report, p. 30. Why does KEMA recommend that a detailed background harmonic voltage measurement program be undertaken?  Would the results of this program be necessary to support the results of the KEMA study?  Have any such voltage measurements been taken?  If so, please provide.

A: In order to quantify the expected harmonic performance of the SWCT system, including the network extensions, harmonic measurements will be required. To KEMA’s knowledge, no detailed harmonic voltage measurements have been undertaken to date.  These measurements may be required for the detailed design of the mitigation options.

- Refer to the KEMA Report, p. 32. Please describe the operational issues with operating numerous STATCOMs.

A: Due to the multi-functional operating characteristics of STATCOMs, numerous STATCOMs in an interconnected system may be difficult to operate manually. They can also “hunt” against each other in an automatic, closed-loop control arrangement.  To KEMA’s knowledge, several large STATCOMs, electrically in close proximity to one another, have not previously been installed and operated on a commercial network.

- Refer to the KEMA Report, p. 37, paragraph 6.1.1, which states that the load was changed between full and half load with all capacitor banks in service and light generator dispatch, because the minimum dispatch scenario would not solve or converge.

  - Did the full load, light generation dispatch scenario converge?  If so, what was the total load and total generation in SW CT, and how much was imported from the rest of New England?  

A: The loadflow of the full load, light generator dispatch scenario with all capacitors ON in harmonic studies using PowerFactory did converge for Phase I. The total load within the modeled 368-bus system in the PowerFactory, which encompasses the entire SW CT region and beyond, was approximately 7.0 GW.  Of this 7.0 GW load plus associated system losses, about 3.4 GW was locally generated, with the rest of power imported from the surrounding system.

  - Would the modeled transmission system be able to successfully deliver this imported power in this scenario?

A: KEMA’s harmonic studies using PowerFactory did not perform a detailed investigation as to whether the system would be able to successfully deliver the imported power for this scenario.

- Refer to the KEMA Report, pp. 37-38, paragraph 6.2.1, which states that the loads on all of the underlying substations are changed between full-load and half –load conditions with all capacitor banks in service and minimum generator dispatch.

  - Did the full load, minimum generation dispatch scenario converge?  If so, what was the total load and total generation in SW CT, and how much was imported from the rest of New England?  

A:  The loadflow for the full load, minimum dispatch case, with all capacitors ON scenario did converge in harmonic studies using PowerFactory. The total load within the modeled 368-bus system in PowerFactory, which encompasses the entire SW CT region and beyond, was approximately 7.0 GW. Of this 7.0 GW load plus associated system losses, about 2.0 GW was locally generated, with the rest of the power imported from the surrounding system.

  - Would the modeled transmission system be able to successfully deliver this imported power in this scenario?

A: KEMA’s harmonic studies using PowerFactory did not include a detailed investigation as to whether the system will be able to successfully deliver the imported power for this scenario. However, KEMA has performed separate loadflow studies for the new Phase II base case and several alternatives in PSS/E, based on the loadflow cases provided by the Applicant in response to Town’s Data Request No. 05—Q-Towns-059. The results of this separate loadflow study will be available in the near future.

- Refer to the KEMA Report, p. 69, Conclusion 6. Is it KEMA’s conclusion that a Phase II 20-mile underground extension with C-filters and / or STATCOM mitigation schemes represents a reliable system? Please explain.

A: The referenced conclusion states that such mitigation schemes can be employed to achieve “. . . a workable solution from a system resonance point of view.”  Additional studies, including transient analyses and voltage and thermal studies, must be performed to confirm that such mitigation would result in a reliable system.

- Refer to the KEMA Report, p. 69, Conclusions 6 and 7. Please explain the difference between “a workable solution from a system resonance point of view” and “a risky choice from a reliability perspective”?

A: “A workable solution from a system resonance point of view” refers to a mitigation scheme that can maintain lower-order resonances above 3.0 or ensure that such resonances are well damped.  “A risky choice from a reliability perspective” refers to a system alternative with lower order resonances that are (approximately) at or below 3.0 and are not well damped.

- Refer to the KEMA Report, pp. 25-26, referencing HPFF and XLPE cable.

- Please provide a summary of the performance history of the various types of cable being considered. How long have these been used in the industry? How many miles of such cable are in the ground? What is the overall operational/maintenance record for such cable?

A: KEMA does not possess such a performance history.  Neither was KEMA asked to prepare such a summary.  HPFF cables have been in use for at least 40 years in the U.S., primarily in urban areas. Extruded dielectric cables, including cross-linked polyethylene (XLPE) cables and low- or high-density polyethylene (PE) cables, have been employed at transmission voltages in the U.S. since the 1980s and have been used in Europe for more than 30 years.  We do not know how many miles of each type of cable are “in the ground.”  Finally, KEMA does not possess an “overall operational/maintenance record for such cable.”  If further checks show that KEMA does have such information, we will make it available.

- Has this performance history demonstrated any notable impacts on system reliability, positive or negative? Please describe.

A: KEMA is not aware of a performance history for either cable type that indicates the impact of its use on “system reliability.”

Submitted by:

KEMA, INC.

3801 Lake Boone Trail, Suite 200

Raleigh, NC  27607