## Table of Contents
AIR POLLUTION CONTROL COST EFFECTIVENESS ASSESSMENT FOR USE WITH RCSA SECTION 22a-174-22e(h)
EXPLANATION
|  | Prepared Date: | 2016-08-31
TABLE OF CONTENTS
SECTION |  |  | Page
1 | DATA ENTRY |  | 1
2 | SELECTIVE CATALYTIC REDUCTION, SCR |  | 2
3 | SELECTIVE NON-CATALYTIC REDUCTION, SNCR |  | 3
4 | HIGH PRESSURE WATER INJECTION, HPWI |  | 4

## tbl (hidden)
Molecular Weight of Various Reagents and NO₂
No. | Component | Molecular Weight
|  | Symbol | lb/mole
1 | 2 | 3 | 4
1 | ammonia | MNH3 | 17.03
2 | urea | Murea | 60.06
3 | NO₂ | MNO2 | 46.01
Various Reagent Aqueous Solutions and Water Selected Properties
No. | Component | Concentration | Density |  | Heat of Vap
|  | c | ρ | ρ | Hv
|  | % by weight | lb/ft³ | lb/gal | Btu/lb
1 | 2 | 3 | 4 | 5 | 6
1 | ammonia 29% | 29 | 56
2 | urea 50% | 50 | 71
3 | urea 10% | 10 |  |  | 900
4 | water | - | 62.4289 | 8.345 | 900
|  |  | 7.481 | gal/ft³
EQUIPMENT BOOK LIFE [1]
No. | Technology | Book Life
Yrs
1 | 2 | 3
1 | Combined cycle | 30
2 | Combustion turbine | 30
3 | Boiler | 40
FUELS
Lower and Higher Heating Values of Selected Fuels
| Fuels | Lower Heating Value (LHV) [1] |  |  | Higher Heating Value (HHV) [1] |  |  | Density |  | Fuel Cost | Comments | Base case Flue Gas Fctr (reclc)
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Gaseous Fuels @ 32 F and 1 atm | Btu/ft3 [2] | Btu/lb [3] | MJ/kg [4] | Btu/ft3 [2] | Btu/lb [3] | MJ/kg [4] | gr/ft3 | grams/cm3 | $/MMBtu |  | CFM/MMBtu/hr
2 | Natural Gas | 983 | 20267.2259 | 47.1413 | 1089 | 22452.705 | 52.2247 | 22 |  | 4.21 |  | 1003.8904
3 | Liquid Fuels | Btu/gal [2] | Btu/lb [3] | MJ/kg [4] | Btu/gal [2] | Btu/lb [3] | MJ/kg [4] | gr/gal
4 | Jet Fuel A (Kerosene K1) |  | 18500 | 43.1 |  | 19861 | 46.2 |  | 0.795 | 23.63 |  | 4177.5829
5 | No. 2 oil | 128450 | 18397.1063 | 42.7914 | 137380 | 19676.0954 | 45.7663 | 3167 | 0.11184 | 24.07 | U.S. conventional diesel | 1466.2111
6 | Ultra low sulfur kerosene oil (ULSD) | 129487.8476 | 18320.1475 | 42.6124 | 138490 | 19593.7864 | 45.5749 | 3206 | 0.11322 | 20.94 | Low-sulfur diesel | 1931.8903
7 | No. 6 Oil | 140352.5222 | 16967.6174 | 39.4664 | 150110 | 18147.2268 | 42.2102 | 3752 |  | 16.95 | Residual oil | 401.1637
8 | Coal |  |  |  |  | 11722.95 |  |  |  | 2.3019 | Bituminous coal (wet basis) [7] | 499.9679
Source:
GREET, The Greenhouse Gases, Regulated Emissions, and Energy Use In Transportation Model, GREET 1.8d.1, developed by Argonne National Laboratory, Argonne, IL, released August 26, 2010.
http://greet.es.anl.gov/
From:
| US DOE - Energy Efficiency & Renewable Energy |  | http://cta.ornl.gov/bedb
| Biomass Energy Data Book |  | http://cta.ornl.gov/bedb/appendix_a.shtml
Notes:
1 | The lower heating value (also known as net calorific value) of a fuel is defined as the amount of heat released by combusting a specified quantity (initially at 25°C) and returning the temperature of the combustion products to 150°C, which assumes the latent heat of vaporization of water in the reaction products is not recovered. The LHV are the useful calorific values in boiler combustion plants and are frequently used in Europe.
The higher heating value (also known as gross calorific value or gross energy) of a fuel is defined as the amount of heat released by a specified quantity (initially at 25°C) once it is combusted and the products have returned to a temperature of 25°C, which takes into account the latent heat of vaporization of water in the combustion products. The HHV are derived only under laboratory conditions, and are frequently used in the US for solid fuels.
2 | Btu = British thermal unit.
3 | The heating values for gaseous fuels in units of Btu/lb are calculated based on the heating values in units of Btu/ft3 and the corresponding fuel density values. The heating values for liquid fuels in units of Btu/lb are calculated based on heating values in units of Btu/gal and the corresponding fuel density values.
4 | The heating values in units of MJ/kg, are converted from the heating values in units of Btu/lb.
5 | For solid fuels, the heating values in units of Btu/lb are converted from the heating values in units of Btu/ton.
6 | Coal characteristics assumed by GREET for electric power production.
7 | Coal characteristics assumed by GREET for hydrogen and Fischer-Tropsch diesel production.

## Data Entry
[16 empty] | Revision: | 00
[16 empty] | Rev. Date: | 2016-08-31
AIR POLLUTION CONTROL COST EFFECTIVENESS ASSESSMENT FOR USE WITH RCSA SECTION 22a-174-22e(h)
[5 empty] | DATA ENTRY |  | EXPLANATION
Line |  | Item Description |  |  |  |  | Symbol | Units | Input / Equation / or Assumed Value |  |  |  | Comments
| I. | Data Required
Note: If an entry is not applicable to the emission unit, leave the entry field blank. All fields marked with an asterisk are required.
Emission Unit ID
1 |  |  |  | Owner/Operator | [7 empty] | * | → User Input - Enter the full legal company / firm name.
2 |  |  |  | Owner/Operator Initials | [8 empty] | → User Input - Enter common short formal name.
3 |  |  |  | Facility Name | [7 empty] | * | → User Input - Enter facility name.
4 |  |  |  | Town | [8 empty] | → User Input - Enter town where the source is located.
5 |  |  |  | DEEP Permit/Registration No. | [8 empty] | → User Input - Enter DEEP Permit/Registration No.
6 |  |  |  | Town Code | [8 empty] | → User Input - Enter town code per DEEP emission unit permit or registration.
7 |  |  |  | Premises No. | [6 empty] | . |  | → User Input - Enter premises no. per DEEP emission unit permit or registration.
8 |  |  |  | Facility Altitude |  |  | h | ft |  | * |  |  | → User Input - Enter altitude with respect to sea level. If elevation is not known and is estimated to be less than 500 ft, assume sea level ''0'' ft.
9 |  |  |  | Unit Tag | [5 empty] | * |  |  | → User Input-Enter DEEP permit or registration tag,if any. If none,assign an ID tag.
10 |  |  |  | Unit Type | [7 empty] | * | → Select from the dropdown list: Combined Cycle Turbine, Combustion Turbine, Engine or Boiler.
11 |  |  |  | No identical Units w/ same controls | [8 empty] | → User Input - Enter number of identical units at the same location with the same type of air pollution control. Note: Control Cost Effectiveness assessment performed for a single emission unit.
12 |  |  |  | Type of Combustion (for boilers only) | [8 empty] | → User Input - Entry refers to a boiler's type of combustion, whether the boiler is a Fluidized Bed (FB) or not (non-FB). If the unit on Line No. 10 is other than a "boiler", the field on Line 12 should be left blank.
Air Pollution Control(s) Selected
13 |  |  |  | Selective Catalytic Reduction - SCR | [5 empty] | * |  |  | → Select the control(s) to be assessed by choosing ''Yes'' or ''No'' from the corresponding adjacent drop down list.
14 |  |  |  | Selective Noncatalytic Reduction - SNCR | [5 empty] | *
15 |  |  |  | High Pressure Water Injection - HPWI | [5 empty] | *
Performance Data
16 |  |  |  | Maximum Heat Rate Input |  |  | QB | MMBtu/hr |  | * |  |  | → User Input - Enter value if the emission unit is a combined cycle turbine or a boiler. If not, it may be left blank. Note: Use as entry data ''Nominal Heat Input Capacity'', if available.
17 |  |  |  | Power Output (MW Rating) at full load capacity. |  |  | BMW | MW |  | * |  |  | → User Input - It may be left blank for combined cycle turbines and boilers if ''Nominal Heat Input'' has been entered on Line No. 16. For all other emission units enter ''Nominal Plate MW Capacity''.
18 |  |  |  | Net Plant Heat Rate, or Nominal Plate Heat Rate |  |  | NPHR | MMBtu/MWh |  | * |  |  | → User Input - Data provided by the emission unit's manufacturer as "Nominal Heat Rate". If not known it can be assessed from EPA's AMPD data.
Fuel
19 |  |  |  | Fuel (Primary) | [7 empty] | * | → User Select from the drop down list.
Special Note (for emission units burning coal, only): Connecticut has only one emission unit that burns coal and that unit burns a mix of bituminous and sub-bituminous coal. The calculation for coal is designed to address that unit's coal inputs. For other coal types, this calculator may require adjustment.
20 |  |  |  | Fuel Sulfur Content |  |  |  | % by weight |  | * |  |  | → User Input - Enter "0" if fuel sulfur content is less than 1%.
21 |  |  |  | SO₂ Content of Fuel |  |  |  | lb/MMBtu |  | * |  |  | → User Input - Enter "0" for coals with SO₂ ≤ 3 lb/MMBtu and also "0" if fuel is other than coal.
22 |  |  |  | Percent Fuel Ash Weight |  |  | % FAW | % by weight |  | * |  |  | → User Input - Enter ''0'' for all fuels other than coal. For coal enter known value or 7.5% (default).
Exhaust Flow
23 |  |  |  | Most Recent Stack Test Date | [8 empty] | → User Input - Enter the most recent stack test date.
24 |  |  |  | Stack Temperature |  |  | Tout | ºF |  | * |  |  | → User Input - Enter data from the latest stack test. If not available, use DEEP Emissions Inventory (EMIT) Data.
25 |  |  |  | Exhaust Flow at Max. Capacity |  |  |  | ACFM |  | *
NOx Removal Specifications
26 |  |  |  | Uncontrolled NOx Emission Level |  |  | NOxin | lb/MMBtu |  | * |  |  | → User Input - From the stack test or from EPA's AMPD data (max. value of the last five years).
27 |  |  |  | Required Annual Average Controlled NOx Emission Level |  |  | NOxout | lb/MMBtu |  | * |  |  | → User Input - Enter NOx limit as required by RCSA 22a-174-22e.
Cost Adjustment
28 |  |  |  | Year Control is Effective (or Current Year) |  |  |  | $year | "2016$"-Default | * |  |  | → User Input - Year posted may be adjusted to a future year. Corresponding CPI may be projected, if is not available on the U.S. Department of Labor website, see Ref. 6., below.
29 |  |  |  | Consumer Price Index (CPI Multiplier) |  |  | CPI("2016$"-Default$) |  | "1.04" - Default | *
Retrofit Factors
30 |  |  |  | Selective Catalytic Reduction |  |  | RFSCR |  | "1.00" - Default | * |  |  | → User Input - Per Ref. 1, §1.4.1-Total Capital Investment, p1-44 (p44-pdf) and Ref. 2, §2.4-Cost Analysis, p2-63(p64-pdf), EPA suggests a retrofit factor for SCR and SNCR systems, between 0.8 and 1.5 (value provided in the excel spreadsheets attached to the documents). A "RF=1", is recommended for projects of average retrofit difficulty. Any retrofit factor greater than "1" must be documented with a justification. A value less than 1 denotes a new construction. A retrofit factor has been applied to HPWI systems, too.
31 |  |  |  | Selective Noncatalytic Reduction |  |  | RFSNCR |  | "1.00" - Default | *
32 |  |  |  | High Pressure Water Injection System |  |  | RFHPWI |  | "1.00" - Default | *
| II. | General Assumptions
[11 empty] | References: | 1 | EPA Air Pollution Control Cost Manual - Seventh Edition, Section 4 - NOx Controls: Chapter 1 - Selective Noncatalytic Reduction, May 2016.
[12 empty] | 2 | EPA Air Pollution Control Cost Manual - Seventh Edition, Section 4 - NOx Controls: Chapter 2 - Selective Catalytic Reduction, May 2016.
[12 empty] | 3 | EPA’s Power Sector Modeling - Integrated Planning Model (IPM) Platform v.5.13, Chapter 8: Financial Assumptions.
[12 empty] | 4 | EPA Air Pollution Control Cost Manual - Sixth Edition (EPA 452/B-02-001), January 2002.
[12 empty] | 5 | Alternative Control Techniques Document - NOx Emissions from Stationary Gas Turbines - EPA ACT Document No.: EPA-453/R-93-007.
[12 empty] | 6 | U.S Department of Labor - Bureau of Labor Statistics: CPI Inflation Calculator.
[9 empty] | Column 1. |  | Column 2.
|  |  | Operation Data | [5 empty] | Default Operation |  | Limited Operation
33 |  |  |  | Emission Unit Annual Hrs of Operation |  |  | top, ems unit | hrs / yr | "8,760" - Default |  |  |  | → User Input on "Limited Operation" column, only. Default operation time for RACT determination is 8,760 hrs. If the emission unit is subject to an enforceable limit on hours of operation, enter the enforceable limit (in hrs).
34 |  |  |  | Air Pollution Control Annual Hrs of Operation |  |  | top, control | hrs/yr | equal to Line 33, Col.1 |  | equal to Line 33, Col.2 |  | The air pollution control is assumed to operate at all times the emission unit is operating. Therefore, the control and emission unit hrs of operation are equal.
35 |  |  |  | Emission Unit Total Operating Time |  |  | tems unit | days/yr | Line 33, Col.1 ∕ 24 hrs/day |  | Line 33, Col.2 ∕ 24 hrs/day |  | Emission unit "Default Operation" and "Limited Operation" time, in days. Data entries on Line 33 divided by 24 hrs/day.
36 |  |  |  | Emission Control Total Operating Time |  |  | tcontrol | days/yr | Line 34, Col.1 ∕ 24 hrs/day |  | Line 34, Col.2 ∕ 24 hrs/day |  | See line 35 comment.
| III. | Economic Factors, Specific Costs and other Specifications | [6 empty] | Note:
Economic Factors and all Specifications listed below apply for both Default Operation and Limited Operation cost effectiveness calculations.
Economic Factors
37 |  |  |  | Cost Year base |  |  |  | $year | "2012$' - Default |  |  |  | Per Ref. 1, § 1.4 Cost Analysis, page 1-43 (p43-pdf) & § 1.5-Ex. Problem, page 1-58 (p58-pdf) and Ref. 2, § 2.4 Cost Analysis, page 2-62 (p63-pdf) & § 2.5 - Ex. Problem, page 2-80 (p81-pdf).
38 |  |  |  | Annual Interest Rate |  |  | i | % | '7%'' - Default |  |  |  | Per Ref. 1, § 1.5-Ex. Problem, p1-58 (p58-pdf) and Ref. 2, § 2.5-Ex. Problem, page 2-80 (p81-pdf).
39 |  |  |  | Equipment Life |  |  | n | years | Auto Input from Ref. 3, Table 8-4 |  |  |  | Per Ref. 3, Chapter 8, Table 8-4, page 8-14 (p9-pdf):
Power Sector Modeling Platform v.5.13 Documentation - Chapter 8: Financial Assumptions.
For the emission units listed in the dropdown list at Line 10, the following book life values have been selected:
[13 empty] | Combined Cycle | 30 | yrs
[13 empty] | Combustion Turbine | 30 | yrs
[13 empty] | Engine | 30 | yrs
[13 empty] | Bolier | 40 | yrs
40 |  |  |  | Capital Recovery Factor |  |  | CRF |  | i (1+ i)n/(1+ i)n - 1 |  |  |  | Calculated per Ref. 1, § 1.4.2 Total Annual Cost, eq. (1.55), p1-57 (p57-pdf) and Ref. 2, § 2.4.2 Total Annual Cost, Capital Recovery, eq. (2.71), p2-79 (p80-pdf).
|  |  | Utilities Specific Costs | [5 empty] | Note:
User has the option to enter the actual values, instead of the default values.
41 |  |  |  | Electrical Power Cost |  |  |  | $/kWh | '0.067''-Default | * | default or actual value |  | Enter actual value or EPA's value of 0.067 $/kWh, per Ref.1, §1.5-Ex. Problem, page 1-58 (p58,pdf).
42 |  |  |  | Water Consumption Cost |  |  |  | $/gal | '0.0065''-Default | * | default or actual value |  | Enter actual value or EPA's value of 0.0065 $/gal, per Ref. 1, § 1.5-Ex. Problem, page1-58 (p58-pdf).
Reagent Costs
43 |  |  |  | 29% Ammonia Solution Cost |  |  |  | $/lb | '0.475'' - Default |  |  |  | Per Ref. 2, § 2.5 - Ex. Problem, page 2-80 (p81-pdf).
44 |  |  |  | 50% Urea Solution Cost |  |  |  | $/lb | "1.620" - Default |  |  |  | Per Ref. 1, § 1.5 - Ex. Problem, page1-58 (p58-pdf).
Labor Costs
45 |  |  |  | Labor Rate |  |  | LR | $/hr | "$60/hr" -Default |  |  |  | The suggested rate is the operator labor cost, including benefits, per Ref. 2, § 2.5 & 2.6 - Example Problem(s) 1 and 2, page 2-80 (p81-pdf) and page 2-88 (p89-pdf).
Other Specifications
46 |  |  |  | NOx properties are provided as |  |  |  |  | "NO₂" - Default |  |  |  | Per Ref. 1, §1.3.1 - Design parameters for Study-Level Estimates, Uncontrolled NOx and Stack NOx, p1-36 (p36-pdf), and Ref. 2, § 2.3.4 - Inlet NOx and Stack NOx, page 2-54 (p55-pdf).
47 |  |  |  | NO₂ Molecular Weight |  |  | MWNO2 | lb/mole | "46.01" - Default |  |  |  | Provided in eq. (1.18), Ref. 1, §1.3.1-Design parameters for Study-Level Estimates, Estimating Reagent Consumption and Tank Size, p1-41 (p41-pdf), and in eq. (2.35), Ref. 2, §2.3.13 - Estimating Reagent Consumption and Tank Size, p2-61 (p62-pdf).

## SCR
[15 empty] | Revision: | 00
[15 empty] | Rev. Date: | 2016-08-31
AIR POLLUTION CONTROL COST EFFECTIVENESS ASSESSMENT FOR USE WITH RCSA SECTION 22a-174-22e(h) EXPLANATION
[11 empty] | References: | 1 | EPA Air Pollution Control Cost Manual - Seventh Edition, Section 4 - NOx Controls: Chapter 2 - Selective Catalytic Reduction, May 2016.
[6 empty] | SELECTIVE CATALYTIC REDUCTION - SCR | [5 empty] | 2 | EPA Air Pollution Control Cost Manual - Sixth Edition (EPA 452/B-02-001), January 2002.
[12 empty] | 3 | Alternative Control Techniques Document - NOx Emissions from Stationary Gas Turbines - EPA ACT Document No.: EPA-453/R-93-007.
[12 empty] | 4 | U.S Department of Labor - Bureau of Labor Statistics: CPI Inflation Calculator.
Line |  | Item Description |  |  |  |  | Symbol | Units |  | Input Source / Equation / or Default Value |  |  | Comments
[10 empty] | Column 1. | Column 2.
[10 empty] | Default Operation | Limited Operation
SCR ASSUMPTIONS
| I. | Air Pollution Control Assumptions
Control Unit Specifications
1 |  |  |  | Control Type | [5 empty] | "SCR" | "SCR" |  | Line 1, Col. 1, will display "SCR", and control's cost effectiveness calculation down the column, only if on Data Entry: select "Yes" on Line 13, fuel on Line 19, enter NOxin on Line 26 and NOxout on Line 27.
To show calculations on ''Limited Operation'' column (2), enter the no. of hours on Data Entry Line 33, Column 2, otherwise the entire column is blank.
2 |  |  |  | Number of SCRs per Combustion Unit |  |  | NSCR |  |  | "1" SCR per emission unit - Default |  |  | Selected SCR design criteria: one SCR system per emission unit
3 |  |  |  | SCR Operating Time |  |  | top, control | hrs |  | Data Entry Line 34, Col. 1. | Data Entry Line 34, Col. 2. |  | Air Pollution Control Annual Hrs of Operation, as entered on Data Entry, Line 34. The SCR is assumed to operate at all times the emission unit is operating.
Note:
All calculations displayed below, in both "Default Operation" and "Limited Operation" columns are using same default values and/or same equations for various intermediate parameters, factors or cost elements, to assess the cost effectiveness of the control. The calculations include control unit sizing, reagent requirements to attain the specified NOx reduction, and cost estimates of procurement, installation and operation of the equipment.
4 |  |  |  | SCR Configuration | [5 empty] | "High Dust" - Default |  |  | Configuration, selected as default, is the configuration of the majority of SCR's (88%) reported in 1997, per Ref. 1, § 2.2.3 - SCR System Configurations, page 2-29 (p30-pdf).
5 |  |  |  | SCR Temperature Inlet (Default) |  |  | Tin | ºF |  | "700 ºF" - Default |  |  | Selected default value of SCR Temperature Inlet.
6 |  |  |  | SCR Removal Efficiency at selected Tin |  |  | h NOxR | % |  | "90%" - Default |  |  | SCR Efficiency at 700ºF, per Ref. 1, Fig. 2.2 - NOx Removal vs. Temperature, page 2-17 (p18-pdf). Selected efficiency is adjusted if the calculated NOxout value falls below the SCR attainable limit.
7 |  |  |  | SCR Lowest Attained NOxout Rate |  |  | NOxout,min | lb/MMBtu |  | "0.040 lb/MMBtu" - Default |  |  | Lowest achievable value suggested in EPA's Clean Air Markets Division (CAMD) database, per Ref. 1, § 2.1- Introduction, footnote #2, page 2-2 (p3-pdf).
Catalyst Design Specifications
8 |  |  |  | Min. Number of Layers | [5 empty] | Min. "2" - Default |  |  | Min. two layers required, per Ref. 1, § 2.3.12 - SCR Reactor Dimensions, p2-60 (p61 pdf).
9 |  |  |  | Catalyst Layers Ratio |  |  | Full/Empty |  |  | 2 full, 1 empty - Default |  |  | Two full, one empty layer ratio, per Ref. 2, §2.5 Ex. Problem, p2-50 (p.54-pdf).
Flue Gas Superficial Velocity
10 |  |  |  |  | Recommended |  | vsuperficial | ft/sec |  | "16 ft/sec" - Default |  |  | Typical flue gas face velocity, per Ref. 1, § 2.3.12-SCR Reactor Dimensions, page 2-59 (p60-pdf).
11 |  |  |  |  | Selected |  | vsuperficial | ft/sec |  | SCR page Line 10 |  |  | Line 10 value. Selected value may be changed if the resulting catalyst height is out of range. Field allows a new entry value, if necessary.
12 |  |  |  | Aspect Ratio Cross-sectional Area |  |  | l / w |  |  | l / w = 1.0 - Default |  |  | Cross-sectional area assumed square, length (l) = width (w), hence l / w = 1. Industry standard aspect ratios are between 1.0 - 1.5, per Ref. 1, § 2.3.12 - SCR Reactor Dim's., p2-59 (p60 pdf).
13 |  |  |  | Catalyst Layer's Height Range |  |  | hlayer | ft |  | "2.5 - 5.0" - Default Range |  |  | Standard industry range, per Ref.1, § 2.3.12-SCR Reactor Dim's, p2-60(p61-pdf).
14 |  |  |  | Nominal Height of Catalyst Layer |  |  | h´layer | ft |  | "3.1 ft" - Default |  |  | Nom.height, per Ref.1, § 2.3.12-SCR Reactor Dim's, footnote #23, p2-60(p61 pdf).
Catalyst Additional Height Clearance
15 |  |  |  |  | Catalyst Layer Clearance |  | c1 | ft |  | "7 ft" - Default |  |  | Both c1 and c2 clearances are based on common industry practice, per Ref. 1, § 2.3.12 - SCR Reactor Dimensions, page 2-61 (p62 pdf).
16 |  |  |  |  | SCR Module Clearance |  | c2 | ft |  | "9 ft" - Default
17 |  |  |  | Pressure Drop for SCR Ductwork |  |  | ΔPduct | in w.g |  | "3 inches w.g." - Default |  |  | Typical pressure drop values, per Ref. 1, § 2.5 & 2.6 - Example Problem(s) 1 and 2, page 2-80 (p81 pdf) and respectively page 2-87 (p88-pdf).
18 |  |  |  | Pressure Drop for each Catalyst Layer |  |  | ΔPcatalyst | in w.g |  | "1 inch w.g." - Default
| II. | Reagent Specifications
Reagent Data
19 |  |  |  | Reagent type | [5 empty] | "ammonia" - Default |  |  | Selected design criteria per Ref.1, §2.2.1-Reduction Chemistry, p2-12 (p13-pdf).
20 |  |  |  | Reagent Molecular Weight |  |  | MWR | lb/mole |  | "17.03" (as NH₃) - Default |  |  | Ammonia Molecular Weight, per Ref. 1, Table 2.2, page 2-13 (p14-pdf).
21 |  |  |  | Acceptable Ammonia Slip |  |  | Slip | ppm |  | "2.0 ppm" - Default |  |  | Acceptable levels of 2-3 ppm, per Ref. 1, Ammonia Slip, page 2-21 (p22-pdf).
22 |  |  |  | Stoichiometric Ratio Factor |  |  | SRF | moles reagent / moles NOx |  | moles reagent /moles NOx removed = 1.05 moles of NH₃ / 1 mole of NOx - Default |  |  | Defined by eq. (2.13) per Ref. 1, §2.3.7- Stoichiometric Ratio Factor, p2-55 (p56-pdf). Typically SCR systems employ 1.05 moles of ammonia to one mole of NOx.
Storage
23 |  |  |  | Stored Ammonia Solution Concentration |  |  | Csol | % by weight |  | "29.4%" - Default |  |  | Typical SCR ammonia concentration, per Ref.1, §2.2.1 - Reduction Chemistry, page 2-12 (p13-pdf).
24 |  |  |  | Ammonia 29.4% Solution Density |  |  | ρsol | lb/ft³ |  | "56.0 lb/ft³" - Default |  |  | Per Ref. 1, § 2.3.12 - SCR Reactor Dim's, page 2-62 (p63 pdf).
25 |  |  |  | No. Storage Days |  |  | tstorage | days |  | "14 days" - Default |  |  | Common onsite storage requirement, per Ref. 1, § 2.3.12 - SCR Reactor Dim's, page 2-62 (p63-pdf).
| III. | Specific Economic Factors
SCR Costs Factors
Catalyst Cost
26 |  |  |  |  | Catalyst Cost,dollars per cubic feet |  | CCreplace, IP | $/ft³ |  | "$160/ft³"- Default |  |  | Per Ref.1, § 2.5 & 2.6 - Ex. Problem(s) 1 and 2, p2-80(p81 pdf) & p2-88(p89-pdf).
27 |  |  |  |  | Catalyst Cost,dollars per cubic meter |  | CCreplace, SI | $/m³ |  | [$/m³] ≈ [$/ft³] x [35.3 ft³ / m³] |  |  | $5,500 $/m³ is equivalent to 160$/ft³. Changing the units, results ~156$/ft³.
28 |  |  |  | Operating Life of Catalyst |  |  | CLife | hrs |  | "24,000 hrs" if coal - Default "32,000 hrs" if oil or nat gas - Default |  |  | Vendor data, per Ref. 1, §2.2.1 - Reduction Chemistry, page 2-14 (p15-pdf).
Labor Costs
29 |  |  |  | Number of hours of operator labor |  |  | top, labor | hrs/day |  | "4.00" - Default |  |  | Per Ref.1, § 2.5 & 2.6 - Ex. Problem(s) 1 & 2, p2-80 (p81 pdf) & p2-88 (p89-pdf).
30 |  |  |  | Labor Rate |  |  | LR | $/hr |  | Data Entry, Line 45 |  |  | EPA suggested "Labor Rate" listed on Data Entry page, Line 45.
Capital Cost Elevation Factor
31 |  |  |  | Elevation Factor |  |  | ELEVF |  |  | 14.7 psia / {2116 x (1/144) x x [(59-(0.00356xh)+459.7)/518.6]5.256} |  |  | Calculated per eq's. (2.39a) & (2.39b), Ref. 1, §2.4.1 - Total Capital Investment, pages 2-64 & 2-65 (p65/66-pdf).
SCR SIZING
| I. | Emission Unit Performance Data at 8760 hrs
Emission Unit Data
32 |  |  |  | Unit Type | [5 empty] | Data Entry, Line 10. |  |  | Emission unit type selected on Data Entry page Line 10.
33 |  |  |  | Maximum Heat Rate Input |  |  | QB | MMBtu/hr |  | Data Entry, Line 16, or calculated as: QB = NPHR x BMW |  |  | Input from Data Entry, Line 16, if emission unit is a Combined Cycle or a Boiler with a known Heat Input, otherwise it is calculated as: [Heat Input, QB = NPHR x BMW].
34 |  |  |  | Nominal Plate Power Capacity |  |  | BMW | MW |  | Data Entry, Line 17, or calculated as: BMW = QB / NPHR |  |  | Input from Data Entry, Line 17, if emission unit is a Combustion Turbine, Engine, or a Boiler with a known MW output, otherwise is calculated as: [BMW = QB / NPHR].
35 |  |  |  | Heat Rate (Nom Plate Heat Rate) |  |  | NPHR | MMBtu/MWh |  | Data Entry, Line 18. |  |  | Emission unit Heat Rate listed on Data Entry, Line 18. Note: Heat Rate listed value should be equal to the ratio of the selected QB and BMW values.
36 |  |  |  | Heat Rate Factor |  |  | HRF |  |  | NPHR / 10 MMBtu/MWh |  |  | Defined by eq. (2.6), Ref. 1, §2.3.2- Heat Rate Factor, page 2-52 (p53-pdf), as the ratio of actual NPHR to a typical heat rate of 10 MMBtu/MWh used in developing capital cost equations.
37 |  |  |  | Annual Hrs of Operation |  |  | top, ems unit | hrs |  | Data Entry Line 33, Col. 1. | Data Entry Line 33, Col. 2. |  | Data Entry - Emission Unit Annual Hrs of Operation, Line 33, Columns 1 & 2. The air pollution control is assumed to operate at all times the emission unit is operating.
38 |  |  |  | Heat Input Max Annual |  |  | HI | MMBtu/yr |  | BMW x NPHR x top,ems unit, or QB x top,ems unit |  |  | Calculated based on BMW, NPHR and emission unit operating time, top,ems unit or QB multiplied by top,ems unit.
39 |  |  |  | Annual Actual MW Output |  |  | Boutput | MW/yr |  | BMW x top,ems unit |  |  | Power Output, BMW, (Line 34) multiplied by the emission unit Annual Hrs. of Operation, top, ems unit (Line 37).
Operating Capacity Factors
40 |  |  |  | Emission Unit Capacity Factor |  |  | CF ems unit |  |  | Boutput / (BMW x 8,760 hrs) |  |  | Per Ref. 1, §2.3.3-System Capacity Factor, eq. (2.8a), p2-53 (p54-pdf). Since max. MW output is selected, eq. (2.8a) is also equivalent with the selected hrs of operation divided by 8,760 hrs.
41 |  |  |  | SCR Capacity Factor |  |  | CF SCR |  |  | top, control / top, ems unit |  |  | Defined by eq. (2.9), Ref. 1, §2.3.3-System Capacity Factor, p2-53 (p54-pdf).
42 |  |  |  | Total System Capacity Factor |  |  | CF Total |  |  | CFems unit x CF SCR |  |  | Defined by eq. (2.7), Ref. 1, §2.3.3-System Capacity Factor, p2-53 (p54-pdf).
Fuel Data
43 |  |  |  | Fuel Type | [5 empty] | Data Entry, Line 19. |  |  | Emission unit fuel type selected on Data Entry, Line 19. Note: Since Connecticut has only one coal-fired emission unit that burns a mix of bituminous and sub-bituminous coal only, all specifications of this calculation for emission units burning coal are selected for bituminous coal.
44 |  |  |  | Air Heater Factor |  |  | AHF |  |  | AHF = 1, if bituminous coal and SO₂> 3lb/MMBtu - Default AHF = 0, if not true, - Default |  |  | Defined in Eq. (2.43), Ref 1, §2.4.1.1 - Utility Boilers, page 2-67 (p68-pdf), as multiplier for Air Pre-Heater Cost. AHF=1, if bituminous coal and SO2> 3lb/MMBtu, =0 if not true. Note: Since Connecticut has only one coal-fired emission unit that burns a mix of bituminous and sub-bituminous coal, AHF is "0", and the air pre-heater term drops out of the overall TCI equation for SCR system, for all CT emission units.
45 |  |  |  | Fuel Factor/Coal factor (if fuel is "Coal") |  |  | FuelF / CoalF (if fuel is "Coal") |  |  | CoalF = 1 - for bituminous coal - Default FuelF = 1 - for lq and gas fuels - Default |  |  | Defined in Eq's. (2.41), (2.43) and (2.44), Ref 1, §2.4.1.1 - Utility Boilers, p2-66 (p67-pdf) & p2-67 (p68-pdf), as "CoalF" multiplier for coal units costs. In eq. (2.60) Ref 1, §2.4.2.-Total Annual Costs, p2-74 (p75-pdf), CoalF is replaced with a (Fuel) factor equal to 1, for oil- and gas fired emission units. CoalF (or FuelF) multiplier applied to CT units is = 1.
46 |  |  |  | Fuel High Heating Value |  |  | HHV | Btu/lb |  | Auto Input from U.S. DOE reference. |  |  | Per US DOE Biomass Energy Databook: | http://cta.ornl.gov/bedb/appendix_a.shtml
Btu/ft³ (for gas)
47 |  |  |  | Max. Fuel Consumption Rate |  |  | m(fuel) | lb/hr |  | (HI x 106/ HHV) / top,ems unit or QB x 106 / HHV |  |  | Calculated as hourly heat input (Line 38 divided by Line 37), and divided by the fuel HHV (Line 46), or Maximum Heat Rate Input (QB) on Line 33, divided by fuel HHV - Line 46.
[7 empty] | V(fuel) | CFH - for gas
48 |  |  |  | Annual Fuel Consumption (estimate based on selected HHV) |  |  | Annual Fuel | lb/yr |  | m (fuel) x top,ems unit |  |  | Fuel consumption rate (Line 47) multiplied by the total annual hours of operation, (Line 37).
[8 empty] | CF/yr - for gas |  | V (fuel) x top,ems unit
Exhaust Flow Specifications
49 |  |  |  | Exhaust Flow Temp Correction Factor |  |  | F(Tin) | ºF |  | (459.67+700ᵒF)/(459.67+T out), where T out = Data Entry, Line 24 |  |  | Adjustment factor to determine exhaust flow rate at temperatures other than 700ᵒF (SCR default Tin), based on physics Charles' Law (V/T = constant).
50 |  |  |  | Flue Gas Flow Rate (selected) |  |  | q flue gas | CFM |  | F(Tin) x Exhaust Flow at Max.Capacity, listed in Data Entry, Line 25. |  |  | Flue Gas Flow provided on Data Entry, Line 25, corrected for 700ᵒF.
51 |  |  |  | Base case Flue Gas Volumetric Flow Rate Factor(calculated) |  |  | q fuel | CFM/MMBtu/hr |  | q flue gas / QB |  |  | Defined in eq. (2.14), Ref. 1, §2.3.8 - Flue Gas Flow Rate, page 2-56 (p57-pdf). Calculated as Flue Gas Flow Rate divided by Max. Heat Rate Input, QB. Factor is determined for comparison with EPA data (see Ref. 1, p2-56). Note: If the calculated base case factor is too different from EPA data, then the flue flow rate entry (Data Entry, Line 25) ought to be revised.
NOx Removal Performance
52 |  |  |  | Uncontrolled NOx Emission Level |  |  | NOxin | lb/MMBtu |  | Data Entry, Line 26. |  |  | Uncontrolled NOx rate entered on Data Entry page, Line 26.
53 |  |  |  | Controlled NOx Outlet (required rate) |  |  | NOxout | lb/MMBtu |  | Data Entry, Line 27. |  |  | Controlled NOx rate, as required by RCSA 22a-174-22e, and listed on Data Entry, Line 27.
54 |  |  |  | Controlled NOx Outlet (selected) |  |  | NOxout,sel | lb/MMBtu |  | MAX(NOxout, NOxmin, NOxin - hNOxR x NOxin) |  |  | Determined as the highest among: the required controlled NOxout, the SCR lowest attained NOxout rate, or the NOxout value based on the 90% default efficiency.
55 |  |  |  | NOx Removal Efficiency (selected) |  |  | h NOxR,sel | % |  | (NOxin - NOx out sel)/NOxin x 100% |  |  | Defined by eq. (2.10) Ref. 1, § 2.3.5 - NOx Removal Efficiency, p2-54 (p55-pdf) and calculated based on NOxin on Line 52 and the value of NOxout sel, on Line 54.
56 |  |  |  | NOx Removal Factor |  |  | NRF |  |  | η NOxR,selected / 80 |  |  | For use with eq. (2.41) to calculate SCR cost, per Ref. 1, §2.4.1.1-Utility Boilers, page 2-66 (p67-pdf).
57 |  |  |  | NOx Removed Hourly Rate |  |  | NOxR/hr | lb/hr |  | NOxin x ηNOxR,sel x QB |  |  | Defined by eq. (2.12), Ref. 1, §2.3.6 - NOx Removal Rates, page 2-55 (p56-pdf).
58 |  |  |  | NOx Removed / yr |  |  | NOxR | tons |  | NOxin x hNOxR,sel x QB x top, control / 2000, or NOxin x hNOxR,sel x QB x CFTotal x8760/2000 |  |  | Defined by eq. (2.11), Ref. 1, §2.3.6 - NOx Removal Rates, page 2-54 (p55-pdf).
| II. | SCR Reactor Calculations
Catalyst Volume
59 |  |  |  | NOx Efficiency Adjustment Factor |  |  | hadj |  |  | 0.2869 + 1.058 x h NOxR,sel |  |  | Factor in eq. (2.22), and defined by eq. (2.23), Ref. 1, §2.3.11 - Catalyst Volume, page 2-58 (p59-pdf).
60 |  |  |  | Ammonia Slip Adjustment Factor |  |  | Slipadj |  |  | 1.2835 - 0.0567 x Slip |  |  | Factor in eq.(2.22), and defined by eq.(2.24), Ref. 1, §2.3.11 - Catalyst Volume, page 2-58 (p59-pdf).
61 |  |  |  | NOx adjustment factor for inlet NOx |  |  | NOxadj |  |  | 0.8524 + 0.3208 x NOxin |  |  | Factor in eq. (2.22), and defined by eq. (2.25), Ref. 1, §2.3.11 - Catalyst Volume, page 2-58 (p59-pdf).
62 |  |  |  | Sulfur in Coal Adjustment Factor |  |  | Sadj |  |  | 0.9636 + 0.0455 x Fuel Sulfur Content x 100 |  |  | Factor in eq. (2.22), and defined by eq. (2.26), Ref. 1, §2.3.11 - Catalyst Volume, page 2-58 (p59-pdf).
63 |  |  |  | Temperature Adjustment Factor |  |  | Tadj |  |  | If Tin = 700ºF → Tadj = 1, If Tin ≠ 700ºF → Tadj = 15.16-0.03937 xTin +0.0000274 xTin² |  |  | Factor in eq. (2.22), and defined by eq. (2.27), Ref. 1 §2.3.11 - Catalyst Volume, page 2-59 (p60-pdf).
64 |  |  |  | Volume estimate of the catalyst |  |  | Volcatalyst,estm | ft³ |  | 2.81 x QB x hadj x Slipadj x NOxadj x Sadj x (Tadj / NSCR) |  |  | Defined by empirical eq. (2.22), per Ref. 1, §2.3.11 - Catalyst Volume, page 2-58 (p59-pdf).
Configuration & Dimensions
65 |  |  |  | Catalyst Cross-sectional Area |  |  | Acatalyst | ft² |  | qflue gas /(vsuperficial, sel x 60 sec/min) |  |  | Defined by eq. (2.28), per Ref. 1 §2.3.12 - SCR Reactor Dim's, p2-59 (p60-pdf).
66 |  |  |  | SCR Cross-sectional Area |  |  | ASCR | ft² |  | 1.15 x Acatalyst |  |  | Per eq. (2.29), Ref. 1 §2.3.12 - SCR Reactor Dim's, page 2-59 (p60-pdf). ASCR > Acatalyst by 15% to account for module geometry and hardware.
67 |  |  |  | Reactor Length (l) & Width (w) |  |  | l=w | ft |  | l = w = (ASCR)1/2 |  |  | Square root of Catalyst Cross-Sectional Area. Area aspect ratio is l / w = 1.0 - Default. Per Ref. 1, §2.3.12 - SCR Reactor Dim's, eq (2.30), page 2-59 (p60-pdf).
No. of Catalyst layers
68 |  |  |  |  | Required |  | nlayer req. |  |  | Volcatalyst,estm / (h´layer x Acatalyst) |  |  | Defined by eq. (2.31), per Ref. 1, §2.3.12 - SCR Reactor Dim's, p2-60 (p61-pdf).
69 |  |  |  |  | Selected |  | nlayer, sel |  |  | Value on Line 68, (Min. 2, if nlayer req.< 2) |  |  | Data on Line 68, above. Note: Min. number of layers selected should be two, if the above result is less than two.
70 |  |  |  | No. of additional empty layers |  |  | nlayer empty |  |  | nlayer, sel / 2 |  |  | Selected based on the criteria, on Line 9, above: "Two full, one empty layer".
Height of catalyst layer
71 |  |  |  |  | hlayer (calculated) |  | hlayer(clc) | ft |  | Volcatalyst,estm/(nlayer,sel x Acatalyst) + 1 |  |  | Defined by eq. (2.32), per Ref. 1 §2.3.12 - SCR Reactor Dim's, p2-60 (p61-pdf).
72 |  |  |  |  | hlayer (selected) |  | hlayer, sel | ft |  | If hlayer (clc) < 2.5ft → Select 2.5 ft If hlayer (clc) > 5.0ft → Re-calculate |  |  | Height of catalyst layer, hlayer,sel should be within standard industry range, between 2.5 - 5.0 ft. If the result is larger than 5.0 ft, select a new superficial (face) velocity, on Line 11 to re-calculate Volcatalyst and hlayer.
73 |  |  |  | Volcatalyst (re)calculated |  |  | Volcatalyst,(clc) | ft³ |  | nlayer,sel x Acatalyst x (hlayer,sel - 1) |  |  | Volume catalyst (re)calculated using, the selected height, on Line 70.
74 |  |  |  | ntotal (incl. empty layers) |  |  | ntotal |  |  | nlayer, sel + nlayer empty |  |  | Eq. (2.33), per Ref. 1 §2.3.12 - SCR Reactor Dim's, page 2-60 (p61-pdf).
75 |  |  |  | SCR height |  |  | hSCR | ft |  | nTotal (c1 + hlayer, sel) +c2 |  |  | Eq. (2.34), per Ref. 1 §2.3.12 - SCR Reactor Dim's, page 2-61 (p62-pdf).
| III. | Reagent Calculations
Flow Rates
76 |  |  |  | Ammonia Consumption |  |  | ṁreagent | lb/hr |  | (NOxin x QB x hNOxR,sel x SFR x Mreagent) /MNOx |  |  | Eq. (2.35), Ref. 1, §2.3.13 - Estimating Reagent Consumption and Tank Size, p2-61 (p62-pdf).
Ammonia 29% Solution
77 |  |  |  |  | Mass Flow Rate |  | ṁsol | lb/hr |  | ṁreagent / Csol |  |  | Eq. (2.36), Ref. 1, §2.3.13 - Estimating Reagent Consumption and Tank Size, p2-61 (p62-pdf).
78 |  |  |  |  | Volumetric Flow Rate |  | qsol | gph |  | ṁsol / ρsol x 7.4805 |  |  | Eq. (2.37), Ref. 1, §2.3.13 - Estimating Reagent Consumption and Tank Size, p2-62 (p63-pdf). Note: 7.4805 - conversion factor of 7.4805 gal/1 ft³.
Storage
79 |  |  |  | Storage Tank Volume |  |  | Voltank | gal |  | qsol x tstorage x 24 hrs/day |  |  | Eq. (2.38), Ref. 1, §2.3.13 - Estimating Reagent Consumption and Tank Size, p2-62 (p63-pdf).
| IV. | Utilities
80 |  |  |  | Power Consumption |  |  | P | kW |  | BMW x (1000)x(0.0056)x(FuelF x HRF)0.42 |  |  | Estimated for SCR equipment, ammonia vaporization, water vaporization, and additional ID fan power, using eq. (2.60) or eq. (2.61), Ref. 1, §2.4.2. Total Annual Costs, page 2-74, (p75-pdf). Note: Eq's. (2.60) and (2.61), are equivalent since the first terms are equal, BMW = QB/NPHR.
SCR COST ESTIMATION
TOTAL CAPITAL COST
| I. | Total Capital Investment (TCI) Estimate
Retrofit Factor
81 |  |  |  | Selective Catalytic Reduction System |  |  | RFSCR |  |  | Data Entry, Line 30. |  |  | SCR System Retrofit Factor entered on Data Entry page, Line 30.
|  |  | SCR Partial Costs | [6 empty] | Note: The SCR partial costs for coal-fired emission units are calculated using EPA's proposed formulas for utility boilers.
82 |  |  |  | Capital Cost of SCR Base Unit |  |  | SCRcost | $ |  | 270,000 x (NRF)0.2 x (BMW x HRF x CoalF)0.92 x ELEVF x RF |  |  | Calculated with eq. (2.41), Ref. 1, §2.4.1.1 - Utility Boilers, page 2-66 (p67-pdf).
83 |  |  |  | Reagent Preparation Cost |  |  | RPC | $ |  | 490,000 x (NOxin x BMW x NPHR x h NOxR,sel)0.25 x RF |  |  | Eq. (2.42), Ref. 1, §2.4.1.1 - Utility Boilers, page 2-66 (p67-pdf).
84 |  |  |  | Balance of Plant Cost |  |  | BPC | $ |  | 460,000 x (BMW x HRF x CoalF)0.42 x ELEVF x RF |  |  | Eq. (2.44), Ref. 1, §2.4.1.1 - Utility Boilers, page 2-67 (p68-pdf).
85 |  |  |  | Air Pre-Heater Modification Cost |  |  | APHC | $ |  | 69,000 x (BMW x HRF x CoalF)0.78 x AHF x RF |  |  | Eq. (2.43), Ref. 1, §2.4.1.1 - Utility Boilers, page 2-67 (p68-pdf). APHC is zero for units burning coal with SO₂ content less than 3 lb/MMBtu and for all other fuels' units.
86 |  |  | Cost Adjustment Factor |  |  |  | CAF |  |  | CAF = 1.10 - for Natural Gas = 1.50 - for all oils = 0.00 - for coal |  |  | Multiplier used with the TCI for utility boilers so that it may be applied to all other units (i.e., engines and turbines). EPA has not provided a specific formula for the turbines and engines in the 2016 referenced documents.
87 |  |  | Total Capital Investment |  |  |  | TCI | $ |  | For coal boilers TCI=1.3x(SCRcost+RPC+BPC+APHC) |  |  | Calculated as follows: - with eq. (2.40), Ref. 1, §2.4.1.1 - Utility Boilers, p2-65(p66-pdf) for coal-fired boilers, - with eq. (2.45), Ref. 1, §2.4.1.1 - Utility Boilers, p2-68 (p69-pdf) for oil- and gas-fired boilers (≥25MW to 500 MW), and - with eq. (2.45), Ref. 1, §2.4.1.1 - Utility Boilers, p2-68 (p69-pdf) for oil- and gas-fired boilers multiplied with CAF on Line 83, for all other oil- and gas-fired units (i.e., turbines and engines).
For oil- and gas-fired boilers within 25 MW ≤ BMW < 500 MW TCI = 80,000 x (200/BMW)0.35 x BMW x ELEVF x RF
For oil- and gas-fired units (other than boilers) TCI = 80,000 x (200/BMW)0.35 x BMW x ELEVF x RF x CAF
| II. | Annual Costs
Direct Annual Elements Cost
88 |  |  |  | Annual Maintenance (0.5% TCI) |  |  | AMC | $/yr |  | 0.005 x TCI |  |  | Annual maintenance labor and material (including nozzle tips for injectors) is assumed 0.5% of TCI, per Ref. 1, §2.4.2 -Total Annual Costs, eq. (2.57), page 2-73 (p74-pdf).
89 |  |  |  | Annual Reagent Cost |  |  | ARC | $/yr |  | ṁreagent x CFTotal x 8,760 x Cost29% NH₃, or ṁreagent x top,control x Cost29% NH₃ |  |  | Calculated based on annual ammonia consumption (in lb/yr) and specific cost, per eq's. (2.58) and (2.59), Ref. 1 §2.4.2. - Total Annual Cost, p2-74 (p75-pdf), where qsol is replaced with ṁreagent, estimated by eq. (2.35). Note: Eq. (2.35) applies since the "Reagent Cost" is provided (in Data Entry, Line 43) in $/lb, instead of $/gal.
90 |  |  |  | Annual Electricity |  |  | AEC | $/yr |  | P x CFTotal x 8,760 x Costelect, or P x top,control x Costelect |  |  | Based on the annual power consumption (P, Line 77), multiplied by the control operating time, top,control, Line 3 (or equivalent CFTotal x 8,760) and electricity specific cost (Data Entry, Line 41), per eq. (2.62), Ref. 1 §2.4.2. - Total Annual Cost, page 2-74 (p75-pdf).
91 |  |  |  | Catalyst Replacement Cost |  |  | CRC | $ |  | Volcatalyst,(clc) x NSCR x CCreplace,IP / nlayer,sel |  |  | Per eq. (2.63), Ref. 1, §2.4.2. - Total Annual Cost, page 2-76 (p77-pdf).
.
92 |  |  |  |  | Yrs of catalyst life |  | Y | yrs |  | CLife / top, control |  |  | Operating life of the catalyst, CLife, Line 28 (in hrs) divided by the control operating time, top,control, Line 3 (in hrs) per eq.(2.66), Ref. 1, §2.4.2. - Total Annual Cost, page 2-77 (p78-pdf).
93 |  |  |  |  | Catalyst Future Worth Factor |  | FWF |  |  | i/[(1+i)Y-1] |  |  | FWF applied to catalyst replacement, assuming the interest rate listed in Data Entry, on Line 38. FWF calculated per eq. (2.65), Ref. 1, §2.4.2. p\2-76 (p77-pdf).
Annual Catalyst Cost
94 |  |  |  |  | Method 1 |  | ACRC1 | $/yr |  | CRC x FWF |  |  | Method 1 - Catalyst Replacement Cost (ACR) times Catalyst FWF, per eq. (2.64), Ref. 1, §2.4.2. p2-76 (p77-pdf).
95 |  |  |  |  | Method 2 |  | ACRC2 | $/yr |  | BMW x 0.4 x (FuelF)2.9 x (NRF)0.71 x CCreplace, SI |  |  | Method 2 - Per Sargent & Lundy, LLC, empirical eq. (2.67), Ref. 1, §2.4.2. p2-77 (p78-pdf).
Direct Annual Cost - DAC
96 |  |  |  | Method 1 |  |  | DAC1 | $/yr |  | Σ (Line 88, 89, 90 and Line 94) |  |  | Sum of the above direct annual costs (maintenance, reagent, electricity and catalyst- Method 1, - Method 2), per Ref. 1, §2.4.2. - Total Annual Cost, eq. (2.56), page 2-73 (p74-pdf).
97 |  |  |  | Method 2 |  |  | DAC2 | $/yr |  | Σ (Line 88, 89, 90 and Line 95)
Indirect Annual Cost (IDAC)
98 |  |  |  | Administrative Charges |  |  | AC | $/yr |  | 0.03 x (tcontrol x top,labor x LR + 0.4 x AMC) |  |  | Per Ref. 1, §2.4.2. - Total Annual Cost, eq. (2.69), page 2-78 (p79-pdf).
99 |  |  |  | Capital Recovery |  |  | CR | $/yr |  | CRF x TCI |  |  | Per Ref. 1 §2.4.2. - Total Annual Cost, eq. (2.70), page 2-79 (p80-pdf).
100 |  |  |  | Indirect Annual Costs |  |  | IDAC | $/yr |  | AC + CR |  |  | Total of the above indirect costs, Line 98 and Line 99, per Ref. 1 §2.4.2. - Total Annual Cost, eq. (2.68), page 2-78 (p79-pdf).
Total Annual Cost
101 |  |  |  | Method 1 |  |  | TAC1 | $/yr |  | DAC1 + IDAC |  |  | Total of direct (Method 1) and indirect costs, per eq. (2.72), Ref. 1 §2.4.2. p2-79 (p80-pdf).
102 |  |  |  | Method 2 |  |  | TAC2 | $/yr |  | DAC2 + IDAC |  |  | Total of direct (Method 2) and indirect costs, per eq. (2.72), Ref. 1 §2.4.2. p2-79 (p80-pdf).
103 | III. | Nox Removal per year |  |  |  |  | NOxR | tons |  | NOxR [Line 58] |  |  | Tons of NOx removed calculated above, on Line 58.
| IV. | Control Cost Effectiveness (2012$)
104 |  |  | Base Year | [6 empty] | Data Entry, Line 37 "2012$" - Default |  |  | Data Entry, Line 37 - Selected base year of EPA's cost analysis.
105 |  |  |  | Cost Effectiveness Method 1 |  |  | Costeffect,$2012,1 | 2012$/ton NOxR |  | TAC1/NOxR |  |  | Control cost effectiveness based on either TAC (method 1 or method 2) divided by the annual tons of NOx removed, per eq. (2.73), Ref. 1 §2.4.2. page 2-79 (p80-pdf).
106 |  |  |  | Cost Effectiveness Method 2 |  |  | Costeffect,$2012,2 | 2012$/ton NOxR |  | TAC2/NOxR
107 |  |  | Year Control is effective | [6 empty] | Data Entry, Line 28 |  |  | Year control is effective (or current year), as entered on Data Entry, Line 28.
108 |  |  |  | Cost Effectiveness Method 1 |  |  | Costeffect,yr,1 | $/ton NOxR |  | Costeffect,$2012,1 x CPI(current yr) |  |  | Control cost effectiveness adjusted for the year the air pollution control is effective (or current year), for either Method 1 or Method 2.
109 |  |  |  | Cost Effectiveness Method 2 |  |  | Costeffect,yr,2 | $/ton NOxR |  | Costeffect,$2012,2 x CPI(current yr)

## SNCR
[14 empty] | Revision: | 00
[14 empty] | Rev. Date: | 2016-08-31
AIR POLLUTION CONTROL COST EFFECTIVENESS ASSESSMENT FOR USE WITH RCSA SECTION 22a-174-22e(h) EXPLANATION
[10 empty] | References: | 1 | EPA Air Pollution Control Cost Manual - Seventh Edition, Section 4 - NOx Controls: Chapter 1 - Selective Noncatalytic Reduction, May 2016.
[11 empty] | 2 | EPA Air Pollution Control Cost Manual - Seventh Edition, Section 4 - NOx Controls: Chapter 2 - Selective Catalytic Reduction, May 2016.
[6 empty] | SELECTIVE NONCATALYTIC REDUCTION - SNCR |  |  |  |  | 3 | EPA Air Pollution Control Cost Manual - Sixth Edition (EPA 452/B-02-001), January 2002.
[11 empty] | 4 | Alternative Control Techniques Document - NOx Emissions from Stationary Gas Turbines - EPA ACT Document No.: EPA-453/R-93-007.
[11 empty] | 5 | U.S Department of Labor - Bureau of Labor Statistics: CPI Inflation Calculator.
Line |  | Item Description |  |  |  |  | Symbol | Units | Input Source / Equation / or Default Value |  |  | Comments
[9 empty] | Column 1. | Column 2.
[9 empty] | Default Operation | Limited Operation
SNCR ASSUMPTIONS
| I. | Air Pollution Control Assumptions
Control Unit Specifications
1 |  |  |  | Control Type |  |  |  |  | "SNCR" | "SNCR" |  | Line 1, Col. 1, will display "SNCR", and control's cost effectiveness calculation down the column, only if on Data Entry, select "Yes" on Line 14, fuel on Line 19, enter NOxin on Line 26 and NOxout on Line 27.
To show calculation on ''Limited Operation'' column (2), enter no. of hours on Data Entry Line 33, Column 2, otherwise the entire column will is blank.
2 |  |  |  | Number of SNCRs per Combustion Unit |  |  | NSNCR |  | "1" SNCR per emission unit - Default |  |  | Selected SNCR design criteria: one SNCR system per emission unit.
3 |  |  |  | SNCR Operating Time |  |  | top, control | hrs | Data Entry Line 34, Col. 1. | Data Entry Line 34, Col. 2. |  | Data Entry - Annual Emission Control Operating Time, in hrs. The SNCR is assumed to operate at all times the emission unit is operating.
Note:
All calculations displayed below, in both "Default Operation" and "Limited Operation" columns are using same default values and/or same equations for various intermediate parameters, factors or cost elements, to assess the cost effectiveness of the control. The calculations include control unit sizing, reagent requirements to attain the specified NOx reduction, and cost estimates of procurement, installation and operation of the equipment.
4 |  |  |  | SNCR Removal Efficiency (Default) |  |  | h NOxR | % | "40%" - Default |  |  | Assumed 40%. Per Ref. 1, §1.1 - Introduction, pages 1-3 (p3-pdf) through 1-7 (p7-pdf), urea based SNCR's exhibit NOx reduction efficiencies of 25% to 60%. Selected efficiency is adjusted if NOxout calculated value falls below the SNCR attainable limit.
5 |  |  |  | SNCR Lowest Attained NOxout Rate |  |  | NOxout, min | lb/MMBtu | "0.100 lb/MMBtu"-Default non-FB boilers "0.080 lb/MMBtu"-Default for all other units |  |  | Lowest achievable NOxout rate, per Ref. 1, §1.4-Cost Analysis, page 1-43 (p43-pdf), for non-FB boilers (0.1 lb/MMBtu) and FB boilers (0.08 lb/MMBtu). The limit of 0.08 lb/MMBtu, also assumed for all other types of emission units.
| II. | Reagent and Reagent Solutions Specifications
Reagent Properties
6 |  |  |  | Reagent type |  |  |  |  | "urea" - Default |  |  | Selected SNCR default reagent based on considerations in Ref. 1, §1.2.2 - Reagents, pages 1-13 through 1-15 (p13-p15, pdf). In addition, per Ref. 1, page 1-8 (p8-pdf), 67% of utility boilers include SNCR using urea as reagent. No reference regarding turbines and engines.
7 |  |  |  | Reagent Molecular Weight |  |  | Mreagent | lb/mole | "60.06 lb/mole"-urea Molecular Weight |  |  | Urea Molecular Weight, per Ref. 1, Table 1.4, page 1-14 (p14-pdf).
8 |  |  |  | Theoretical Stoichiometric Ratio |  |  | SRT |  | "2" - urea Default "1" - ammonia Default |  |  | Term in eq. (1.15), Ref. 1, §1.3.1 - Design Parameters for Study-Level Estimate, Normalized Stoichiometric Ratio, page 1-38 (p38-pdf).
Water Properties
9 |  |  |  | Water Standard Density |  |  | ρwater | lb/gal | "8,345 lb/gal" - Default |  |  | Per Ref.1, §1.4.2-TAC, Water Consumption, eq.(1.44), p1-54(p54-pdf).
10 |  |  |  | Water Heat of Vaporization (at 310ºF) |  |  | Hv | Btu/lb | "900 Btu/lb at 310ºF" - Default |  |  | Per Ref. 1, §1.4.2 - Total Annual Cost, Additional Fuel to Vaporize Water in Reagent Solution, eq. (1.47) pages 1-54 & 1-55 (p54-p55, pdf); Note: Urea 10% solution has same Hv as water. 310ºF is the representative temperature for an exiting flue gas.
Storage
11 |  |  |  | Stored Urea Solution Concentration |  |  | Curea sol stored | % by weight | "50%" - Default |  |  | Typical value, per Ref. 1, §1.2.2 - Reagents, page 1-14 (p14-pdf).
12 |  |  |  | Urea 50% Solution Density (at 80ºF) |  |  | ρ 50% urea | lb/ft³ | "71.0 lb/ft³ "- Default |  |  | Per Table 1-4-Urea and Ammonia Reagent Properties, Ref. 1, §1.2.2-Reagents, page 1-14 (p14-pdf).
13 |  |  |  | Injected Urea Concentration |  |  | Curea sol injected | % by weight | "10%"- Default |  |  | Per Ref. 1, §1.2.4 - SNCR System, Diluting, Metering and Mixing of the Reagent, page 1-26 (p26-pdf). Selected 10% as default.
14 |  |  |  | No. Storage Days |  |  | tstorage | days | "14 days" - Default |  |  | Common onsite storage requirement, per Ref. 1, §1.3.1 - Design Parameters for Study-Level Estimate, Estimating Reagent Consumption and Tank Size, eq.(1.21), page 1-41 (p41-pdf).
| III. | Specific Economic Factors
SNCR Costs Factors
15 |  |  |  | Ash Disposal Cost |  |  | Costash | $/ton | "15.00 $/ton" - Default |  |  | For coal unit only, per Ref. 1, § 1.5-Example Problem, p1-58 (p58-pdf).
Capital Cost Elevation Factor
16 |  |  |  | Elevation Factor |  |  | ELEVF |  | 14.7 psia / {2116 x (1/144) x x [(59-(0.00356xh)+459.7)/518.6]5.256} |  |  | Calculated per eq's. (1.22) & (1.23), Ref. 1, §1.4.1 - Total Capital Investment, page 1-45 (p45-pdf).
SNCR SIZING
| I. | Emission Unit Performance Data
Emission Unit Data
17 |  |  |  | Unit Type |  |  |  |  | Data Entry, Line 10. |  |  | Emission unit type selected on Data Entry page, Line 10.
18 |  |  |  | Boiler Type Factor (for boilers only) |  |  | BTF |  | BTF = 1 if Data Entry, Line 12 = "non-FB" |  |  | Based on the input from Data Entry, Line 12, specifying whether the boiler is a Fluidized Bed (FB) unit or a non-FB boiler unit such as cyclone, wall-fired, tangential-fired, etc.
BTF = 0.75 if Data Entry, Line 12 = "FB"
19 |  |  |  | Maximum Heat Rate Input |  |  | QB | MMBtu/hr | Data Entry, Line 16, or calculated as: QB = NPHR x BMW |  |  | Input from Data Entry, Line 16, if emission unit is a Combined Cycle or a Boiler with a known Heat Input, otherwise it is calculated as: [Heat Input, QB = NPHR x BMW].
20 |  |  |  | Power Output (MW Rating) at full load capacity. |  |  | BMW | MW | Data Entry, Line 17, or calculated as: BMW = QB / NPHR |  |  | Input from Data Entry, Line 17, if emission unit is a Combustion Turbine, Engine, or a Boiler with a known MW output, otherwise is calculated as: [BMW = QB / NPHR].
21 |  |  |  | Heat Rate (Nom Plate Heat Rate) |  |  | NPHR | MMBtu/MWh | Data Entry, Line 18. |  |  | Emission unit Heat Rate listed on Data Entry, Line 18. Note: Heat Rate listed value should be equal to the ratio of the selected QB and BMW values.
22 |  |  |  | Heat Rate Factor |  |  | HRF |  | NPHR / 10 MMBtu/MWh |  |  | Defined by eq. (1.6), Ref. 1, §1.3.1 - Design Parameters for Study-Level Estimates, p1-35 (p35-pdf), as the ratio of actual NPHR to a typical heat rate of 10 MMBtu/MWh, used in developing capital cost equations.
23 |  |  |  | Annual Hrs of Operation |  |  | top, ems unit | hrs | Data Entry Line 33, Col. 1. | Data Entry Line 33, Col. 2. |  | Data Entry - Emission Unit Annual Hrs of Operation, Line 33, Columns 1 & 2. The air pollution control is assumed to operate at all times the emission unit is operating.
24 |  |  |  | Heat Input Max Annual |  |  | HI | MMBtu/yr | BMW x NPHR x top,ems unit, or QB x top,ems unit |  |  | Calculated based on BMW and NPHR, or QB, multiplied by the emission unit top,ems unit.
25 |  |  |  | Annual Actual MW Output |  |  | Boutput | MW/yr | BMW x top,ems unit |  |  | Power Output, BMW, (Line 20) multiplied by the Annual Hrs. of Operation, top, ems unit (Line 23).
Operating Capacity Factors
26 |  |  |  | Emission Unit Capacity Factor |  |  | CF plant |  | Boutput / (BMW x 8,760 hrs) |  |  | Per Ref. 1, § 1.3.1 - Design Parameters for Study-Level Estimates, System Capacity Factor, eq. (1.8a), p1-36 (p36-pdf). Since max. MW output is selected, eq. (1.8a) is equivalent with the selected hrs. of operation divided by 8,760 hrs.
27 |  |  |  | SNCR Capacity Factor |  |  | CF SNCR |  | top, control / top, ems unit |  |  | SNCR Capacity Factor is the ratio between SNCR operating time and emission unit operating time, similar to the SCR Capacity Factor defined by eq. (2.9), Ref. 2, §2.3.3 - System Capacity Factor, p2-53 (p54-pdf).
28 |  |  |  | Total Capacity Factor |  |  | CF Total |  | CFems unit x CF SNCR |  |  | Defined by eq. (1.7), Ref. 1, § 1.3.1 - Design Parameters for Study-Level Estimates, System Capacity Factor, page 1-35 (p35-pdf).
Fuel Data
29 |  |  |  | Fuel Type |  |  |  |  | Data Entry, Line 19. |  |  | Emission unit fuel type selected on Data Entry, Line 19. Note: Since Connecticut has only one coal-fired emission unit that burns a mix of bituminous and sub-bituminous coal only, all specifications of this calculation for emission units burning coal are selected for bituminous coal.
30 |  |  |  | Air Heater Factor |  |  | AHF |  | AHF = 1, if bituminous coal and SO₂> 3lb/MMBtu - Default AHF = 0, if not true, - Default |  |  | Defined in Eq. (1.26), Ref 1, §1.4.1.1 - Utility Boilers, p1-46 (p46-pdf) & 1-47 (p47-pdf), as multiplier for Air Pre-Heater Cost. AHF=1, if bituminous coal and SO2> 3lb/MMBtu, =0 if not true. Note: Since Connecticut has only one coal-fired emission unit that burns a mix of bituminous and sub-bituminous coal, AHF is "0", and the air pre-heater term drops out of the overall SNCR cost equation, for all CT emission units.
31 |  |  |  | Fuel Factor/Coal factor (if fuel is "Coal") |  |  | FuelF/CoalF (if fuel is "Coal") |  | CoalF = 1 - for bituminous coal - Default FuelF = 1 - for lq and gas fuels - Default |  |  | Defined in eq's. (1.25) and (1.26), Ref 1, §1.4.1.1 - Utility Boilers, p1-46 (p46-pdf) and eq's (1.32) and (1.33), Ref 1, §1.4.1.3 - Industrial Boilers, p1-49 (p49-pdf) & 1-50 (p50-pdf), as "CoalF" multiplier for coal units. CoalF is replaced with a (Fuel) factor equal to 1, for oil- and gas-fired emission units. CoalF (or FuelF) multiplier applied to CT units is = 1.
32 |  |  |  | Fuel High Heating Value |  |  | HHV | Btu/lb | Auto Input from U.S. DOE reference. |  |  | Per US DOE Biomass Energy Databook: | http://cta.ornl.gov/bedb/appendix_a.shtml
Btu/ft³ (for gas)
33 |  |  |  | Fuel Cost |  |  | Costfuel | $/MMBtu | Auto Input from U.S. EIA reference. |  |  | Input from U.S. Energy Information Administration - EIA 2011-2012 data. In the web page below, select year in the Annual Energy Review archives and in Data Categories select fuel:
http://www.eia.gov/totalenergy/data/annual/index.cfm
34 |  |  |  | Max. Fuel Consumption Rate |  |  | m(fuel) | lb/hr | (HI x 106/ HHV) / top,ems unit or QB x 106 / HHV |  |  | Calculated as hourly heat input (Line 24 divided by Line 23) and divided by the fuel HHV (Line 32), or Maximum Heat Rate Input (QB) on Line 19 divided by fuel HHV - Line 32.
[7 empty] | V(fuel) | CFH - for gas
35 |  |  |  | Annual Fuel Consumption |  |  | Annual Fuel | lb/yr | m (fuel) x top,ems unit |  |  | Fuel consumption rate (Line 33) multiplied by the annual hours of operation (Line 23).
|  |  |  | (estimate based on selected HHV) |  |  |  | CF/yr - for gas | V (fuel) x top,ems unit
NOx Removal Performance
36 |  |  |  | Uncontrolled NOx Emission Level |  |  | NOxin | lb/MMBtu | Data Entry, Line 26. |  |  | Uncontrolled NOx rate, entered on Data Entry, Line 26.
37 |  |  |  | Controlled NOx Outlet (required) |  |  | NOxout | lb/MMBtu | Data Entry, Line 27. |  |  | Controlled NOx rate, as required by RCSA 22a-174-22e, and listed on Data Entry, Line 27.
38 |  |  |  | Controlled NOx Outlet (selected) |  |  | NOxout | lb/MMBtu | MAX(NOxout, NOxmin, NOxin - hNOxR x NOxin) |  |  | Determined as the highest among: the required controlled NOxout, the SCR lowest attained NOxout rate, or the NOxout value based on the 90% default efficiency.
39 |  |  |  | NOx Removal Efficiency (selected) |  |  | h NOx | % | (NOxin - NOx out sel)/NOxin x 100% |  |  | Defined by eq. (1.10) Ref. 1, §1.3.1. - Design Parameters for Study-Level Estimates, NOx Removal Efficiency, p1-37 (p37-pdf) and calculated based on NOxin on Line 35 and the value of NOxout sel, on Line 37.
40 |  |  |  | NOx Removed Hourly Rate |  |  | NOxR/hr | lb/hr | NOxin x ηNOxR,sel x QB |  |  | Defined by eq. (1.12), Ref. 1, §1.3.1 - Design Parameters for Study-Level, NOx Removal Rates, page 1-37 (p37-pdf).
41 |  |  |  | NOx Removed (annually) |  |  | NOxR | tons | NOxin x hNOxR,sel x QB x top, control / 2,000, or NOxin x hNOxR,sel x QB x CFTotal x 8,760 / 2,000 |  |  | Defined by eq. (1.11), Ref. 1, §1.3 - Design Parameters for Study-Level, NOx Removal Rates, page 1-37 (p37-pdf).
| II. | Reagent Calculations
Reagent Data
42 |  |  |  | Normalized Stoichiometric Ratio |  |  | NSR |  | [2 NOxin + 0.7] h NOxR,sel / NOxin |  |  | Ratio of moles of equivalent NH3 injected to the moles of uncontrolled NOx, defined by empirical eq. (1.17), Ref. 1, §1.3.1 - Design Parameters for Study-Level, Normalized Stoichiometric Ratio, page 1-38 (P38-pdf).
43 |  |  |  | Actual Stoichiometric Ratio |  |  | ASR |  | NSR / SRT |  |  | Ratio of moles of reagent reacted to the moles of uncontrolled NOx, defined by eq. (1.15), Ref. 1, §1.3.1 - Design Parameters for Study-Level, Normalized Stoichiometric Ratio, page 1-38 (P38-pdf).
44 |  |  |  | Utilization |  |  | Utilization |  | h NOxR,sel / NSR |  |  | Ratio of moles of reagent reacted to the mole injected - defined by eq. (1.16), Ref. 1, §1.3.1 - Design Parameters for Study-Level, Normalized Stoichiometric Ratio, page 1-38 (P38-pdf).
Flow Rates
45 |  |  |  | Urea Consumption |  |  | ṁreagent | lb/hr | NOxin x QB x hNOxR,sel x ASR x Mreagent / MNOx |  |  | Eq. (1.18), Ref. 1, §1.3.1 - Design Parameters for Study-Level, Estimating Reagent Consumption and Tank Size, page 1-40 (p40-pdf).
Aqueous Urea 50% Solution
46 |  |  |  |  | Mass Flow Rate |  | ṁsol | lb/hr | ṁreagent / Curea sol stored |  |  | Eq. (1.19), Ref. 1, §1.3.1 - Design Parameters for Study-Level, Estimating Reagent Consumption and Tank Size, page 1-40 (p40-pdf).
47 |  |  |  |  | Volumetric Flow Rate |  | qsol | gph | ṁsol x 7.4805 [gal/ft³] / ρ50% urea |  |  | Eq. (1.20), Ref. 1, §1.3.1 - Design Parameters for Study-Level, Estimating Reagent Consumption and Tank Size, page 1-40 (p40-pdf).
Fuel Rq'd to Vaporize Water in Reagent Solution
48 |  |  |  | Fuel to Prepare 10% Reagent Sol. |  |  | ΔFuelReagent | MMBtu/hr | Hv x ṁreagent x ( 1/Curea sol injected -1) /10⁶ |  |  | Additional fuel to evaporate the injected water in 10% urea solution, estimated by eq's (1.47) and (1.48), Ref.1, §1.4.2. - Total Annual Cost, Additional Fuel to Vaporize Water in Reagent Solution, pages: 1-54, 1-55 (p54-55, pdf).
Storage
49 |  |  |  | Storage Tank Volume |  |  |  | gal | qsol x tstorage x 24 [hrs/day] |  |  | Eq. (1.21), Ref. 1, §1.3.1 - Design Parameters for Study-Level, Estimating Reagent Consumption and Tank Size, page 1-41 (p41-pdf).
| III. | Utilities
50 |  |  |  | Power Consumption |  |  | P | kW | 0.47 x NOxin x NSR x QB / NPHR |  |  | Estimated by eq. (1.42), Ref. 1, §1.4.2. Total Annual Costs, Utilities, page 1-53 (p53-pdf).
51 |  |  |  | Water Consumption |  |  | q water | gph | ṁsol / ρwater x (Curea sol stored/Curea sol injected -1) |  |  | Estimated by eq. (1.44), Ref. 1, §1.4.2. Total Annual Costs, Water Consumption, page 1-54 (p54-pdf).
52 |  |  |  | Coal Ash Disposal |  |  |  |  | ΔFuelReagent x ash product / HHV x 10⁶ |  |  | Disposal of ash in added fuel used to vaporize water in reagent solution, estimated by eq. (1.50), Ref. 1, §1.4.2. Total Annual Costs, Coal Ash Disposal, page 1-55 (p55-pdf).
SNCR COST ESTIMATION
TOTAL CAPITAL COST
| I. | Total Capital Investment (TCI) Estimate
Retrofit Factor
53 |  |  |  | Selective Noncatalytic Reduction System |  |  | RFSNCR |  | Data Entry, Line 31 |  |  | SNCR System Retrofit Factor entered on Data Entry page, Line 31.
|  |  | SNCR Partial Costs | [5 empty] | Note:
Connecticut has no industrial boliers and only one utility bolier. Therefore, SNCR partial costs for that unit are determined using EPA's formulas for utility boliers.
54 |  |  |  | Capital Cost of SNCR Base Unit |  |  | SNCRcost | $ | For coal boilers SNCRcost = 220,000 x (BMW x HRF)0.42 x CoalF x BTF x ELEVF x RF |  |  | Coal boilers' SNCRcost is calculated with eq. (1.25), Ref. 1, §1.4.1.1 - Utility Boilers, Coal-fired Units, page 1-46 (p46-pdf).
[9 empty] | For oil- and gas fired boilers and all other emission units SNCRcost = 147,000 x (BMW x HRF)0.42 x ELEVF x RF |  |  | Oil- and gas burning boilers' SNCRcost is estimated per eq. (1.29), Ref. 1, §1.4.1.2 - Utility Boilers, Oil- and gas-fired units, p1-48 (p48-pdf). Since EPA has not provided a specific formula for all other emission units (i.e., turbines and engines), the same eq. (1.29) is applied adjusted with the CAF multiplier defined below at Line 57.
55 |  |  |  | Balance of Plant Cost |  |  | BOPCost | $ | For coal boilers BOPcost = 320,000 x (BMW)0.33 x (NOxR/hr)0.12 x BTF x RF |  |  | Coal boilers' BOPcost is calculated with eq. (1.27), Ref. 1, §1.4.1.1 - Utility Boilers, Coal-fired Units, page 1-47 (p47-pdf).
[9 empty] | For oil- and gas fired boilers and all other emission units BOPcost = 213,000 x (BMW)0.33 x (NOxR/hr)0.12 x RF |  |  | Oil- and gas burning boilers (≥ 25 MW) BOPcost is estimated per eq. (1.30), Ref. 1, §1.4.1.2 - Utility Boilers, Oil- and gas-fired units, p1-48 (p48-pdf). Since EPA has not provided a specific formula and in lieu of actual cost data or cost assessment formulas, for all other emission units such as turbines (single and combined cycle) and engines, the same eq. (1.30) is applied, results being adjusted with CAF multiplier defined below, at Line 57.
56 |  |  |  | Air Pre-Heater Modification Cost |  |  | APHCcost | $ | 69,000 x (BMW x HRF x CoalF)0.78 x AHF x RF |  |  | Per eq. (1.26), Ref. 1 §1.4.1.1 - Utility Boilers, Coal-fired Units, page 1-46 (p46-pdf). APHCcost is zero for utility boilers burning coal with SO₂ content less than 3 lb/MMBtu and also "zero" for all other fuels' burning units.
57 |  |  | Cost Adjustment Factor |  |  |  | CAF |  | CAF = 1.10 - for Natural Gas and oils = 0.00 - for coal |  |  | Multiplier used with the TCI for utility boilers so that it may be applied to all other units (i.e., engines and turbines). EPA has not provided a specific formula for the turbines and engines in the 2016 referenced documents.
58 |  |  | Total Capital Investment |  |  |  | TCI | $ | For coal boilers TCI=1.3x(SNCRcost+BOPcost+APHCcost) |  |  | Calculated as follows: - with eq. (1.24), Ref. 1, §1.4.1.1, p1-45 (p45-pdf), for boilers on coal, - with eq. (1.28), Ref. 1, §1.4.1.2 p1-47 (p47-pdf), for oil- and gas-fired boilers (≥25MW) and - with eq. (1.28), Ref. 1, §1.4.1.2 p1-47 (p47-pdf), multiplied with CAM on Line 57, for all other (than boilers) oil- and gas-fired units, such as turbines (single and combined cycle) and engines.
For oil- and gas-fired boilers ≥ 25 MW TCI = 1.3 x (SNCRcost +BOPcost)
For other oil- and gas-fired units (other than boilers) TCI = 1.3 x (SNCRcost +BOPcost) x CAF
| II. | Annual Costs
Direct Annual Elements Cost
59 |  |  |  | Annual Maintenance |  |  | AMC | $/yr | 0.015 x TCI |  |  | Annual maintenance labor and material (including nozzle tips for injectors) is assumed 1.5% of TCI, per Ref. 1, §1.4.2 -Total Annual Costs, Maintenance, eq. (1.39), page 1-52 (p52-pdf).
60 |  |  |  | Annual Reagent Cost |  |  | ARC | $/yr | qsol x CFTotal x 8,760 x Cost50% urea, or qsol x top,control x Cost50% urea |  |  | Calculated based on 50% sol. urea consumption (in gal/yr) and specific cost, per eq's. (1.40) and (1.41), Ref. 1 §2.4.2. - Total Annual Cost, p1-52 (p52-pdf).
61 |  |  |  | Annual Electricity |  |  | AEC | $/yr | P x CFTotal x 8,760 x Costelect, or P x top,control x Costelect |  |  | Based on the annual power consumption (P, Line 50), multiplied by the control operating time, top,control, Line 3 (or equivalent CFTotal x 8,760) and electricity specific cost (Data Entry, Line 41), per eq (1.43), Ref. 1, § 1.4.2. - Total Annual Cost, page 1-53 (p53-pdf).
62 |  |  |  | Annual Water Cost |  |  | AWC | $/yr | qwater x CFTotal x 8,760 x Costwater, or qwater x top,control x Costwater |  |  | Annual water consumption times water specific cost, per eq. (1.46), Ref. 1, §1.4.2. - Total Annual Cost, page 1-54.
63 |  |  |  | Annual ΔFuel Reagent Cost |  |  | ΔFuelReagent Cost | $/yr | ΔFuelReagent x top, control x Costfuel |  |  | Per eq. (1.49), Ref. 1, §1.4.2. - Total Annual Cost, page 1-55 (p55-pdf).
64 |  |  |  | Annual ΔAsh Cost |  |  | ΔAsh Cost | $/yr | ΔAsh x top, control / 2000[lb/ton] x Costfash |  |  | Per eq. (1.51), Ref. 1, §1.4.2. - Total Annual Cost, page 1-56 (p56-pdf).
65 |  |  | Direct Annual Cost - DAC |  |  |  | DAC | $/yr | Σ (Line 59... Line 64) |  |  | Sum of the above direct annual costs, Line 59 through Line 64, per eq. (1.38), Ref. 1, §2.4.2.-Total Annual Cost, page 1-52, (p52-pdf).
Indirect Annual Cost (IDAC)
66 |  |  |  | Administrative Charges |  |  | AC | $/yr | 0.035 x AMC |  |  | Per eq. (1.53), Ref. 1 §1.4.2. - Total Annual Cost, page 1-56 (p56-pdf).
67 |  |  |  | Capital Recovery |  |  | CR | $/yr | CRF x TCI |  |  | Per eq. (1.54), Ref. 1 §1.4.2. - Total Annual Cost, page 1-57 (p57-pdf).
68 |  |  |  | Indirect Annual Costs |  |  | IDAC | $/yr | AC + CR |  |  | Total of the above indirect costs, Line 66 and Line 67,
69 |  |  | Total Annual Cost |  |  |  | TAC | $/yr | DAC + IDAC |  |  | Total of direct and indirect costs, per eq.(1.56), Ref. 1, §1.4.2-Total Annual Costs, page 1-57(p57-pdf).
70 | III. | NOx Removal per year |  |  |  |  | NOxR | tons | NOxR [Line 41] |  |  | Tons of NOx removed calculated above, on Line 41.
| IV. | Control Cost Effectiveness
71 |  |  | Base Year | [5 empty] | Data Entry, Line 37 "2012$" - Default |  |  | Data Entry, Line 37 - Selected base year of EPA's cost analysis.
72 |  |  |  | Cost Effectiveness |  |  | Costeffect,$2012 | 2012$/ton NOxR | TAC / NOxR |  |  | Control cost effectiveness based on TAC divided by the annual tons of NOx removed, per eq. (1.57), Ref. 1, §1.4.2. - Total Annual Cost, p1-57 (p57-pdf).
73 |  |  | Year Control is effective | [5 empty] | Data Entry, Line 28 |  |  | Year control is effective (or current year), as entered on Data Entry, Line 28.
74 |  |  |  | Cost Effectiveness |  |  | Costeffect,yr | $/ton NOxR | Costeffect,$2012 x CPI(current yr) |  |  | Control cost effectiveness adjusted for the year air pollution control is effective (or current year).

## HPWI
[13 empty] | Revision: | 00
[13 empty] | Rev. Date: | 2016-08-31
AIR POLLUTION CONTROL COST EFFECTIVENESS ASSESSMENT FOR USE WITH RCSA SECTION 22a-174-22e(h) EXPLANATION
[9 empty] | References: | 1 | EPA Air Pollution Control Cost Manual - Seventh Edition, Section 4 - NOx Controls: Chapter 1 - Selective Noncatalytic Reduction, May 2016.
[10 empty] | 2 | EPA Air Pollution Control Cost Manual - Seventh Edition, Section 4 - NOx Controls: Chapter 2 - Selective Catalytic Reduction, May 2016.
[5 empty] | HIGH PRESSURE WATER INJECTION |  |  |  |  | 3 | EPA Air Pollution Control Cost Manual - Sixth Edition (EPA 452/B-02-001), January 2002.
[10 empty] | 4 | Alternative Control Techniques Document - NOx Emissions from Stationary Gas Turbines - EPA ACT Document No.: EPA-453/R-93-007.
[10 empty] | 5 | U.S Department of Labor - Bureau of Labor Statistics: CPI Inflation Calculator.
Line |  | Item Description |  |  |  | Symbol | Units | Input Source / Equation / or Default Value |  |  | Comments
[8 empty] | Column 1. | Column 2.
[8 empty] | Default Operation | Limited Operation
HPWI ASSUMPTIONS
Note: HPWI Cost Effectiveness Calculation is disabled for emission units on coal, since no unit burning coal will install HPWI to control NOx emissions.
| I. | Air Pollution Control Assumptions
Control Unit Specifications
1 |  |  |  | Control Type |  |  |  | "HPWI" | "HPWI" |  | Line 1, Col. 1, will display "HPWI", and control's cost effectiveness calculation down the column, only if on Data Entry: select "Yes" on Line 15, fuel on Line 19, enter NOxin on Line 26 and NOxout on Line 27.
To show calculation on ''Limited Operation'' Colum (2), enter no. of hours on Data Entry Line 33, Column 2, otherwise the entire column will be blank.
2 |  |  |  | Number of HPWI per Combustion Unit |  | NHPWI |  | "1" HPWI per emission unit - Default |  |  | Selected design criteria: one HPWI system per emission unit.
3 |  |  |  | HPWI Operating Time |  | top, control | hrs | Data Entry Line 32, Col. 1. | Data Entry Line 32, Col. 2. |  | Data Entry - Annual Emission Control Operating Time, in hrs. The HPWI is assumed to operate at all times the emission unit is operating.
Note:
All calculations displayed below, in both "Default Operation" and "Limited Operation" columns are using same default values and/or same equations for various intermediate parameters, factors or cost elements, to assess the cost effectiveness of the control. The calculations include control unit sizing, reagent requirements to attain the specified NOx reduction, and cost estimates of procurement, installation and operation of the equipment.
4 |  |  |  | HPWI Removal Efficiency (Default) |  | h NOxR | % | "60%" - Default |  |  | Selected 60% as default. Control efficiency needs to be recalculated if NOxout falls below the HPWI attainable limit.
5 |  |  |  | HPWI Lowest Attained NOxout Rate |  | NOxout, min | lb/MMBtu | "0.170" - Default |  |  | Per Ref. 4, §5.1.4 - Achievable NOx Emissions Using Wet Controls, page 5-53 (p144-pdf), 0.17 lb/MMBtu approx. corresponds to 42 ppm (for both natural gas and oils) and is considered a practical achievable lowest NOx rate of a HPWI system.
| II. | Reagent and Reagent Solutions Specifications
Water Properties
6 |  |  |  | Water Standard Density |  | ρwater | lb/gal | "8,345 lb/gal" - Default |  |  | Defined in eq. (1.44), Ref. 1 (SNCR), §1.4.2-Total Annual Cost, p1-54 (p54-pdf).
7 |  |  |  | Water Heat of Vaporization |  | Hv | Btu/lb | "900 Btu/lb at 310ºF" - Default |  |  | Per Ref. 1 (SNCR), §1.4.2 - Total Annual Cost, Additional Fuel to Vaporize Water in Reagent Solution, eq. (1.47) pages 1-54 & 1-55 (p54-p55, pdf); Note: 310ºF is the representative temperature for an exiting flue gas.
| III. | Specific Economic Factors and Costs
Capital Cost Elevation Factor
8 |  |  |  | Elevation Factor |  | ELEVF |  | 14.7 psia / {2116 x (1/144) x x [(59-(0.00356xh)+459.7)/518.6]5.256} |  |  | Multiplier defined by eq. (1.22), Ref. 1 (SNCR), §1.4.1 - TCI, p1-41 (p41-pdf) and by eq's. (2.39a) & (2.39b), Ref. 2 (SCR), §2.4.1 - TCI, p2-64 & p2-65 (p65/p66-pdf), to be also applied to HPWI.
Cost Adjustment Multiplier 2012$/1990$
9 |  |  |  | Consumer Price Index Inflation |  | CPI Inflation | 2012$/1990$ | "0.176" - Default |  |  | CPIInflation to convert 1990$ to 2012$ (base year of 2016 EPA's SNCR & SCR Cost Manuals) - see Ref. 5 web link.
HPWI Water Treatment and Disposal Costs
10 |  |  |  | Water Treatment Cost, $/gal |  | WTC$/gal | $/gal | $1.97/1,000gal (Default) x CPIInflation |  |  | Water Treatment Cost, WTC$/gal, in 1990$, published on Table 6-3, Ref. 4, p6-213 (p304-pdf), taken as default, times CPIInflation, to convert in 2012$.
11 |  |  |  | Water Treatment Labor Cost, $/gal |  | WTLC$/gal | $/gal | $0.70/1,000gal (Default) x CPIInflation |  |  | Water Treatment Labor Cost, WTLC$/gal, in 1990$, published on Table 6-5, Ref. 4, p6-222 (p313-pdf), taken as default, times CPIInflation, to convert in 2012$.
12 |  |  |  | Water Disposal Cost, $/gal |  | WDC$/gal | $/gal | $3.82/1,000gal (Default) x CPIInflation |  |  | Water Disposal Cost, WDC$/gal, in 1990$, published on Table 6-3, Ref. 4, p6-213 (p304-pdf), taken as default, times CPIInflation., to convert in 2012$.
Labor Costs
13 |  |  |  | Number of hours of operator labor |  | top, labor | hrs/day | "4.00" - Default |  |  | HPWI systems, as SCR's systems require daily maintenance for repair and replacements, when necessary. Selected 4 hrs as default, same as SCR's suggested value, per Ref. 2, § 2.5 & 2.6-Ex. Problem(s) 1 and 2, p2-80(p81-pdf) and p2-88(p89-pdf).
14 |  |  |  | Labor Rate |  | LR | $/hr | Data Entry, Line 44 |  |  | EPA suggested "Labor Rate" listed on Data Entry, Line 45.
HPWI SIZING
| I. | Emission Unit Performance Data at 8760 hrs
Emission Unit Data
15 |  |  |  | Unit Type |  |  |  | Data Entry, Line 10. |  |  | Emission unit type selected on Data Entry page Line 10.
16 |  |  |  | Maximum Heat Rate Input |  | QB | MMBtu/hr | Data Entry, Line 16, or calculated as: QB = NPHR x BMW |  |  | Input from Data Entry, Line 16, if emission unit is a Combined Cycle or a Boiler with a known Heat Input, otherwise is calculated as: [Heat Input, QB = NPHR x BMW].
17 |  |  |  | Nominal Plate Power Capacity |  | BMW | MW | Data Entry, Line 17, or calculated as: BMW = QB / NPHR |  |  | Input from Data Entry, Line 17, if emission unit is a turbine, engine, or a boiler with a known MW output, otherwise is calculated as: [BMW = QB / NPHR].
18 |  |  |  | Heat Rate (Nom Plate Heat Rate) |  | NPHR | MMBtu/MWh | Data Entry, Line 18. |  |  | Emission unit Heat Rate listed on Data Entry, Line 18. Note: Heat Rate listed value should be equal to the ratio of selected QB and BMW values.
19 |  |  |  | Annual Hrs of Operation |  | top, ems unit | hrs | Data Entry Line 33, Col. 1. | Data Entry Line 33, Col. 2. |  | Data Entry page - Emission Unit Annual Hrs of Operation, Line 33, Col's 1 & 2. The air pollution control is assumed to operate at all times the emission unit is operating.
20 |  |  |  | Heat Input Max Annual |  | HI | MMBtu/yr | BMW x NPHR x top,ems unit, or QB x top,ems unit |  |  | Calculated based on BMW and NPHR, or QB, multiplied by top,ems unit.
21 |  |  |  | Annual Actual MW Output |  | Boutput | MW/yr | BMW x top,ems unit |  |  | Power Output, BMW, (Line 17) multiplied by top, ems unit (Line 19).
Operating Capacity Factors
22 |  |  |  | Emission Unit Capacity Factor |  | CF ems unit |  | Boutput / (BMW x 8,760 hrs) |  |  | See Ref. 1, § 1.3.1, eq. (1.8a), p1-36 (p36-pdf) and Ref. 2 §2.3.3, eq. (2.8a), p2-53 (p54-pdf).
23 |  |  |  | HPWI Capacity Factor |  | CF HPWI |  | top, control / top, ems unit |  |  | See eq. (2.9), Ref. 2, §2.3.3 - System Capacity Factor, page 2-53 (p54-pdf)
24 |  |  |  | Total Capacity Factor |  | CF Total |  | CFems unit x CF HPWI |  |  | See Ref. 1, § 1.3.1, eq. (1.7), p1-35 (p35-pdf) and Ref. 2 §2.3.3, eq. (2.7), p2-53 (p54-pdf).
25 |  |  |  | Fuel Type |  |  |  | Data Entry, Line 19. |  |  | Data Entry input, Line 19.
26 |  |  |  | Fuel Low Heating Value |  | LHV | BTU/lb | Auto Input from a U.S. DOE reference. |  |  | Per US DOE Biomass Energy Databook: | http://cta.ornl.gov/bedb/appendix_a.shtml
[7 empty] | Btu/ft³ (for gas) |  |  |  | Note: Cost analysis in ACT (Ref. 4) is based on fuel LHV.
27 |  |  |  | Fuel Cost |  | Costfuel | $/MMBtu | Auto Input from a U.S. EIA reference. |  |  | Input from U.S. Energy Information Administration - EIA 2011-2012 data. In the web page below, select year in the Annual Emery Review archives and in Data Categories select fuel:
http://www.eia.gov/totalenergy/data/annual/index.cfm
28 |  |  |  | Max. Fuel Consumption Rate |  | m(fuel) | lb/hr | (HI x 106/ HHV) / top,ems unit or QB x 106 / HHV |  |  | Hourly heat input divided by the fuel LHV, or Maximum Heat Rate Input (QB) divided by fuel LHV.
[6 empty] | V(fuel) | CFH - for gas
29 |  |  |  | Annual Fuel Consumption |  | Annual Fuel | lb/yr | m (fuel) x top,ems unit |  |  | Equal to Max. Fuel Consumption Rate, Line 28, multiplied by Annual Hours of Operation, Line 19.
|  |  |  | (estimate based on selected LHV) |  |  | CF/yr - for gas | V (fuel) x top,ems unit
NOx Removal Performance
30 |  |  |  | Uncontrolled NOx Emission Level |  | NOxin | lb/MMBtu | Data Entry, Line 26. |  |  | Uncontrolled NOx rate entered on Data Entry page, Line 26.
31 |  |  |  | Controlled NOx Outlet (required) |  | NOxout | lb/MMBtu | Data Entry, Line 27. |  |  | Controlled NOx rate, as required by RCSA 22a-174-22e, and listed on Data Entry, Line 27.
32 |  |  |  | Controlled NOx Outlet (selected) |  | NOxout | lb/MMBtu | MAX(NOxout, NOxmin, NOxin - hNOxR x NOxin) |  |  | Determined as the highest among: the required controlled NOxout, the SCR lowest attained NOxout rate, or the NOxout value based on the 90% default efficiency.
33 |  |  |  | NOx Removal Efficiency (selected) |  | h NOx | % | (NOxin - NOx out sel)/NOxin x 100% |  |  | Defined by either eq. (1.10) Ref. 1, § 1.3.1. - Design Parameters for Study-Level Estimates, NOx Removal Efficiency, p1-37 (p37-pdf) or eq. (2.10) Ref. 2, § 2.3.5 - NOx Removal Efficiency, p2-54 (p55-pdf), and determined based on NOxin on Line 30 and NOxout sel, on Line 32.
34 |  |  |  | NOx Removed Hourly Rate |  | NOxR/hr | lb/hr | NOxin x ηNOxR,sel x QB |  |  | Applied the SNCR's eq. (1.12), Ref. 1, §1.3.1 - Design Parameters for Study-Level, NOx Removal Rates, page 1-37 (p37-pdf).
35 |  |  |  | NOx Removed (annually) |  | NOxR | tons | NOxin x hNOxR,sel x QB x top, control / 2000, or NOxin x hNOxR,sel x QB x CFTotal x 8760/2000 |  |  | Defined either by SNCR's eq. (1.11), Ref. 1, §1.3 - Design Parameters for Study-Level, NOx Removal Rates, p1-37 (p37-pdf), or by SCR's eq. (2.11), Ref. 1, §2.3.6 - NOx Removal Rates, p2-54 (p55-pdf).
| II. | Water Specifications Calculations
Flow Rates
36 |  |  |  | Estimated Water Flow Factor/Rate |  | WFR | lb(water)/lb(fuel) | "0.70" - Default |  |  | Bulk average of the WFR data, HPWI control, in Table 6-2, Ref. 4, §6.0 - Control Costs, page 6-211, (p302-pdf).
37 |  |  |  | Water Flow |  | qwater | gpm | ṁ(fuel) lbfuel/hr x 1 hr/60 min x 8.345 lb/gal x WFR lbwater/lbfuel |  |  | Based of Max. Fuel Consumption Rate, lb(fuel)/hr, on Line 28 and WFR, lb(water)/lb (fuel), on Line 36, in gal/min (gpm).
Treatment System Capacity
38 |  |  |  | Design Factor |  | DF |  | "1.30" - Default |  |  | Recommended by a HPWI system supplier, per Table 6-2, footnote [c], Ref. 4, §6.0 - Control Costs, page 6-211, (p302-pdf).
39 |  |  |  | Waste Stream Factor |  | WSF |  | "1.29" - Default |  |  | Factor to account for waste stream, per same reference mentioned at Line 38.
40 |  |  |  | Treatment System Design Capacity |  | Qwater | gpm | DF x WSF x qwater |  |  | Treatment system design capacity is the system water flow increased by the above two multipliers, on Line 38 and Line 39, respectively.
Water Injection Electricity Consumption
41 |  |  |  | Pumping Factor |  | PF | kW/gpm | 0.161 - Default |  |  | Per Ref. 4, pages 6-224, 6-225, (p315-316, pdf), Pumping factor is based on: total pump head H = 200 psig (468 ft), pump efficiency, 60%, electric motor efficiency, 90%, feed water temperature 130ᵒF, water density 61.6 lb/ft³, water standard density 62.4 lb/ft³ (to determine Specific Gravity SG = 61.6/62.4), conversion factor 0.7457 kW equivalent to 1 hp, and 3,960 factor to covert units in feed water, qwater (gpm) and head, H(ft) to hp, hence: 468/3,960 x 61.6/62.4 x 1/0.6 x 0.7457 x 1/0.9 = 0.161.
42 |  |  |  | Power Injection Pump |  | P | kW | PF x qwater |  |  | Determined as water flow (Line 37) multiplied by the pumping factor (Line 41).
43 |  |  |  | Electricity HPWI Consumption |  | E | kWh | P x top, control |  |  | Annual water injection electricity is the injection pump power times the annual HPWI hrs of operation.
Water Injection Fuel Penalty
44 |  |  |  | Fuel Penalty Impact |  | FPpercentage | % | 3.5% - Default |  |  | Per Ref. 4, page 6-223 (p314-pdf), is 3.5 % of Annual Heat Input, at WFR=1, for HPWI.
45 |  |  |  | Fuel Penalty |  | FP | MMBtu/yr | FPpercentage x HI x (WFR/WFR=1) |  |  | Annual fuel penalty, is the reduction percent (FPpercenrage x WFR) of the max. annual heat input, corrected for the actual WFR = 0.7 lbwater/lbfuel.
HPWI COST ESTIMATION
TOTAL CAPITAL COST
| I. | Total Capital Investment (TCI) Estimate
Retrofit Factor
46 |  |  |  | High Pressure Water Injection System |  | RFHPWI |  | Data Entry, Line 32 |  |  | HPWI System Retrofit Factor entered on Data Entry page, Line 32.
HPWI Available Cost Data
47 |  |  |  | HPWI 1990 Investment Cost |  | TCI 1990$ | 1990$ | (43.638 x BMW + 191.14) x 1,000 |  |  | Cost estimate based on a linear variation of HPWI Systems TCI vs. unit nom. plate power capacity, BMW, on Line 15, per data in Table 6-5, Ref. 4, §6.0 - Control Costs, page 6-222, (p313-pdf).
48 |  |  | Total Capital Investment |  |  | TCI2012$ | 2012$ | TCI1990$ x CPI 2012$/1990$ x ELEVF x RFHPWI |  |  | 2012$ HPWI suggested cost is: 1990$ HPWI Cost (TCI1990$, Line 47) x (CPI2012$/1990$, Line 9) x (ELEVF, Line 8) x (RFHPWI, Line 46).
| II. | Annual Costs (adjusted to 2012$)
|  |  | Direct Annual Elements Cost | [7 empty] | Note: Direct Annual Elements Costs estimated below, are determined per Table 6-5, Ref. 4, §6.0 - Control Costs, page 6-222, (p313-pdf).
49 |  |  |  | Annual Maintenance |  | AMC | $/yr | CPI2012$/1990$ x (340 x BMW + 23,000) |  |  | Cost estimate based on a linear variation of HPWI Systems maintenance costs vs. nom. plate power capacity, BMW , per data in Table 6-5, Ref. 4, §6.0 - Control Costs, page 6-222, (p313-pdf).
50 |  |  |  | Annual Electricity |  | AEC | $/yr | E x Costelec [Data Entry, Line 41] |  |  | Water injection electricity annual consumption, on Line 43, times the 2012 kWh cost, listed on Data Entry, Line 41.
51 |  |  |  | Annual Water Cost |  | AWC | $/yr | qwater x 60 min/hr x top, control x WSF x Costwater [Data Entry, Line 41] |  |  | Based on actual water injection flow, qwater (Line 37), control operating time, top,control (Line 3), waste stream factor (suggested by system suppliers), WSF (Line 39) and water 2012$ specific cost, on Data Entry, Line 41, per Table 6-5, Ref. 4, page 6-222, (p313-pdf).
52 |  |  |  | Fuel Penalty Cost |  | FPcost | $/yr | FP x Costfuel |  |  | Fuel penalty, FP (Line45),in MMBtu/hr times fuel specific cost, per EIA 2012$data, Costfuel (Line27).
53 |  |  |  | Water Treatment Cost |  | WTC | $/yr | qwater x 60min/hr x top,control x WSF x WTC$/gal |  |  | Based on actual water injection flow, qwater (Line 37), control operating time, top,control (Line 3), waste stream factor (suggested by system suppliers), WSF (Line 39) and specific costs, water treatment cost, WTC$/gal (Line 10), or water treatment labor cost, WTLC$/gal (Line 11) and water disposal cost, WDC$/gal (Line 12), respectively, per Table 6-5, Ref. 4, page 6-222, (p313-pdf).
54 |  |  |  | Water Treatment Labor Cost |  | WTLC | $/yr | qwaterx 60min/hr x top, control x WSFxWTLC$/gal
55 |  |  |  | Water Disposal Cost |  | WDC | $/yr | qwaterx 60min/hr x top, control x WSF xWDC$/gal
56 |  |  | Direct Annual Cost - DAC |  |  | DAC | $/yr | Σ (Line 49... Line 55) |  |  | Sum of the above direct annual costs, Line 49 through Line 55.
Indirect Annual Cost (IDAC)
57 |  |  |  | Administrative Charges |  | ADM | $/yr | 0.03 x (tcontrol x top,labor x LR + 0.4 x AM) |  |  | Calculated based on the same assumptions proposed for SCR, see eq. (2.69), Ref. 2 §2.4.2. - Total Annual Cost, page 2-78 (p79-pdf).
58 |  |  |  | Capital Recovery |  | CR | $/yr | CRF x TCI |  |  | Calculated based on the same eq. proposed for SCR, see eq. (2.70), Ref. 2, §2.4.2. - Total Annual Cost, page 2-79 (p80-pdf).
59 |  |  |  | Indirect Annual Costs |  | IDAC | $/yr | Σ (Line 57, Line 58) |  |  | Total of the above indirect costs, Line 57 and Line 58.
60 |  |  | Total Annual Cost |  |  | TAC | $/yr | DAC + IDAC |  |  | Total of direct and indirect costs, per eq. (2.72), Ref. 2, §2.4.2. page 2-79 (p80-pdf).
61 | III. | NOx Removal per year |  |  |  | NOxR | tons | NOxR [Line 35] |  |  | Tons of NOx removed calculated above, on Line 35.
| IV. | Control Cost Effectiveness
62 |  | Base Year | [5 empty] | Data Entry, Line 37 "2012$" - Default |  |  | Data Entry, Line 36 - Selected base year of EPA's cost analysis.
63 |  |  | Cost Effectiveness |  |  | Costeffect,$2012 | 2012$/ton NOxR | TAC / NOxR |  |  | Control cost effectiveness based on TAC divided by the annual tons of NOx removed, per eq. (1.57), Ref. 1 § 1.4.2 - Total Annual Costs, page 1-57 (p57-pdf) or per eq. (2.73), Ref. 2, §2.4.2. page 2-79 (p80-pdf).
64 |  | Year Control is effective | [5 empty] | Data Entry, Line 28 |  |  | Year control is effective (or current year), as entered on Data Entry, Line 28.
65 |  |  | Cost Effectiveness |  |  | Costeffect,yr | $/ton NOxR | Costeffect,$2012 x CPI(current yr) |  |  | Control cost effectiveness adjusted for the year control is effective (or current year).