## NOx - SCR-More 95th
Variable | Designation | Units |  | Calculation
Unique ID |  |  | Bridgeport
Plant |  |  | Bridgeport
Unit |  |  | 3
Unit Size | A | MW | 410
Gross Heat Rate | C | Btu/kwhr | 10000
NOx Rate | D | lb/MMBtu | 0.157 | 95th percentile 2012-mid 2015
CF | J | CF | 1 | Assumed, per regulation
Type of Coal | F |  | LowS
Coal Factor | G |  | 1.05 | Bit=1; PRB (low S)=1.05; Lig=1.07
Retrofit Factor | B |  | 1 | 1 = typical retrofit
HR Factor | H |  | 1 | C/10000
Heat Input | I | Btu/hr | 4100000000 | A*C*1000
CF | J |  | 1
NOx Removal Eff | K | % | 51.8% | Calculation, per modeling
NOx Removal factor | L |  | 0.6475 | equals K/80% based upon 8/10/12 email from Sargent & Lundy, and See pdf pg 10/79 at http://www.epa.gov/airmarkets/progsregs/epa-ipm/docs/SuppDoc410MATS.pdf
NOx Removed | M | lb/hr | 333.4366 | D*I/10^6*K
Urea rate (100%) | N | lb/hr | 232.9443 | M*0.525*60/46*1.01/.99
Steam Required | O | lb/hr | 263.2271 | N*1.13
Aux. Power | P | % | 0.57187 | 0.56*(G*H)^0.43
Urea Cost (50% sol) | R | $/ton | 400 |  | http://www.epa.gov/airmarkets/progsregs/epa-ipm/BaseCasev410.html#documentation
Catalyst Cost | S | $/m3 | 8000
Aux Power Cost | T | $/kwh | 0.06
Steam Cost | U | $/Klb | 4
Operating Labor Rate | V | $/hr | 60 | Total Labor Cost
Capital Cost Calculation (includes equipment, installation, buildings, foundations,electrical, minor physical/chemical ww treatment and retrofit difficulty)
BMR ($) = | SCR |  | 43729625.9946
BMF ($) = | base reagent preparation cost |  | 1752012.3933
BMA ($) = | APH (SO@> 3lb/Mmbtu)
BMB ($) = | fans/aux power |  | 4853469.6929
BM ($) = | Total base cost |  | 50335108.0808
BM ($/KW) = |  |  | 122.7686
Total Project Cost
A1 = 10% of BM ($) = | Eng. and Construction management |  | 5033510.8081
A2 = 10% of BM ($) = | Labor adjustment |  | 5033510.8081
A3 = 10% of BM ($) = | Contractor profit/fees |  | 5033510.8081
CECC ($) = | Cap., Eng. and management |  | 65435640.5051
CECC ($/kw) = |  |  | 159.5991
B1 = 5% of CECC | owners cost |  | 3271782.0253
B2 = 6% of CECC + B1 | AFUDC (2yr cycle) |  | 7197920.4556
TPC ($) = | Total project cost |  | 75905342.9859
TPC ($/kw) = |  |  | 185.135
Fixed O&M Cost
FOMO ($/kw-yr) = | fixed O&M - additional labor cost |  | 0.1522
FOMM ($/kw-yr) = | fixed O&M - additional maintenace, mtl and labor cost |  | 0.73171
FOM ($/kw-yr) = | Total Fixed O&M Cost |  | 0.8839
Variable O&M Cost
VOMR ($/MWhr) = | Variable O&M - urea |  | 0.22726
VOMW ($/MWhr) = | Variable O&M - catalyst disposal |  | 0.23181 | See pdf pg 10/79 at http://www.epa.gov/airmarkets/progsregs/epa-ipm/docs/SuppDoc410MATS.pdf
VOMP ($/MWhr)= | Variable O&M Power |  | 0.34312 | This is not included in the S&L calculations, but should be
VOMM ($/MWhr) = | Variable O&M - steam |  | 0.0025681
VOM ($/MWhr) = | Total Variable O&M Cost |  | 0.80477
CR = |  |  | 0.0944 | [i=7%, n=20]
Property Taxes and Insurance |  |  | 0.012 | [Insurance = 0.3%, Tax = 0.9%]
Total Charge Rate |  |  | 10.64%
Cost of control - $/Ton
CF |  |  | 100%
Control Efficiency |  |  | 51.8%
Uncontrolled Rate | (lb/Mbtu*Heat Input)/1000000
NOx Rate (lb/hr) | Lb/hr*8760*CF/2000 |  | 643.7
NOx Rate (lb/MMBtu) |  |  | 0.157
NOx (TPY) |  |  | 2819.406
Controlled Rate
NOx Rate (lb/hr) |  |  | 310.2634
NOx Rate (lb/MMBtu) | TPC*CR+(FOM*MW)+VOM(MW*8760)*CF |  | 0.075674 | [95th percentile, per modeling]
NOx (TPY) |  |  | 1358.9537
Tons/Year Removed |  |  | 1460.4523
Total Cost/year |  |  | 11329128.7184
$/Ton |  |  | 7757.274

## NOx - SCR-More 50th
Variable | Designation | Units |  | Calculation
Unique ID |  |  | Bridgeport
Plant |  |  | Bridgeport
Unit |  |  | 3
Unit Size | A | MW | 410
Gross Heat Rate | C | Btu/kwhr | 10000
NOx Rate | D | lb/MMBtu | 0.135 | 50th percentile 2012-mid 2015
CF | J | CF | 1 | Assumed, per regulation
Type of Coal | F |  | LowS
Coal Factor | G |  | 1.05 | Bit=1; PRB (low S)=1.05; Lig=1.07
Retrofit Factor | B |  | 1 | 1 = typical retrofit | 0.8963
HR Factor | H |  | 1 | C/10000
Heat Input | I | Btu/hr | 4100000000 | A*C*1000
CF | J |  | 1
NOx Removal Eff | K | % | 89.6% | Calculation, per modeling
NOx Removal factor | L |  | 1.12 | equals K/80% based upon 8/10/12 email from Sargent & Lundy, and See pdf pg 10/79 at http://www.epa.gov/airmarkets/progsregs/epa-ipm/docs/SuppDoc410MATS.pdf
NOx Removed | M | lb/hr | 495.936 | D*I/10^6*K
Urea rate (100%) | N | lb/hr | 346.4691 | M*0.525*60/46*1.01/.99
Steam Required | O | lb/hr | 391.5101 | N*1.13
Aux. Power | P | % | 0.57187 | 0.56*(G*H)^0.43
Urea Cost (50% sol) | R | $/ton | 400 |  |  | http://www.epa.gov/airmarkets/progsregs/epa-ipm/BaseCasev410.html#documentation
Catalyst Cost | S | $/m3 | 8000
Aux Power Cost | T | $/kwh | 0.06
Steam Cost | U | $/Klb | 4
Operating Labor Rate | V | $/hr | 60 | Total Labor Cost
Capital Cost Calculation (includes equipment, installation, buildings, foundations,electrical, minor physical/chemical ww treatment and retrofit difficulty)
BMR ($) = | SCR |  | 48794560.7657
BMF ($) = | base reagent preparation cost |  | 1934818.6521
BMA ($) = | APH (SO@> 3lb/Mmbtu)
BMB ($) = | fans/aux power |  | 4853469.6929
BM ($) = | Total base cost |  | 55582849.1107
BM ($/KW) = |  |  | 135.5679
Total Project Cost
A1 = 10% of BM ($) = | Eng. and Construction management |  | 5558284.9111
A2 = 10% of BM ($) = | Labor adjustment |  | 5558284.9111
A3 = 10% of BM ($) = | Contractor profit/fees |  | 5558284.9111
CECC ($) = | Cap., Eng. and management |  | 72257703.8439
CECC ($/kw) = |  |  | 176.2383
B1 = 5% of CECC | owners cost |  | 3612885.1922
B2 = 6% of CECC + B1 | AFUDC (2yr cycle) |  | 7948347.4228
TPC ($) = | Total project cost |  | 83818936.4589
TPC ($/kw) = |  |  | 204.4364
Fixed O&M Cost
FOMO ($/kw-yr) = | fixed O&M - additional labor cost |  | 0.1522
FOMM ($/kw-yr) = | fixed O&M - additional maintenace, mtl and labor cost |  | 0.73171
FOM ($/kw-yr) = | Total Fixed O&M Cost |  | 0.8839
Variable O&M Cost
VOMR ($/MWhr) = | Variable O&M - urea |  | 0.33802
VOMW ($/MWhr) = | Variable O&M - catalyst disposal |  | 0.34206 | See pdf pg 10/79 at http://www.epa.gov/airmarkets/progsregs/epa-ipm/docs/SuppDoc410MATS.pdf
VOMP ($/MWhr)= | Variable O&M Power |  | 0.34312 | This is not included in the S&L calculations, but should be
VOMM ($/MWhr) = | Variable O&M - steam |  | 0.0038196
VOM ($/MWhr) = | Total Variable O&M Cost |  | 1.027
CR = |  |  | 0.0944 | [i=7%, n=20]
Property Taxes and Insurance |  |  | 0.012 | [Insurance = 0.3%, Tax = 0.9%]
Total Charge Rate |  |  | 10.64%
Cost of control - $/Ton
CF |  |  | 100%
Control Efficiency |  |  | 89.6%
Uncontrolled Rate | (lb/Mbtu*Heat Input)/1000000
NOx Rate (lb/hr) | Lb/hr*8760*CF/2000 |  | 553.5
NOx Rate (lb/MMBtu) |  |  | 0.135
NOx (TPY) |  |  | 2424.33
Controlled Rate
NOx Rate (lb/hr) |  |  | 57.564
NOx Rate (lb/MMBtu) | TPC*CR+(FOM*MW)+VOM(MW*8760)*CF |  | 0.01404 | [50th percentile, per modeling]
NOx (TPY) |  |  | 252.1303
Tons/Year Removed |  |  | 2172.1997
Total Cost/year |  |  | 12969382.8821
$/Ton |  |  | 5970.6219

## NOx - SCR-Less 95th
Variable | Designation | Units |  | Calculation
Unique ID |  |  | Bridgeport
Plant |  |  | Bridgeport
Unit |  |  | 3
Unit Size | A | MW | 410
Gross Heat Rate | C | Btu/kwhr | 10000
NOx Rate | D | lb/MMBtu | 0.157 | 95th percentile 2012-mid 2015
CF | J | CF | 1 | Assumed, per regulation
Type of Coal | F |  | LowS
Coal Factor | G |  | 1.05 | Bit=1; PRB (low S)=1.05; Lig=1.07
Retrofit Factor | B |  | 1 | 1 = typical retrofit
HR Factor | H |  | 1 | C/10000
Heat Input | I | Btu/hr | 4100000000 | A*C*1000
CF | J |  | 1
NOx Removal Eff | K | % | 36.65% | Calculation, per modeling
NOx Removal factor | L |  | 0.45812 | equals K/80% based upon 8/10/12 email from Sargent & Lundy, and See pdf pg 10/79 at http://www.epa.gov/airmarkets/progsregs/epa-ipm/docs/SuppDoc410MATS.pdf
NOx Removed | M | lb/hr | 235.9161 | D*I/10^6*K
Urea rate (100%) | N | lb/hr | 164.8149 | M*0.525*60/46*1.01/.99
Steam Required | O | lb/hr | 186.2408 | N*1.13
Aux. Power | P | % | 0.57187 | 0.56*(G*H)^0.43
Urea Cost (50% sol) | R | $/ton | 400 |  | http://www.epa.gov/airmarkets/progsregs/epa-ipm/BaseCasev410.html#documentation
Catalyst Cost | S | $/m3 | 8000
Aux Power Cost | T | $/kwh | 0.06
Steam Cost | U | $/Klb | 4
Operating Labor Rate | V | $/hr | 60 | Total Labor Cost
Capital Cost Calculation (includes equipment, installation, buildings, foundations,electrical, minor physical/chemical ww treatment and retrofit difficulty)
BMR ($) = | SCR |  | 40806054.6465
BMF ($) = | base reagent preparation cost |  | 1606842.1992
BMA ($) = | APH (SO@> 3lb/Mmbtu)
BMB ($) = | fans/aux power |  | 4853469.6929
BM ($) = | Total base cost |  | 47266366.5386
BM ($/KW) = |  |  | 115.2838
Total Project Cost
A1 = 10% of BM ($) = | Eng. and Construction management |  | 4726636.6539
A2 = 10% of BM ($) = | Labor adjustment |  | 4726636.6539
A3 = 10% of BM ($) = | Contractor profit/fees |  | 4726636.6539
CECC ($) = | Cap., Eng. and management |  | 61446276.5002
CECC ($/kw) = |  |  | 149.869
B1 = 5% of CECC | owners cost |  | 3072313.825
B2 = 6% of CECC + B1 | AFUDC (2yr cycle) |  | 6759090.415
TPC ($) = | Total project cost |  | 71277680.7402
TPC ($/kw) = |  |  | 173.848
Fixed O&M Cost
FOMO ($/kw-yr) = | fixed O&M - additional labor cost |  | 0.1522
FOMM ($/kw-yr) = | fixed O&M - additional maintenace, mtl and labor cost |  | 0.73171
FOM ($/kw-yr) = | Total Fixed O&M Cost |  | 0.8839
Variable O&M Cost
VOMR ($/MWhr) = | Variable O&M - urea |  | 0.16079
VOMW ($/MWhr) = | Variable O&M - catalyst disposal |  | 0.18132 | See pdf pg 10/79 at http://www.epa.gov/airmarkets/progsregs/epa-ipm/docs/SuppDoc410MATS.pdf
VOMP ($/MWhr)= | Variable O&M Power |  | 0.34312 | This is not included in the S&L calculations, but should be
VOMM ($/MWhr) = | Variable O&M - steam |  | 0.001817
VOM ($/MWhr) = | Total Variable O&M Cost |  | 0.68706
CR = |  |  | 0.0944 | [i=7%, n=20]
Property Taxes and Insurance |  |  | 0.012 | [Insurance = 0.3%, Tax = 0.9%]
Total Charge Rate |  |  | 10.64%
Cost of control - $/Ton
CF |  |  | 100%
Control Efficiency |  |  | 36.65%
Uncontrolled Rate | (lb/Mbtu*Heat Input)/1000000
NOx Rate (lb/hr) | Lb/hr*8760*CF/2000 |  | 643.7
NOx Rate (lb/MMBtu) |  |  | 0.157
NOx (TPY) |  |  | 2819.406
Controlled Rate
NOx Rate (lb/hr) |  |  | 407.784
NOx Rate (lb/MMBtu) | TPC*CR+(FOM*MW)+VOM(MW*8760)*CF |  | 0.099459 | [95th percentile, per modeling]
NOx (TPY) |  |  | 1786.0937
Tons/Year Removed |  |  | 1033.3123
Total Cost/year |  |  | 10413987.8233
$/Ton |  |  | 10078.2579

## NOx - SCR-Less 50th
Variable | Designation | Units |  | Calculation
Unique ID |  |  | Bridgeport
Plant |  |  | Bridgeport
Unit |  |  | 3
Unit Size | A | MW | 410
Gross Heat Rate | C | Btu/kwhr | 10000
NOx Rate | D | lb/MMBtu | 0.135 | 50th percentile 2012-mid 2015
CF | J | CF | 1 | Assumed, per regulation
Type of Coal | F |  | LowS
Coal Factor | G |  | 1.05 | Bit=1; PRB (low S)=1.05; Lig=1.07
Retrofit Factor | B |  | 1 | 1 = typical retrofit
HR Factor | H |  | 1 | C/10000
Heat Input | I | Btu/hr | 4100000000 | A*C*1000
CF | J |  | 1
NOx Removal Eff | K | % | 74.07% | Calculation, per modeling | 0.74074
NOx Removal factor | L |  | 0.92588 | equals K/80% based upon 8/10/12 email from Sargent & Lundy, and See pdf pg 10/79 at http://www.epa.gov/airmarkets/progsregs/epa-ipm/docs/SuppDoc410MATS.pdf
NOx Removed | M | lb/hr | 409.9775 | D*I/10^6*K
Urea rate (100%) | N | lb/hr | 286.4171 | M*0.525*60/46*1.01/.99
Steam Required | O | lb/hr | 323.6513 | N*1.13
Aux. Power | P | % | 0.57187 | 0.56*(G*H)^0.43
Urea Cost (50% sol) | R | $/ton | 400 |  |  | http://www.epa.gov/airmarkets/progsregs/epa-ipm/BaseCasev410.html#documentation
Catalyst Cost | S | $/m3 | 8000
Aux Power Cost | T | $/kwh | 0.06
Steam Cost | U | $/Klb | 4
Operating Labor Rate | V | $/hr | 60 | Total Labor Cost
Capital Cost Calculation (includes equipment, installation, buildings, foundations,electrical, minor physical/chemical ww treatment and retrofit difficulty)
BMR ($) = | SCR |  | 46971916.4761
BMF ($) = | base reagent preparation cost |  | 1844904.3259
BMA ($) = | APH (SO@> 3lb/Mmbtu)
BMB ($) = | fans/aux power |  | 4853469.6929
BM ($) = | Total base cost |  | 53670290.4948
BM ($/KW) = |  |  | 130.9031
Total Project Cost
A1 = 10% of BM ($) = | Eng. and Construction management |  | 5367029.0495
A2 = 10% of BM ($) = | Labor adjustment |  | 5367029.0495
A3 = 10% of BM ($) = | Contractor profit/fees |  | 5367029.0495
CECC ($) = | Cap., Eng. and management |  | 69771377.6433
CECC ($/kw) = |  |  | 170.1741
B1 = 5% of CECC | owners cost |  | 3488568.8822
B2 = 6% of CECC + B1 | AFUDC (2yr cycle) |  | 7674851.5408
TPC ($) = | Total project cost |  | 80934798.0662
TPC ($/kw) = |  |  | 197.4019
Fixed O&M Cost
FOMO ($/kw-yr) = | fixed O&M - additional labor cost |  | 0.1522
FOMM ($/kw-yr) = | fixed O&M - additional maintenace, mtl and labor cost |  | 0.73171
FOM ($/kw-yr) = | Total Fixed O&M Cost |  | 0.8839
Variable O&M Cost
VOMR ($/MWhr) = | Variable O&M - urea |  | 0.27943
VOMW ($/MWhr) = | Variable O&M - catalyst disposal |  | 0.29882 | See pdf pg 10/79 at http://www.epa.gov/airmarkets/progsregs/epa-ipm/docs/SuppDoc410MATS.pdf
VOMP ($/MWhr)= | Variable O&M Power |  | 0.34312 | This is not included in the S&L calculations, but should be
VOMM ($/MWhr) = | Variable O&M - steam |  | 0.0031576
VOM ($/MWhr) = | Total Variable O&M Cost |  | 0.92453
CR = |  |  | 0.0944 | [i=7%, n=20]
Property Taxes and Insurance |  |  | 0.012 | [Insurance = 0.3%, Tax = 0.9%]
Total Charge Rate |  |  | 10.64%
Cost of control - $/Ton
CF |  |  | 100%
Control Efficiency |  |  | 74.07%
Uncontrolled Rate | (lb/Mbtu*Heat Input)/1000000
NOx Rate (lb/hr) | Lb/hr*8760*CF/2000 |  | 553.5
NOx Rate (lb/MMBtu) |  |  | 0.135
NOx (TPY) |  |  | 2424.33
Controlled Rate
NOx Rate (lb/hr) |  |  | 143.5225
NOx Rate (lb/MMBtu) | TPC*CR+(FOM*MW)+VOM(MW*8760)*CF |  | 0.035006 | [50th percentile, per modeling]
NOx (TPY) |  |  | 628.6288
Tons/Year Removed |  |  | 1795.7012
Total Cost/year |  |  | 12294410.0633
$/Ton |  |  | 6846.5788