## SSO SUMMARY
The first two sections count the number of events and volume amounts for each type of Sanitary Sewer Overflow (SSO) for each municipality and in total | [28 empty] | This secion keeps track of the approximate gallons spilled from SSOs by municipality - a combined total of CSOs and SSOs is on the Reached Water Summary Tab
THIS IS 2025 DATA SUMMARIZED FOR THE 2026 REPORT
Municipality | # of SSO Events | # of NPDES Permitted Bypasses | # ot TOTAL EVENTS | All Events Total Estimated Gallons | # Reached Water | # Excessive Flows - Storm Event | Volume (gallons) Excessive Flows - Storm Event | # Electrical Equipment Failure | Volume (gallons) Eletrical Equipt Failure | # Mechanical Equipment Failure | Volume (gallons) Mech Equipt Failure | # Other - Sewer Break, Crack or Failure | Volume (gallons) Other - Sewer Break, Crack or Failure | # Other - Contractor or Operator Error or other mechanical | Volume (gallons) Other - Contractoror Operator error or other mechanical | # Sewer Line Blockage - Grease | Volume (gallons) Line Blockage - Grease | # Sewer Line Blockage - Rags | Volume (gallons) Line Blockage - Rags | # Sewer Line Blockage - Roots | Volume (gallons) Line Blockage - Roots | # Sewer Line Blockage - Debris (Bricks, Carts,Silt, etc) | Volume (gallons) Line Bolckage - Debris (Bricks, Carts, Silt, etc) | # Sewer Line Blockage - Other | Volume (gallons) Link Bolckage - Other | # Unknown Cause | Volume (gallons) Unknown Cause | Unnamed Waterbody (gallons) | Ash Creek (gallons) | Beaver Brook (gallons) | Betts Brook (gallons) | Bridgeport Harbor / LIS (gallons) | Bruce Brook (gallons) | Byram River (gallons) | Cedar Creek / LIS (gallons) | Connecticut River (gallons) | Cove River (gallons) | Eugene Pond (gallons) | Farmington River (gallons) | Folly Brook Dike (gallons) | Goodwives River (gallons) | Great Swamp (gallons) | Greenwich Cove / Harbor (gallons0 | Gulfstream (gallons) | Gully Brook Conduit (gallons) | Housatonic River (gallons) | Island Brook (gallons) | Keeler Brook (gallons) | Lake Forest Creek (gallons) | Lake Phipps (gallons) | Lake Wackawana (gallons) | Long Island Sound (gallons) | Mad River (gallons) | Mill Brook (gallons) | Mill River (gallons) | Mohegan Brook (gallons) | Moosup River (gallons) | Muddy Gutter Brook (gallons) | Naugatuck River (gallons) | New Haven Harbor (gallons) | Norwalk River (gallons) | Old Field Creek (gallons) | Park River (incl N, S & Conduit) (gallons) | Paulk Hill Brook (gallons) | Pequabuck River (gallons) | Pequannock River (gallons) | Pine Marsh Creek (gallons) | Piper Brook (gallons) | Pomperug River (gallons) | Quinnipiac River (gallons) | Radey Pond (gallons) | Rawlins Brook (gallons) | Rooster River (gallons) | Scantic River (gallons) | Shaw Cove (gallons) | Shetucket River (gallons) | Stamford Harbor East Branch (gallons) | Thames River (gallons) | Tom Brook (gallons) | Trout Brook (gallons) | Troy Brook (gallons) | Two-Mile Brook (gallons) | Union Pond (gallons) | West River (gallons) | Willimantic River (gallons) | Yantic & Yantic West River (gallons) | Yellow Mill Channel (gallons)
Ansonia | 4 | 0 | 4 | 41000 | 2 |  |  |  |  | 4 | 41000 | [70 empty] | 11000
Beacon Falls | 1 | 0 | 1 | 25 | 0 | [16 empty] | 1 | 25
Berlin | 1 | 0 | 1 | 30000 | 0 | [6 empty] | 1 | 30000
Bloomfield (MDC) | 1 | 0 | 1 | 0 | 0 | [8 empty] | 1 | 0
Branford | 1 | 0 | 1 | 30 | 0 | [10 empty] | 1 | 30
Bridgeport | 28 | 16 | 44 | 68160520 | 7 | 16 | 68140000 | [6 empty] | 1 | 500 | 20 | 19070 | 3 | 620 |  |  | 1 | 100 | 2 | 130 | 1 | 100 |  | 500 |  |  | 17890000 | 950 |  | 47250000 | [11 empty] | 500 |  | 500 | [16 empty] | 10020 | [6 empty] | 6000 | [13 empty] | 100
Bristol | 7 | 0 | 7 | 84505 | 2 | [10 empty] | 1 | 50 | 3 | 7450 | 1 | 5 |  |  |  |  | 2 | 77000 | [37 empty] | 77000
Brookfield | 2 | 0 | 2 | 50500 | 0 | [6 empty] | 1 | 10500 | [12 empty] | 1 | 40000
Canton | 1 | 0 | 1 | 950 | 0 | [10 empty] | 1 | 950
Cheshire | 1 | 0 | 1 | 2000 | 1 | [10 empty] | 1 | 2000 | [52 empty] | 2000
Cromwell (Mattabassett) | 3 | 0 | 3 | 2172888 | 3 | 3 | 2172888 | [28 empty] | 2172888
Danbury | 3 | 0 | 3 | 1600 | 1 | [10 empty] | 1 | 1000 | 2 | 600 | [31 empty] | 100
Darien | 2 | 0 | 2 | 150 | 1 | [6 empty] | 1 | 60 | [12 empty] | 1 | 90 | [13 empty] | 90
Derby | 3 | 0 | 3 | 2833030 | 2 |  |  | 1 | 583000 | [6 empty] | 1 | 30 | [8 empty] | 1 | 2250000 | [18 empty] | 2833000
East Hampton | 2 | 0 | 2 | 10950 | 1 | [6 empty] | 1 | 9750 | [12 empty] | 1 | 1200 | [30 empty] | 1200
East Hartford (MDC) | 3 | 0 | 3 | 300 | 0 | [10 empty] | 2 | 200 |  |  |  |  | 1 | 100
East Haven (GNHWPCA) | 2 | 0 | 2 | 108 | 0 | [10 empty] | 2 | 108
East Windsor | 1 | 0 | 1 | 380000 | 1 | [20 empty] | 1 | 380000 | [8 empty] | 380000
Enfield | 1 | 0 | 1 | 33000 | 1 | [6 empty] | 1 | 33000 | [60 empty] | 33000
Fairfield | 2 | 0 | 2 | 1650 | 2 | [8 empty] | 1 | 1500 |  |  | 1 | 150 | [32 empty] | 1500 | [14 empty] | 150
Farmington | 1 | 0 | 1 | 4500 | 0 | [6 empty] | 1 | 4500
Glastonbury | 2 | 0 | 2 | 525 | 0 | [10 empty] | 1 | 25 |  |  | 1 | 500
Griswold (Jewett City) | 1 | 0 | 1 | 5 | 0 |  |  | 1 | 5
Greenwich | 3 | 0 | 3 | 7600 | 3 | [6 empty] | 2 | 5500 | [12 empty] | 1 | 2100 | 2100 | [5 empty] | 3000 | [8 empty] | 2500
Groton | 6 | 0 | 6 | 305 | 3 |  |  |  |  | 2 | 40 | 1 | 5 |  |  | 1 | 100 |  |  |  |  | 2 | 160 | [54 empty] | 45
Hamden (GNHWPCA) | 4 | 0 | 4 | 729 | 1 | [6 empty] | 1 | 300 |  |  | 2 | 54 | 1 | 375 | [35 empty] | 300
Hartford (MDC) | 12 | 52 | 64 | 612306750 | 57 | 53 | 612290090 |  |  |  |  | 2 | 1900 |  |  | 1 | 800 |  |  |  |  | 3 | 9790 | 4 | 1170 | 1 | 3000 | [8 empty] | 612297700 |  |  |  | 900 |  |  |  |  | 3000 | [17 empty] | 2800
Harwinton | 1 | 0 | 1 | 100 | 0 | [8 empty] | 1 | 100
Killingly | 2 | 0 | 2 | 170 | 0 |  |  |  |  | 1 | 120 | [6 empty] | 1 | 50
Lisbon | 1 | 0 | 1 | 1000 | 0 | [6 empty] | 1 | 1000
Manchester | 5 | 0 | 5 | 4800 | 1 | [12 empty] | 3 | 4000 | 1 | 500 |  |  |  |  | 1 | 300 | [55 empty] | 500
Meriden | 1 | 0 | 1 | 75 | 0 | [10 empty] | 1 | 75
Milford | 3 | 0 | 3 | 170 | 0 | [10 empty] | 1 | 100 |  |  | 2 | 70
Montville | 4 | 0 | 4 | 950 | 1 |  |  |  |  | 1 | 200 | 2 | 500 |  |  |  |  | 1 | 250 | [36 empty] | 200
Naugatuck | 4 | 0 | 4 | 16500310 | 2 | 1 | 10500000 | 1 | 6000000 |  |  |  |  | 1 | 10 | [6 empty] | 1 | 300 | [35 empty] | 16500000
New Britain | 3 | 0 | 3 | 2090 | 0 | [10 empty] | 2 | 590 | 1 | 1500
New Haven (GNHWPCA) | 8 | 44 | 52 | 100791323 | 44 | 44 | 100789200 |  |  |  |  | 1 | 75 |  |  | 4 | 1869 |  |  |  |  | 1 | 90 | 1 | 19 | 1 | 70 | [32 empty] | 100789200
New London | 2 | 0 | 2 | 673970 | 1 | [8 empty] | 1 | 50 | 1 | 673920 | [57 empty] | 673920
New Milford | 1 | 0 | 1 | 500 | 0 | [10 empty] | 1 | 500
Newtown | 1 | 0 | 1 | 500 | 1 | [8 empty] | 1 | 500 | [63 empty] | 500
North Haven | 4 | 0 | 4 | 1895 | 0 | [6 empty] | 1 | 500 | 1 | 450 | 1 | 900 |  |  | 1 | 45
Norwalk | 6 | 0 | 6 | 50266 | 5 |  |  |  |  | 1 | 48800 | 2 | 971 | 1 | 200 | 1 | 110 | 1 | 185 | [11 empty] | 110 | [16 empty] | 48800 | [12 empty] | 1156
Norwich | 15 | 0 | 15 | 1661946 | 7 | 1 | 500 |  |  | 1 | 0 | 4 | 1552886 | 3 | 107342 | 1 | 200 | 4 | 800 | [6 empty] | 1 | 218 | [48 empty] | 940833 |  | 54600 | [7 empty] | 665513
Orange | 6 | 0 | 6 | 2365 | 0 |  |  |  |  | 1 | 45 | 2 | 1350 |  |  |  |  | 1 | 20 |  |  | 1 | 500 | 1 | 450
Plainfield | 7 | 0 | 7 | 2310 | 2 |  |  | 2 | 1000 | [6 empty] | 2 | 110 | 1 | 50 |  |  | 1 | 850 | 1 | 300 | [28 empty] | 500 |  |  | 500
Plymouth | 4 | 0 | 4 | 310 | 1 | [10 empty] | 1 | 200 | 2 | 60 | [6 empty] | 1 | 50 | [10 empty] | 50
Ridgefield | 1 | 0 | 1 | 2500 | 1 | [6 empty] | 1 | 2500 | [28 empty] | 2500
Rocky Hill (MDC) | 1 | 0 | 1 | 90 | 0 | [6 empty] | 1 | 90
Seymour | 1 | 0 | 1 | 1 | 0 | [20 empty] | 1 | 1
Shelton | 3 | 0 | 3 | 750 | 0 | [10 empty] | 1 | 250 |  |  |  |  | 2 | 500
Simsbury | 4 | 0 | 4 | 1190 | 1 | 1 | 250 | [10 empty] | 1 | 15 |  |  |  |  | 2 | 925 | [13 empty] | 900
South Windsor | 4 | 0 | 4 | 2397 | 3 |  |  | 1 | 520 | 1 | 777 | [12 empty] | 2 | 1100 | [10 empty] | 2397
Southbury | 2 | 0 | 2 | 2170 | 1 | [10 empty] | 2 | 2170 | [51 empty] | 1920
Southington | 2 | 0 | 2 | 27 | 0 | [6 empty] | 1 | 2 |  |  |  |  | 1 | 25
Stafford | 1 | 0 | 1 | 10000 | 1 |  |  |  |  | 1 | 10000 | [73 empty] | 10000
Stamford | 3 | 0 | 3 | 7596 | 1 |  |  | 1 | 7291 | 1 | 300 | [12 empty] | 1 | 5 | [51 empty] | 7291
Stonington | 1 | 0 | 1 | 9 | 0 | [18 empty] | 1 | 9
Suffield | 1 | 0 | 1 | 750 | 1 |  |  |  |  | 1 | 750 | [60 empty] | 750
Thomaston | 1 | 0 | 1 | 500 | 0 | [6 empty] | 1 | 500
Tolland | 1 | 0 | 1 | 200 | 1 | [6 empty] | 1 | 200 | [50 empty] | 200
Torrington | 4 | 0 | 4 | 3100 | 2 | [12 empty] | 2 | 800 | [6 empty] | 2 | 2300 | [16 empty] | 500 | [36 empty] | 300
Trumbull | 2 | 0 | 2 | 95 | 0 | [6 empty] | 2 | 95
Waterbury | 5 | 0 | 5 | 2105 | 3 |  |  | 1 | 25 | [6 empty] | 1 | 50 |  |  | 1 | 30 | 1 | 1250 |  |  | 1 | 750 |  |  | 1250 | [22 empty] | 800
Waterford | 1 | 0 | 1 | 100 | 0 | [6 empty] | 1 | 100
West Hartford | 22 | 0 | 22 | 36063520 | 14 | 15 | 36038980 | [6 empty] | 1 | 90 | 5 | 24360 | [8 empty] | 1 | 90 | [40 empty] | 21208000 | [11 empty] | 14854800
West Haven | 7 | 0 | 7 | 645 | 4 |  |  |  |  | 1 | 100 | 1 | 65 |  |  | 4 | 380 | [6 empty] | 1 | 100 | [11 empty] | 80 | [12 empty] | 100 | [11 empty] | 100 | [21 empty] | 65
Windsor (MDC) | 3 | 0 | 3 | 25180 | 1 |  |  |  |  | 1 | 25000 |  |  |  |  | 2 | 180 | [21 empty] | 25000
Windsor Locks | 1 | 0 | 1 | 3600 | 0 | [16 empty] | 1 | 3600
Woodbury | 1 | 0 | 1 | 30000 | 1 | [14 empty] | 1 | 30000 | [49 empty] | 30000
Woodridge (GNHWPCA) | 1 | 0 | 1 | 30000 | 0 |  |  |  |  | 1 | 30000
SUMMARY | 249 | 112 | 361 | 842005195 | 188 | 134 | 829931908 | 8 | 6591841 | 18 | 157132 | 34 | 1656349 | 13 | 110742 | 66 | 730381 | 29 | 16950 | 8 | 31150 | 16 | 17265 | 16 | 4208 | 19 | 2757269 | 2100 | 500 | 1250 | 110 | 17890000 | 950 | 3000 | 47250000 | 614852985 | 80 | 50 | 25900 | 900 | 90 | 2500 | 2500 | 500 | 3000 | 2833000 | 500 | 48800 | 500 | 100 | 100 | 1500 | 800 | 500 | 300 | 200 | 500 | 1200 | 16500000 | 100789200 | 1156 | 100 | 2800 | 200 | 77000 | 10020 | 150 | 21208000 | 1920 | 2000 | 30000 | 750 | 6000 | 33000 | 673920 | 940833 | 7291 | 54645 | 500 | 14854800 | 300 | 11000 | 500 | 65 | 10000 | 665513 | 100
[7 empty] | Event Count | 361
[7 empty] | Gallons Count | 842005195
[29 empty] | TOTAL REACHED WATER: |  | 838806178
Data Caveats
While DEEP is the storehouse for the SRTK data, DEEP makes the following caveats:
· All data is submitted by publicly owned wastewater treatment plants and publicly owned satellite collection systems.
· DEEP does not issue notifications about individual discharges, they are inputted by the reporters for each municipality and issued by the electronic system automatically.
· The reports are being submitted by the municipalities in a short time frame after discovery of a discharge and specific details may not be known.
· Data is estimated based on the existing systems, models, and personal knowledge of the sewer systems by the reporters.
· Data quality, especially volumes, is not checked by DEEP.
· The electronic program allows for zero duration, short durations and zero quantities for volumes.
· Addresses may not be entered by municipalities in a way that allows the parts of the address to be separated nor with an exact location.
· Multiple notifications may be sent for the same discharge since municipalities need to submit daily and termination reports for ongoing discharges.
· Duplicate reports and reports submitted that resulted in zero flow may be rescinded in the system.

## Ansonia
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
ANSONIA | Closed | Sewage Bypass | Dry | 2025-01-15 | 12:45 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Submersible pump not functioning due to tripping out under high amperage and overheating. | autodialer from pump station | 10,000+ gallons totalStill intermittently bypassing while vac trucks are working to keep up with flow. Meanwhile, a pump station bypass is underway. | Visual and flow rate. | Yes | 9031 | Twomile Brook | 2025-01-15 | 11:00 PM | approximately 10,000 total gallons estimated | 10000 |  | A bypass pump was brought in and installed to bypass the entire pump station. Meanwhile, the pump was pulled to determine the cause of the failure. The cause of the failure was motor failure (burned out). Ansonia had a new spare replacement pump ready to | Ansonia | 17 Glen Dr, Ansonia, CT
ANSONIA | Closed | Sewage Bypass | Dry | 2025-05-31 | 11:30 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Two issues occurred at the same time. A ground fault electrical issue combined with a pump seal failure. | Auto-dialer called out to the emergency on-call operator stating a high wet well level. | 10-20 gallons per minute | Visual, best estimate. | Yes | 9621 | Two-Mile Brook | 2025-06-01 | 00:30 AM | 1000 gallons | 1000 | null | Pump station has been bypassed while repairs are being made. | Ansonia | 17 Glen Dr, Ansonia, CT
ANSONIA | Closed | Sewage Bypass | Dry | 2025-06-08 | 05:30 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Pump had rags in them | Call from fire dept | 10000 gallons | Pump specs | No | 9634 | null | 2025-06-08 | 00:00 AM | 10000 gallons | 10000 | null | Pulled pump and cleared rags | Ansonia | 20 Fitzpatrick Rd, Ansonia, CT
ANSONIA | Closed | Sewage Bypass | Dry | 2025-06-15 | 02:30 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure | broken fitting on pipe | alarm dialed out for high wet well | 2000 gallons at this time (03:22) | based on typical flow rate into the pump station and pump specs | No | 9656 | null | 2025-06-15 | 06:30 AM | approximately 20,000 | 20000 | null | A new fitting was installed to replace the broken one. | Ansonia | 20 Fitzpatrick Rd, Ansonia, CT
[18 empty] | TOTAL VOLUME | 41000

## Beacon Falls
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BEACON FALLS | Closed | Sewage Bypass | Dry | 2025-01-06 | 09:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | stone, sand | Resident phone call | less that a gallon a minute | direct observation, manhole was surcharged, but only leaking intermittently | No | 9016 | null | 2025-01-06 | 12:30 PM | 25 gallons or less | 25 |  | line was jetted and cleared | Beacon Falls | Avenue E, Beacon Falls, CT
[18 empty] | TOTAL VOLUME | 25

## Berlin
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BERLIN WATER CONTROL | Closed | Sewage Bypass | Dry | 2025-01-26 | 01:00 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | BROKEN MAIN DISCHRGE ONLY WHEN PUMPS are PUMPING | Routine daily Inspection | 21,000 gals. | based on pumping rate | No | 9055 | NONE into wetlands | 2025-01-27 | 07:00 PM | approx. 30,000 gallons | 30000 |  | Sewer main was dug up and broken pipe replaced | Berlin | 440 Middletown Rd, Berlin, CT
[18 empty] | TOTAL VOLUME | 30000

## Branford
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRANFORD | Closed | Sewage Bypass | Dry | 2025-09-21 | 11:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Sewage backup in sewer line. | Police department | 30 gallons | visual. | No | 9930 | null | 2025-09-21 | 11:30 AM | 30 gallons | 30 | null | jetting sewer line | Branford | Driscoll Rd, Branford, CT
[18 empty] | TOTAL VOLUME | 30
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-10-03 | 09:30 AM | Select... | Raw Sewage | Sewage Line Blockage - Grease | null | Called in by homeowner | N/A | N/A | No | 9966 | null | 2025-10-03 | 10:15 AM | Unknown |  | null | Line was cleared of Grease | Bridgeport | 307 Texas Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain 2-3" per hour | 2025-09-06 | 04:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Operators on site | total flow 27 MGD | flow meter | No | 9870 | null | 2025-09-06 | 11:00 PM | 2.51 MG |  | null | Storm event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-08-06 | 08:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Reported By Homeowner | N/A | N/A | No | 9782 | null | 2025-08-06 | 09:45 AM | N/A |  | null | Line was cleaned | Bridgeport | 132 Burnsford Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-07-14 | 07:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Reported by resident | unknown | n/a | No | 9715 | null | 2025-07-14 | 09:00 PM | n/a |  | null | Main line cleared | Bridgeport | 774 Capitol Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-05-30 | 04:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | plumber on site earlier potential source of problem | called in by resident | Unknown | NA | No | 9601 | NA | 2025-05-30 | 04:30 PM | NA |  | null | Mainline cleared with high velocity jetting | Bridgeport | 330 French St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-05-16 | 07:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | NA | Resident call | Unknown | NA | No | 9560 | NA | 2025-05-16 | 08:30 PM | unknown |  | null | high pressure jetting main line | Bridgeport | 97 Alfred St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-05-15 | 12:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | na | called in by resident | 20gal | visual | Yes | 9558 | Pequannock River | 2025-05-15 | 01:45 PM | 20 gal es |  | null | high pressure jetting main line | Bridgeport | 129 Huntington Rd, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 09:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Call from resident | unknown | n/a | No | 9474 |  | 2025-05-06 | 09:15 AM | unknown |  |  | Line jetted | Bridgeport | 369 Hawley Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-03-11 | 11:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Homeowner notified | unknown | NA | No | 9219 |  | 2025-03-11 | 12:45 PM | Unknown |  |  | Main line was cleared by high pressure jetting | Bridgeport | 383 Arctic St, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 11:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Plant flow meter | 1.21 MG | plant flow meter | Yes | 9172 | Bridgeport Harbor | 2025-03-06 | 01:45 AM | 1.21MG 1.45" rain |  |  | weather event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-02-18 | 09:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | some rocks and rags | visual on site | 6000 gals | visual | Yes | 9120 | Rooster River | 2025-02-18 | 12:00 PM | 6000 gals |  |  | cleared main line with high pressure jetter | Bridgeport | 149 Rooster River Blvd, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-02-16 | 02:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | rain with snowmelt and high tide | permitted flow meter | pending | certified flow meter | Yes | 9108 | Bridgeport Harbor | 2025-02-16 | 05:30 PM | 1.71 MG |  |  | event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-02-13 | 02:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | homeowner | unknown | NA | No | 9093 |  | 2025-02-13 | 02:45 PM | Unknown |  |  | Mainline cleaned with high pressure jetting | Bridgeport | 175 High Ridge Dr, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-11-09 | 01:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Call from resident | 500 | visual | Yes | 10116 | Island Brook | 2025-11-09 | 02:00 PM | 500 gallons |  | null | Line was jetted and cleared | Bridgeport | 455 Trumbull Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-10-16 | 02:15 PM | Basement | Raw Sewage | Unknown | null | Reported by resident | unknown | na | No | 10020 | null | 2025-10-16 | 02:30 PM | unknown |  | null | Line jetted in street, no obstruction encountered. Unknown if main line was cause of back up. | Bridgeport | 213 Harral Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-18 | 11:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Resident reported. | unknown | N/A | No | 9927 | null | 2025-09-18 | 12:30 PM | unknown |  | null | Line jetted and cleared | Bridgeport | 410 Dexter Dr, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-17 | 02:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Reported by resident | 100 gallons | visual observation | Yes | 9926 | Bruce Brook | 2025-09-17 | 02:30 PM | 100 gallons |  | null | Line jetted and cleared | Bridgeport | 1905 Barnum Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-14 | 08:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Reported by homeowner | Unknown | Unknown | No | 9920 | null | 2025-09-14 | 10:00 PM | Unknown |  | null | Line jetted and cleared | Bridgeport | 133 Clark St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-08 | 09:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Resident called and reported back up. | n/a | n/a | No | 9892 | null | 2025-09-08 | 09:30 AM | unknown |  | null | line jetted and cleared | Bridgeport | 426 Savoy St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-05 | 11:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Call in report from Fire Department | less than 500 gallons | visual | No | 9868 | null | 2025-09-05 | 11:45 PM' | less than 500 gallons |  | null | line jetted and cleared | Bridgeport | 476 Woodlawn Ave Ext, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-08-21 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | reported by operators | 30 MGD | flow meter | No | 9826 | null | 2025-08-21 | 04:00 AM | estimated 3 MG |  | null | storm ended | Bridgeport | Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-06-18 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Called in by resident | approx. 10,000 gallons | visual estimate | Yes | 9665 | Pequonneck River | 2025-06-18 | 03:00 PM | approx. 10,000 gallons |  | null | Line jetted and cleared | Bridgeport | 20 Crescent Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-06-13 | 09:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Bridgeport PD | 750 | Visual | Yes | 9655 | Bruce Brook | 2025-06-14 | 10:45 AM | 750 |  | null | line jetted and cleared | Bridgeport | Boston Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-05-20 | 01:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Rags, Wipes | Homeowner Called it in | Unknown | N/A | Yes | 9565 | Bruce Brook | 2025-05-20 | 02:30 PM | Unknown |  | null | Line was cleared | Bridgeport | 49 Sage Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-05 | 10:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | operations | N/A | N/A | Yes | 9455 | Long Island Sound Cedar Creek | 2025-05-06 | 00:45 AM | 2.5 mg |  |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-04-28 | 09:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Called in by a resident | 500 | Visual | Yes | 9414 | Ash Creek | 2025-04-28 | 11:00 PM | 500 |  |  | Line was cleared | Bridgeport | 280 Scofield Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-04-25 | 08:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Rags, Roots | Called in by Bridgeport Public Works | Unknown | N/A | Yes | 9403 | 7103 Yellow Mill Channel | 2025-04-25 | 09:45 AM | Unknown |  |  | Line was jetted and cleaned out | Bridgeport | 1680 Reservoir Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-04-25 | 10:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Other | Rags, Wipes and Grease | Homeowner report | Unknown | N/A | No | 9404 |  | 2025-04-25 | 10:45 AM | Unknown |  |  | Main Line was Jetted | Bridgeport | 426 Savoy St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-03-17 | 04:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other |  | Notified by resident | 30 gallons | visual observation | No | 9251 |  | 2025-03-17 | 05:15 PM | 30 |  |  | High pressure jetting cleared line | Bridgeport | Iranistan Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-17 | 03:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observation | N/A | N/A | Yes | 9235 | Cedar Creek Long Island Sound | 2025-03-17 | 09:30 AM | 5.05 MG |  |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 09:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | plant flow meter | 5.18MG | plant flow meter | Yes | 9169 | Bridgeport Harbor | 2025-03-06 | 04:00 AM | 5.18 MG - 1.43" rain |  |  | weather event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-02-16 | 01:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observation | N/A | N/A | Yes | 9107 | Cedar creek Long Island sound | 2025-02-16 | 10:45 PM | 11.2 mg |  |  | event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-01-27 | 01:30 PM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | D&D Construction cracked Lakeside Pump Station force main, pump station shut down while repair made, sufficient wet well capacity, can bypass to sanitary gravity manhole Contractor conducting repair | Contractor notified WPCA | Estimated 500 gals | estimated prior to station shutdown | No | 9057 | Lake Forest Creek | 2025-01-27 | 05:15 PM | 500 gal estimated |  |  | force main repaired by contractor, used 2 vactor trucks to keep excavation empty when PS on line during repair | Bridgeport | 395 Lakeside Dr, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-01-01 | 00:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observation | N/A | N/A | Yes | 8979 | Cedar Creek Long Island Sound | 2025-01-01 | 03:30 AM | 2.99 mg |  |  | event eneded | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-30 | 02:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | Buildup of mostly rags and grease in main sewer line | 1) Department received a possible stoppage call from Ryan Mallet from GW property management on 10/30 and 11/1. | According to Ryan there is roughly 2 feet of sewage in the basement of 189 Divinity street. Ryan stated at least two thousand gallons. | Based on what the property management company relayed to staff. | No | 10064 | null | 2025-10-30 | 03:30 PM | estimated final quantity is between 4,000 and 8,000 gallons. |  | null | On both occasions the jet cleaned to removed blockage. On 11/1 line was also video inspected to confirm no debris, roots or sections of compromised pipe. | Bristol | 190 Divinity St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2025-09-02 | 08:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Roots | Blockage was a combination of grease, rags and grease. | Sewer department received possible stoppage call from homeowner at 24 Roberge Road. | 5 gallons. | Based on conversation with the homeowner (Sharon) | No | 9851 | null | 2025-09-02 | 09:45 AM | 5 gallons |  | null | Staff jet cleaned the line. | Bristol | 24 Roberge Rd, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2025-04-28 | 04:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | Buildup of rags and grease in the main sewer line. | Received a call form resident at 242 High Street | less than 50 gallons | Based on description from resident. | No | 9416 |  | 2025-04-28 | 04:30 PM | 50 gallons or less |  |  | Staff jet cleaned the line. | Bristol | 214 High St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Snowmelt | 2025-03-01 | 07:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | Rags and some grease. | Resident called in. | 500-1,000 gallons estimated on roadway. | Estimate. | No | 9150 |  | 2025-03-01 | 09:00 PM | 500-1,000 gallons |  |  | Jetted main line to clear stoppage | Bristol | 328 South St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2025-02-10 | 12:00 PM | Sewer Main | Raw Sewage | Other | Discharge from an unidentified 6" line not mapped. Discharge is clean and clear without odor. | The City is performing bridge rehabilitation at this location. During preliminary field work a line was discovered penetrating through the bridge abutment discharging water into the Pequabuck River | 15-20 gpm | Through CCTV footage. | Yes | 9086 | Pequabuck River | 2025-02-13 | 08:00 AM | 60,000-80,000gallons of clear/clean water |  |  | Installing line plug. | Bristol | 9 East St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2025-01-06 | 10:00 AM | Lateral - Private | Raw Sewage | Other | compromised private lateral. | Homeowner notified the City of Bristol with a culvert issue. City investigated culvert and was notified during inspection of a sewage back up in house 211 Park Street. A contractor was hired by property owner to clear the blockage. City requested camera f | 280 gpd | Water usage records. | Yes | 9035 | Pequabuck River | 2025-01-31 | 01:15 PM | 7000 gallons |  |  | Contractor repaired. | Bristol | 211 Park St, Bristol, CT
BROOKFIELD | Closed | Sewage Bypass | Dry | 2025-11-18 | 04:00 AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Wrong couplings used by contractor on PVC to DIP connection which caused the bypass. | Daily pump station check. Discovered @ 745am. | 10,500 gallons +/- | SCADA system/flow numbers. | No | 10135 | null | 2025-11-18 | 08:00 AM | 10,500 gallons +/- |  | null | Contractor installed proper couplings. | Brookfield | 120 Junction Rd, Brookfield, CT
BROOKFIELD | Closed | Sewage Bypass | Dry | 2025-11-18 | 04:00 AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Bad connection made by contractor. | Daily pump station check. | 20,000 gallons | Flow numbers/SCADA system. | No | 10130 | null |  | null | null |  | null | null | Brookfield | 120 Junction Rd, Brookfield, CT
BROOKFIELD | Closed | Sewage Bypass | Dry | 2025-04-05 | 04:00 AM | Sewer Main | Raw Sewage | Unknown | Possible sewer force main break. Investigation underway.* Force Main break | Brookfield Police call to BWPCA. | 40,000 gallons. | Peak flow vs low flow. Pump starts and stops/runtimes via scada system.Visual of discharge. | No | 9337 |  | 2025-04-05 | 11:30 AM | 40,000 Gallons |  |  | Pumps turned off at Pump Station upon acknowledgement of bypass.Pump trucks on site to handle in coming flow at pump station.Contractor exposed broken force main and repaired.2 catch basins IAO bypass pumped and cleaned.Site affected cleaned/restored. | Brookfield | 64 Federal Rd, Brookfield, CT
CANTON | Closed | Sewage Bypass | Dry | 2025-11-16 | 08:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Seemed to find grease upon clearing of stoppage | Operator received notification from Canton dispatch that a manhole appeared it was overflowing. | <1000 | Visual estimate of 5 gpm for 2 or so hours. | No | 10128 | null | 2025-11-16 | 09:30 PM | <1000 |  | null | Sewer jetter cleared stoppage | Canton | 47-49 Sunset Terrace, Canton, CT
CHESHIRE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-12 | 05:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Excessive grease blocking our drop manhole | police | 10GPM | visual | Yes | 9366 | Quinnipiac River | 2025-04-12 | 09:45 PM | 2000 gallons |  | null | jetted blocked line. | Cheshire | 1728 Highland Ave, Cheshire, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2025-06-20 | 12:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | buildup of rags | homeowner at 19 Allen discovered | 100 gallons | based off of flow coming out of drain pipe for ~ 1 hr | Yes | 9674 | Lake Wackawanna |  | null | null |  | null | null | Danbury | 21 Alan Ave, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2025-06-20 | 12:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | rags | Citizen report | 100 gallons | estimated based on flow and duration of bypass | Yes | 9672 | Lake Wackawana | 2025-06-20 | 01:00 PM | 100 gallons |  | null | Public utilities jetted the line and cleared the blockage | Danbury | 21 Alan Ave, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2025-05-27 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | null | Reported to Public Utilities by a City worker | 500 Gallons | Estimated based on duration of bypass | No | 9595 | null | 2025-05-27 | 03:00 PM | 500 Gallons |  | null | The sewer line was jetted to clear the obstruction and normal sewer flow resumed at 3PM on 5/27/25 | Danbury | 1 Patriot Dr, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-25 | 04:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Grease and Rags | Condo tenant woke up and found floor covered in sewage | 1,000 gallons | Estimated based on square footage of area containing the sewage | No | 9298 | null | 2025-03-25 | 11:00 AM | 1,000 gallons |  | null | Jetted sewer main and cleared blockage. Treated with Potassium Permanganate | Danbury | 7 Padanaram Rd, Danbury, CT
DARIEN | Closed | Sewage Bypass | Snowmelt | 2025-02-27 | 10:45 AM | Lateral - Private | Raw Sewage | Sewage Line Broken by Contractor or other utility | Construction activity on site, low pressure sewer lateral valve box impacted by equipment (dumpster), box was marked in earth area with flags in earth area and paint on road surfaces. | Contractor call it in, 1 Swifts Lane, Darien, CT | 1 gallon per minute for 10 minutes and 0 gallons per minute for 10 minutes estimated. Flow is intermittent and related to pump activation within the system. | Visual observation of flow from area of break into containment excavation. | No | 9146 | N/A | 2025-02-27 | 12:45 PM | 60 gallons - zero gallons reached waterbody. |  |  | broken pipe repaired and new valve assembly installed. | Darien | 1 Swifts Ln, Darien, CT
DARIEN | Closed | Sewage Bypass | Dry | 2025-02-04 | 01:30 PM | Manhole | Raw Sewage | Unknown | looking for clogged pipe. will confirm.This was the result of a clog in sewer pipe. | DPW crew member observed and called sewer dept. | to be determined upon correction60 to 100 gallons total | 3 gpm | Yes | 9072 | Goodwives River via CB. CB cleaned out. | 2025-02-04 | 02:00 PM | Actually ended at 1:50 PM. 3 to 5 gallons per minute for 20 minutes. 60 to 100 gallons total volume estimated. |  |  | jet rodder and vactor truck utilized to clear pipe. | Darien | 36 Old Kings Hwy S, Darien, CT
DERBY | Closed | Sewage Bypass | Dry | 2025-09-08 | 04:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Electrical Equipment Failure | Line power outage. One if the insulators of the three phase line power feeding the treatment plant failed. Due to this event we still had two phase power feeding the plant which caused the secondary control building generator to run intermittently while t | Upon initial walk around the plant at 4:45am I noticed the secondary building generator running. | We are estimating 0.583MG were discharged | The on call operator was called in Sunday 9/7/25 at 3pm for a fire alarm trouble call. As he checked the plant no generators were running and all equipment was operational. Because the auto dialer did not call out, we are going to use the time the on call | Yes | 9895 | Housatonic River | 2025-09-08 | 05:45 AM | 0.583MG |  | null | Plant mechanics manually started main plant generator 9/8/25 by 5:45am. United Illuminating changed all the insulators and we were back on line power by 8:00am 9/8/25 | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Dry | 2025-09-08 | 04:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Electrical Equipment Failure | Power outage | Upon initial walk around the plant at 4:45am I noticed the secondary building generator running. | Unknown at this time | Further investigation required | Yes | 9891 | Housatonic River | 2025-09-08 | 05:45 AM | We are estimating 0.583MG |  | null | Plant mechanics manually started main plant generator 9/8/25 by 5:45am. United Illuminating changed all the insulators and we were back on line power by 8:00am 9/8/25 | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Dry | 2025-06-09 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Unknown | We are currently investigating the cause of why the blower had shut off. We are also investigating why no plant alarms went off calling in our stand-by crew. | Upon visual walk around the plant. | Quantity undetermined at this time. Best guess 100,000 - 500,000 gallons. | Plant mechanic was called out to the plant on Saturday 6/7/25 at 4:07pm for a high wet well level alarm. Upon leaving the plant at approximately 7:00pm the plant blower was still in operation. Once the blower was back in operation the color and foam in th | Yes | 9635 | Housatonic River | 2025-06-09 | 05:30 AM | Approximately 2.25MG |  | null | At approximately 5:30am the main plant blower was back in operation. | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Dry | 2025-04-21 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Backpressure from using the Jet truck to clear a clogged sewer main. | Call from homeowner. | 30 gallons total | Visual estimation | No | 9397 | null | 2025-04-21 | 10:15 AM | 30 Gallons |  | null | The sewer main was unclogged, relieving the back pressure in this manhole, and allowing the sewage to flow again. | Derby | 210 Emmett Ave, Derby, CT
EAST HAMPTON WPCA | Closed | Sewage Bypass | Dry | 2025-03-26 | 08:00 AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Assumed break in 4" ductile iron pipe. | During a routine pump station inspection. | The leak appears to be about 15 gallons per minute and pump station runtime data suggests that it may have been leaking for approximately 650 minutes. I would estimate the discharge at approximately 9,750 gallons. | The estimated rate was determined by visually inspecting the leak while the pump was running, reviewing pump station runtimes, and confirming that water was pumped to the next pump station and it was not all coming out of the break. | No | 9295 | null | 2025-03-26 | 08:00 AM | 9,750 |  | null | The pump was shut off and the pipe was isolated by closing valves and installing blind flanges in the piping. There is a second pump at the pump station that is still up and running with no issues. | East Hampton | 30 Pine Trail, East Hampton, CT
EAST WINDSOR WPCF | Closed | Sewage Bypass | Dry | 2025-06-15 | 05:30 AM | Treatment Plant | Fully treated sewage from WWTP | Other | High chlorine residual (1.56) resulted in a bypass of fully treated wastewater. Everything at the plant is functioning properly, no high flows or abnormal flow rates shown to give reason for high chlorine residual. | Operator performed a chlorine residual test at 5:30am on 6/15/25. | 58,000 Gallons | peak flow rate within the time frame of testing multiplied by the time between testing | Yes | 9658 | Connecticut River | 2025-06-15 | 07:30 AM | 58,000 Gallons |  | null | lowered ratio set point on chlorine pumps | East Windsor | 192 S Water St, East Windsor, CT
EAST WINDSOR WPCF | Closed | Sewage Bypass | Dry | 2025-04-25 | 07:00 AM | Treatment Plant | Fully treated sewage from WWTP | Other | bypassed final contact tank located after first contact tank to clean final contact tank | N/A - performing routine maintenance | N/A | N/A | No | 9405 | Connecticut River | 2025-04-25 | 12:00 PM | 0 |  | null | NA | East Windsor | 192 S Water St, East Windsor, CT
EAST WINDSOR WPCF | Closed | Sewage Bypass | Other | 2025-04-04 | 08:00 AM | Sewer Main | Raw Sewage | Other | Wash out of main truck line due to storm water drainage | Loss of flow at plant. Went to visually check the sewer line and found broken gravity main | 300,000 to 400,000 gallons per day | flow meter at plant | Yes | 9336 | Connecticut River | 2025-04-04 | 11:45 PM' | around 300,000 to 400,000 gallons |  |  | Currently bypass pumping is in place to work around the broken pipe. Permeant repairs plans are being worked on. | East Windsor | 249 S Water St, East Windsor, CT
EAST WINDSOR WPCF | Closed | Sewage Bypass | Dry | 2025-03-25 | 08:00 AM | Sewer Main | None - for Construction Bypass | Other | Sewer line abandonment and connection to new sewer line | Planned by contractor ROTHA in conjunction with CT DOT | 4000 gallons being transfered from one manhole to another every 20 minutes | timing the truck from start pumping to end pumping when full. Truck can hold 4,000 gallons | No | 9294 | scantic river | 2025-03-26 | 03:00 AM | unknown amount transfered. No sewer was spilled |  |  | ROTHA made connection with new piping system | East Windsor | 5 Old Ellington Rd, East Windsor, CT
ENFIELD POTW | Closed | Sewage Bypass | Dry | 2025-06-05 | 12:15 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | The hole was located under the pipe possibly sitting on a rock that wore through overtime or perhaps it had a hair line fracture during installation that finally wore through | Routine lift station inspection | We calculated 33,000 gallons had reached the Scantic River | Pump run times from SCADA | Yes | 9626 | Scantic River | 2025-06-05 | 03:00 PM | 33,000 gallons |  | null | Repaired pipe on 6/9/25, tested on 6/10/25 and put back online 6/10/25 | Enfield | 73 Simon Rd, Enfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2025-04-22 | 09:45 AM | Pump Station | Raw Sewage | Sewage Line Broken by Contractor or other utility | Town's contracted Engineer's drilling subcontractor drilled into the force Main. | Contractor called . | 750 gallons per pump cycle. | Best guest per pump gpm discharge | Yes | 9400 | Long Island Sound | 2025-04-22 | 02:30 PM | @1500 gallons |  |  | Contractor excavated the road and repaired pipe with an Adams clamp. | Fairfield | 1610 Fairfield Beach Rd, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-01-01 | 04:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Called in by resident | 150 Gallons | Visual estimate | Yes | 8999 | Pine Creek Marsh | 2025-01-01 | 04:45 PM | 150 Gallons |  |  | Jet line to break blockage | Fairfield | 11 Rugby Rd, Fairfield, CT
FARMINGTON | Closed | Sewage Bypass | Dry | 2025-07-28 | 01:30 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Crack in Ductile Iron pipe, material found in trench not suitable for compaction. | Sewage coming out from crack in roadway | Under 200 gpm | 5 gallon buckets over the course of a minute | No | 9760 | null | 2025-07-28 | 11:45 PM' | Under 5,000 |  | null | 5 foot Force main section of line was replaced | Farmington | 38 Patrick H Flood Rd, Farmington, CT
GLASTONBURY | Closed | Sewage Bypass | Dry | 2025-11-07 | 12:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease | Possible grease trap issue. | Town Fire Marshall, then reported to Town Engineer staff. | Under 25 gallons | WPCF staff estimated. | No | 10113 | null |  | null | null |  | null | null | Glastonbury | 70-124 Hebron Ave, Glastonbury, CT
GLASTONBURY | In Progress | Sewage Bypass | Dry | 2025-09-21 | 06:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Roots | Combination of rags, paper and roots | Citizen | under 500 gallons | Estimated | No | 9931 | null |  | null | null |  | null | null | Glastonbury | 76 Mill St, Glastonbury, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-11-08 | 03:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease and rags caused the backup. Crew jetted the line and restored flow. | Called in by homeowner. | Less than 50 gallons were discharged into the basement. | Field estimate by crew. | No | 10115 | N/A | 2025-11-08 | 03:30 AM | Less than 50 gallons |  | null | Crew jetted the line and restored flow. Pro Klein was contracted to clean and sanitize. | Hamden | 361 Belden Rd, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-09-26 | 10:30AM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | This is a combined line, and it was full of plastic and debris from storm basins. | Prperty manager called first, then the property owner called. | Less than 100 gallons | Field estimate by crew. | No | 9959 | N/A | 2025-09-26 | 11:15 AM | less than 100 gallons. |  | null | Crew jetted the line on Stanley St and restored flow.Pro Klean was contracted to clean and sanitize the building. | New Haven | 68 Norton St, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-09-11 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | A break in the sanitary sewer was causing the flow to drop out of the sanitary system and make its way to the storm system. | Odor complaint from the Whitney Museum at the back of the museum parking lot. GNHWPCA staff found flow at the storm discharge to the Mill River. | 300 gal based on 5 gallons / minute for 1 hour. | Field estimate by crew. | Yes | 9915 | Mill River | 2025-09-11 | 11:45 AM' | 300 Gallons |  | null | A vac truck was set up to hold flow, contractor coming out to repair line. | Hamden | 65 Armory St, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-07-28 | 11:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease was blocking the sewer main. | Resident called it in. | Less than 10 Gallons | Field estimate by crew. | No | 9759 | N/A | 2025-07-28 | 12:00 PM | Less than 10 gallons. |  | null | Crew jetted the line and restored flow. The area around the manhole was washed down with the Vac truck. | Hamden | Pine Rock Ave, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-06-23 | 09:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease in line on Dewey Ave caused the issue. | Property owner called it in. | Crew estimated 20 gallons were discharged into the basement. | Field estimate by crew. When the crew inspected the basement only the floor was damp, no ponding or standing water. | No | 9670 | N/A | 2025-06-23 | 10:45 AM | Less than 20 gallons was estimated by the crew. |  | null | Crew jetted the line and restored flow. Cleaning services were offered to the owner. The crew CCTV and grease cut the line. | East Haven | 144 Coe Ave, East Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-15 | 02:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9539 | NEW HAVEN HARBOR | 2025-05-15 | 03:45 AM | 0.8318 MG Diverted |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-14 | 09:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | UNDETERMINED | Yes | 9533 | NEW HAVEN HARBOR | 2025-05-15 | 00:00 AM | 0.9623 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-09 | 10:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | .Rain event 0.7" | SCADA | 6.3 mgd | SCADA | Yes | 9494 | NEW HAVEN HARBOR | 2025-05-09 | 10:00 PM | 6.3 mgd |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 00:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9460 | NEW HAVEN HARBOR | 2025-05-06 | 09:00 AM | 12.400 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-05 | 06:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | Crew found the sewer full of grass clippings. The line was partially blocked. During heavy rain the sewer backed up. This sewer is combined. | Homeowner called it in. | Less than 20 gallons.field estimate by crew. | There was a small puddle of water at the cleanout in the basement. | No | 9454 | N/A | 2025-05-05 | 07:30 PM | Less than 20 gallons |  |  | Crew jetted the sewer and cleared the grass clipping. Flow was restored. | New Haven | 1 W Park Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-05 | 02:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | 9453 | NEW HAVEN HARBOR | 2025-05-05 | 10:00 PM | 7.3000 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-04 | 08:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9439 | NEW HAVEN HARBOR | 2025-05-05 | 00:00 AM | 0.4181 MG |  |  | Flow event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-26 | 06:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9411 | NEW HAVEN HARBOR | 2025-04-26 | 10:15 PM | 5.3301 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-15 | 05:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | 0.6136 mgd | SCADA | Yes | 9384 | NEW HAVEN HARBOR | 2025-04-15 | 06:00 AM | 0.6136 mgd |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-04-06 | 03:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9347 | NEW HAVEN HARBOR | 2025-04-06 | 03:30 AM | 0.9887 MG Diverted |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-04-01 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | 9322 | NEW HAVEN HARBOR | 2025-04-01 | 01:00 AM | 0.4395 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-04-01 | 07:00 PM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure | Crew found rocks and fresh dirt coming back during the jetting process. Bypass pumps are being set up. Repairs are being scheduled. | Homeowner had a backup in the basement. | 75 gallons were discharged into the basement. | Field estimate by crew. | No | 9327 | N/A | 2025-04-01 | 08:00 PM | 75 gallons were discharged into the basement. |  |  | Crew pumped the line down, a bypass pump will be set up. | New Haven | 126 Cedar Hill Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-31 | 09:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9312 | NEW HAVEN HARBOR | 2025-04-01 | 00:00 AM | 0.0244 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-24 | 03:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9284 | NEW HAVEN HARBOR | 2025-03-24 | 06:00 PM | 1.6080 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-21 | 02:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | Undetermined | Undetermined | Yes | 9272 | NEW HAVEN HARBOR | 2025-03-21 | 03:30 AM | 0.8089 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-17 | 01:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | rain event | SCADA | n/a | undetermined | Yes | 9233 | NEW HAVEN HARBOR | 2025-03-17 | 08:30 AM | 4.7370 MG |  |  | rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-06 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | N/A | Undetermined | Yes | 9177 | NEW HAVEN HARBOR | 2025-03-06 | 03:00 AM | 3.6002 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 07:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | N/A | SCADA Flow monitoring | Yes | 9163 | NEW HAVEN HARBOR | 2025-03-06 | 00:00 AM | 5.5941 MG |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-02-25 | 01:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | After further investigation it was determined that the property owners' lateral was broken causing the basement back up, Surcharge in the street was coincidental and not the cause of the discharge in basement. | Called in by property owner | Less than 50 Gallons | Feild estimate by road crew | No | 9139 |  | 2025-02-25 | 01:45 PM | Less Than 50 Gallons |  |  | sewer main was jetted and flow was restored | New Haven | 25-27 Lander St, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-02-25 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Called in by property owner | Approx 300 gallons | Field estimate by road crew | No | 9140 |  | 2025-02-25 | 02:30 PM | 375 gallons |  |  | sewer main was jetted and flow was restored | Hamden | 80 Skiff St, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-02-16 | 08:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | 9101 | NEW HAVEN HARBOR | 2025-02-16 | 10:00 PM | 8.8483 MG Diverted |  |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-02-12 | 10:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage on Middletown Ave in front of the 91 Diner. | Homeowners called it in. | 560 Middletown Ave had approximately 100 gallons at the time of inspection.641-643 Middletown Ave had approximately 1600 gallons at the time of inspection. This sewage was throughout the basement.The combined total gallons is approximately 1700 | Square footage times inches of water times1 7.48. | No | 9092 | N/A | 2025-02-12 | 11:15 PM | 1700 gallons were discharged into the basements. |  |  | Crew jetted the line and restored flow. Pro Klein was contracted to clean and sanitize both basements. | New Haven | 560 Middletown Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-02-11 | 08:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | There was grease blocking the gravity line near the pump station. | Called in by contractor. | 75-80 gallons were spilled to the road surface. The area was washed down after the line was cleared. | Field estimate by crew. | No | 9091 | N/A | 2025-02-11 | 09:00 PM | 75-80 gallons |  |  | Crew jetted the line and restored flow. The area around the spill was washed back into the MH. | New Haven | 1024 Quinnipiac Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-02-06 | 03:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by property owner | less than 50 gallons | Feild estimate by crew | No | 9077 |  | 2025-02-06 | 03:30 PM | less than 50 gallons |  |  | Sewer main was jetted and flow restored | New Haven | 180 Main Street Anx, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-01-21 | 11:30 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure | By-pass pumps failed causing construction site to flood. Sewage was contained in the work site. | Contractor called it in. | over 3000 gallons of sewage was discharged into the construction site.Holzner estimated 30,000 gallons of sewage were discharged into the construction site. | One vac truck has been filled removing the sewage. The contractor is still working on the spill. | No | 9045 | N/A | 2025-01-22 | 09:00 AM | 30,000 gallons were estimated by Holzner. |  |  | Contractor hired McVac to remove the sewage from the site. | Woodbridge | 2 Brookside Dr, Woodbridge, CT
GNHWPCA | Closed | Sewage Bypass | Other | 2025-01-19 | 04:30 PM | Manhole | Raw Sewage | Unknown | Unknown cause, manhole had debris in it. | Property owner or manager called it in. | Less than 75 gallons. | Field estimate by crew. | No | 9043 | N/A | 2025-01-19 | 05:15 PM | Less than 75 gallons were discharged from the sanitary sewer. |  |  | Crew jetted the sanitary sewer and restored flow. The area was washed down and all visible debris was picked up. The parking lot drains run to the sanitary sewer. | New Haven | 130 Winchester Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Other | 2025-01-06 | 11:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Other | Grease and rags were removed from the system. | Resident called it in. | Less than 100 gallons were discharged into the basement. | Field estimate by crew. | No | 9018 | N/A | 2025-01-06 | 11:45 AM' | Less than 100 gallons. |  |  | Crew flushed the sanitary sewer and restored flow. The GNHWPCA contracted Pro Klean to clean and sanitize the basement. | East Haven | 690 Thompson St, East Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-01-01 | 00:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | 8985 | NEW HAVEN HARBOR | 2025-01-01 | 02:45 AM | 2.7239 MG Diverted |  |  | Rain Event Ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2025-05-01 | 01:15 PM | Manhole | Raw Sewage | Other | Holes found in the base of an existing sewer manhole structure | Routine inspection by Sewer Division for a utility markout | Unknown | N/A | Yes | 9448 | Byram River | 2025-05-01 | 02:00 PM | Unknown |  |  | Holes in sewer manhole patched with hydraulic cement | Greenwich | 21 Byram Rd, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2025-04-14 | 09:00 AM | Lateral - Private | Raw Sewage | Unknown |  | Phone call from neighbor | Unkown | N/A | Yes | 9378 | Unkown | 2025-04-21 | 12:00 PM | Unknown - it was from one home - estimate 300 gpd so total could have been approximately 2,100 gallons |  |  | Property owner had plumber come and snake their lateral on April 21st. | Greenwich | 32 Chapel St, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2025-03-06 | 10:30AM | Treatment Plant | Fully treated raw sewage except disinfection | Sewage Line Break, Crack or Failure | This is treated wastewater prior to UV disinfection that has additional chlorine added to it. It is a 2-inch diameter plant effluent line. A break occurred in a pipe coupling connection. | Visually observed water coming to the surface of the ground | Estimated approximately a total discharge of 2,500 gallons. | Based on visual observations, and comparison to the Sewer Spill Estimation Guide (by Orange County, CA) that the USEPA has previously provided as a reference. | Yes | 9189 | Greenwich Harbor | 2025-03-06 | 11:15 AM | Estimated approximately a total discharge of 2,500 gallons. |  |  | We shut the water off, hand excavated and repaired the pipe. | Greenwich | 250A Shore Rd, Greenwich, CT
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2025-01-26 | 03:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | Gravity line is clogged | Resident called it in | .5 gpm | Visual | No | 9053 |  | 2025-01-26 | 05:30 AM | 60 gallons |  |  | Jetted line | Groton | 5 Riverview Ave, Groton, CT
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2025-01-15 | 04:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | resident called in | 100 gallons | Estimation from volume coming out of manhole about 3 gallons a minute for 30 minutes | No | 9033 |  | 2025-01-15 | 04:45 AM | 100 gallons |  |  | Jetted gravity line | Groton | 5 Riverview Ave, Groton, CT
GROTON, TOWN OF | Closed | Sewage Bypass | Dry | 2025-01-14 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | routine inspection | 100 Gallons | estimate | No | 9028 |  | 2025-01-14 | 12:15 PM | 100 gallons |  |  | Clear sewer blockage by hydro jet | Groton | 144 Pamela Ave, Groton, CT
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Dry | 2025-09-11 | 01:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | A resident saw sewage coming out of a manhole in a parking lot | 2 to 5 gallons a minute. | Visual estimate | No | 9916 | null | 2025-09-11 | 02:15 PM | 200 to 300 gallons. |  | null | Jetted line and used vacuum truck to clean area. | Southbury | 450 Heritage Rd, Southbury, CT
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Dry | 2025-05-27 | 09:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Residents of that area dump grease down the drain into the septic system. This caused a partial blockage of the main sewer line. | Resident sent an email to DEEP and DEEP contacted CT Water. | 20 to 50 gallons per hour | Visual estimation. | Yes | 9594 | Tributary to the Pomperaug River. | 2025-05-27 | 10:45 AM | Between 50 to 75 gallons from the time that the call came in. To when it was cleared. The resident that reported the SSO said that it has been overflowing for four days. |  | null | The main line was jetted to clear the blockage. | Southbury | 339 Grove Pond Ln, Southbury, CT
JEWETT CITY WPCA | Open | Sewage Bypass | Dry | 2025-09-15 | 12:30 PM | Manhole | Raw Sewage | Electrical Equipment Failure | null | Call from customer | 5 gallons | visual | No | 9922 | null |  | null | null |  | null | null | Griswold | 302 E Main St, Griswold, CT
KILLINGLY | Closed | Sewage Bypass | Dry | 2025-03-13 | 01:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Maintenance worker at the school | 50-75 gallons | 1 inch opening in manhole leaking slowly for 45-60 minutes until we unclogged the pipe. | No | 9224 |  | 2025-03-13 | 02:30 PM | 50 gallons |  |  | Blockage in manhole was cleared by sewer jet. | Killingly | 60 Soap St, Killingly, CT
KILLINGLY | Closed | Sewage Bypass | Dry | 2025-01-18 | 02:15 AM | Treatment Plant | Sludge Spill | Mechanical Equipment Failure | Sludge hauler was removing trailer from facility when tailgate opened dumping sludge cake on the roadway | State Police notified us of some water on the road at the intersection of Wauregan St. and Dyer St. at 2:15am. | 100 gallons of soupy sludge on the top of the regular sludge. | By the size of 3 piles of sludge that was picked up. | No | 9037 |  | 2025-01-18 | 02:45 AM | 120 gallons |  |  | Kropp Environmental Cleanup 1/18/2025 | Killingly | 39 Wauregan Rd, Killingly, CT
LISBON | Closed | Sewage Bypass | Dry | 2025-01-30 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Customer Call | 1000 Gallons | Visual Estimate | No | 9064 |  | 2025-01-30 | 02:30 PM | 1000 |  |  | Repaired force main | Lisbon | 16 River Rd, Lisbon, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2025-11-28 | 04:00 PM | Basement | Raw Sewage | Unknown | While jetting the main line, we found nothing indicative of a sewer main blockage. Homeowner said after we jetted the main, the water subsided, but nothing was in the line that indicated there was a sewer back up. | Property owner called answering service | Approximately 300 gallons | Estimated based on description of property owner- Event was over by the time of my arrival. | No | 10155 | null | 2025-11-28 | 04:30 AM | 300 Gallons |  | null | Jetted sewer main with combination Jet/Vac truck | Manchester | 53 Niles Dr, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2025-06-24 | 07:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Roots | null | Homeowner called | Approximately 500 gal | Visual estimation | No | 9676 | null | 2025-06-24 | 07:30 AM | 500 Gal |  | null | Crew responded with Sewer combination truck and jetted and cleared the line. | Manchester | 156 Kennedy Rd, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-07 | 05:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Property owner contacted Manchester Fire Dept- Manchester Fire Dept contacted Water Dept. | 3200 Gal | Sq footage x Depth | No | 9353 |  | 2025-04-07 | 07:00 PM | 3200 gal |  |  | Water Dept. personnel responded to scene with combination sewer truck and cleared the line w/ jet. Line is functioning normally | Manchester | 107 Vernon St, Manchester, CT
MANCHESTER (Hockanum River WPCF) | In Progress | Sewage Bypass | Dry | 2025-03-20 | 07:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Rags accumulated in line | Called in by passerby | Approximately 300 gallons | Visual estimation | No | 9265 | null |  | null | null |  | null | null | Manchester | 68 Woodbridge St, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2025-03-20 | 07:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Rags accumulated in linej | Called in by passerby | Approximately 300 Gallons | Visual estimation | No | 9266 |  | 2025-03-20 | 08:45 PM | Approximately 300 gallons |  |  | Collection system operators responded to location with combination sewer jet/vac truck. They jetted the line, cleared the blockage and removed remaining rags from the upstream manhole. | Manchester | 68 Woodbridge St, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2025-01-05 | 05:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Manchester Police Department | 500 Gallons | Visual estimate | Yes | 9014 | Union Pond | 2025-01-05 | 06:15 PM | 500 Gallons |  |  | Crew cleared sewer blockage with combination jet/vac truck | Manchester | 107 N School St, Manchester, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Operator opened bypass gate | Plant influent was approximately 62MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | 9511 | Connecticut River | 2025-05-10 | 06:15 AM | 1,919,167 gallons of partially treated effluent, combined with 30,936,354 gallons of fully treated effluent during the 12.25 hour event. |  | null | When flows subsided under 55 MGD, operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 11:45 AM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Operator opened bypass gate. | Plant influent was approximately 60 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | 9476 | Connecticut River | 2025-05-06 | 03:00 PM | 339,999 gallons of partially treated effluent, combined with 9,741,336 gallons of fully treated effluent during the 4.25 hour event. |  | null | When flows subsided under 55 MGD, operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-06 | 05:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate | Plant influent was approximately 63 MGD at the time of opening bypass gate | Using the difference between the calibrated influent and effluent parshall flumes | Yes | 9179 | Connecticut River | 2025-03-06 | 09:45 AM | 219,722 gallons of partially treated effluent, combined with 10,667,198 gallons of fully treated effluent during the 4.66 hour event. |  |  | When flows subsided under 55 MGD, operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-31 | 04:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | null | MDC SCADA | 0.012 MG | MDC SCADA | Yes | 10088 | PIPER BROOK | 2025-10-31 | 06:30 AM | 0.017 MG |  | null | RAIN EVENT ENDED. | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-10-08 | 11:45 AM' | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | PAPERS CAUSING BLOCKAGE | MDC PERSONNEL | < 10,000 GALLONS | SCADA | Yes | 9993 | CONNECTICUT RIVER | 2025-10-09 | 08:30 AM | 7700 GALLONS |  | null | Main sewer flushed by jet truck and stoppage relieved | Hartford | 2370 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-30 | 09:00 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | null | Railroad worker | <1000 | MDC Personnel visual observation | No | 9962 | null | 2025-09-01 | 03:15 PM | <1000 |  | null | Crews responded to by-pass with equipment to stop the overflow. Contractor responding to repair collapsed section | Hartford | Albany Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-30 | 03:15 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | SEWER MAIN COLLAPSE | RAILROAD PERSONNEL | < 1000 | MDC PERSONNEL | No | 9970 | null | 2025-10-03 | 02:00 PM | 1000 GALLONS |  | null | CONTRACTOR REPAIRED SEWER MAIN | Hartford | 1419 1/2 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-29 | 04:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | OVERFLOW MAIN SEWER BACKED UP | PASSER BY | <100G | MDC PERSONNEL | Yes | 9961 | FOLLY BROOK DIKE | 2025-09-30 | 02:30 PM | < 1000 GALLONS |  | null | BYPASS ELIMINATED ONCE COLLAPSED SEWER MAIN WAS REPAIRED | Hartford | 1010 Wethersfield Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-05 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | null | MDC OPERATIONS CREW | LESS THAN 100 GAL | MDC PERSONEL | No | 9867 | null | 2025-09-05 | 07:30 PM | LESS THAN 100 GAL |  | null | MDC OPERATIONS FIXED BREAK ON FORCE SEWER MAIN | Rocky Hill | 235 Dividend Rd, Rocky Hill, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-02 | 08:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Homeowner/Resident | <100 Gallons | MDC Personnel | No | 9850 | null | 2025-09-02 | 09:30 AM | <100 Gallons |  | null | Main sewer flushed by jet truck and stoppage relieved | Windsor | 120 Preston St, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-07-30 | 09:30 PM | Basement | Raw Sewage | Unknown | MAIN SEWER BACKED UP JET TRUCK IN ROUTE | HOMEOWNER / PROPERTY MANAGER | <100GALLONS | MDC PERSONELL | No | 9761 | null | 2025-07-30 | 11:15 PM | <100GALLONS |  | null | JET TRUCK RELIEVED BLOCKAGE. | West Hartford | New Britain Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-07-16 | 07:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Also paper | Homeowner | <100 | Visual observation by MDC personnel | No | 9722 | null | 2025-07-16 | 10:00 AM | <100 Gallons |  | null | Main sewer flushed by jet truck and stoppage relieved | East Hartford | 26 Rector St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-07-12 | 10:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | PARTIAL BLOCKAGE DUE TO GREASE. | MDC SCADA | LESS THAN 500 GAL | MDC SCADA | Yes | 9710 | PARK RIVER CONDUIT | 2025-07-12 | 11:45 PM' | 800 GAL |  | null | JET TRUCK RELIEVED. | Hartford | Capitol Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-07-08 | 11:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT EXCESSIVE FLOWS | HOMEOWNER | <100G | MDC PERSONEL | No | 9695 | null | 2025-07-09 | 07:30 AM | <100g |  | null | WET WEATHER EVENT ENDED | Hartford | Morningside St W, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-06-24 | 02:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | MDC Personnel | <100 | Visual observation by MDC personnel | No | 9677 | null | 2025-06-24 | 03:00 PM | <100 |  | null | Main sewer flushed by jet truck and stoppage relieved | West Hartford | 10 Trotwood Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-05-29 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | EVERSOURCE DRILLED A POLE THROUGH THE SEWER MAIN | HOMEOWNER | >1000 GALLONS | MDC PERSONNEL | No | 9600 | null | 2025-05-30 | 12:30 PM | 17000 GALLONS PUMPED - BYPASS OF M/S ONLY - NO SPILL |  | null | SEWER MAIN WAS REPAIRED | Bloomfield | 1067 Blue Hills Ave, Bloomfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-05-14 | 01:00 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Mechanical Issues at pump stationSSO bypass started approx. 2:00pm | MDC PERSONNEL | > 5000 | MDC PERSONNEL | Yes | 9526 | Farmington River | 2025-05-14 | 08:45 PM | 25000gal |  | null | Pump bypass was setup to downstream manhole | Windsor | 34 Ridge St, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 03:00 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | HEAVY RAIN | SCADA | 400,000 GAL | SCADA | Yes | 9509 | TROUT BROOK | 2025-05-10 | 04:15 AM | 0.44 MG |  |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOMEOWNER CALLED MDC | LESS THAN 100 GAL | MDC PERSONEL | No | 9515 |  | 2025-05-10 | 07:30 AM | LESS THAN 100 GAL |  |  | EXTRANEOUS FLOWS IN MAIN SEWER RECEDED | West Hartford | 152 N Main St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONEL | LESS THAN 500 GAL | MDC PERSONEL | Yes | 9513 | TROUT BROOK | 2025-05-10 | 12:30 PM | LESS THAN 1,000 GAL |  |  | EXTRANEOUS FLOWS RECEDED IN MAIN LINE SEWER | West Hartford | 1 Linbrook Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 02:00 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | Heavy rain | SCADA | 2.3 MG | SCADA | Yes | 9507 | PIPER BROOK | 2025-05-11 | 02:30 PM | 9.13 MG |  |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONEL | LESS THAN 500 GAL | MDC PERSONEL | Yes | 9514 | TROUT BROOK | 2025-05-10 | 12:30 PM | LESS THAN 1,000 GAL |  |  | EXTRANEOUS FLOWS RECEDED | West Hartford | 3 Linnard Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 02:15 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | Heavy Rain | SCADA | 3.5 MG | SCADA | Yes | 9508 | TROUT BROOK | 2025-05-10 | 04:00 PM | 7.112 MG |  |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONEL | LESS THAN 500 GAL | MDC PERSONEL | Yes | 9512 | TROUT BROOK | 2025-05-10 | 12:30 PM | LESS THAN 1,000 GAL |  |  | RAIN EVENT ENDED EXTRANEOUS FLOWS RECEDED IN MAIN SEWER | West Hartford | N Main St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 05:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | .020 MG | MDC SCADA | Yes | 9464 | TROUT BROOK | 2025-05-06 | 10:15 AM | .007MG |  |  | RAIN EVENT ENDED FLOWS RECEDED | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 03:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | .010 MG | MDC SCADA | Yes | 9462 | TROUT BROOK | 2025-05-06 | 01:15 PM | 2.041 MG |  |  | RAIN EVENT ENDED FLOWS RECEDED | West Hartford | 121 Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 03:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 6.307 MG | MDC SCADA | Yes | 9463 | PIPER BROOK | 2025-05-07 | 02:30 AM | 6.461 MG |  |  | Bypass is eliminated once flows drop below overflow | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-04-20 | 07:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | MAIN SEWER BACKUP | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | No | 9396 |  | 2025-04-20 | 10:45 PM | < 100 GALLONS |  |  | JET-TRUCK RELIEVED SEWER BLOCKAGE | Hartford | 129 Woodland Dr, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-12 | 10:30AM | Basement | Raw Sewage | Sewage Line Blockage - Other | BYPASS DUE TO MAIN SEWER BACKED UP | HOMEOWNER | <100GALLONS | MDC PERSONNEL | No | 9365 |  | 2025-04-12 | 12:00 PM | <100GALLONS |  |  | JET TRUUCK RELIEVED MAIN SEWER | Hartford | 900 West Blvd, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-12 | 07:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | MAIN SEWER BACKED UP | CITY HARTFORD PUBLIC WORKS PASSER BY | <100GALLONS | MDC PERSONNEL | No | 9364 |  | 2025-04-12 | 12:00 PM | <100GALLONS |  |  | MAIN SEWER RELIEVED BY JET TRUCK | Hartford | S Whitney St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-04-07 | 10:30AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | MDC personnel | <100 | MDC personnel | No | 9350 |  | 2025-04-07 | 11:30 AM | <100 |  |  | Main sewer flushed by jet truck and stoppage relieved | East Hartford | 345 Main St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-03-21 | 10:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | MDC personnel | <100 | Visual by MDC personnel | No | 9274 |  | 2025-03-21 | 11:30 AM | <100 |  |  | Main sewer flushed by jet truck and stoppage relieved | East Hartford | 49 King St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-17 | 10:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | MDC personnel | <100 | MDC personnel | No | 9248 |  | 2025-03-17 | 10:45 AM | <100 |  |  | Main sewer flushed by jet truck and stoppage relieved | Windsor | 103 Poquonock Ave, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-03-14 | 03:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | WHFD CALLED MDC COMMAND CENTER | LESS THAN 1000 | MDC PERSONELL | Yes | 9227 | TROUT BROOK | 2025-03-14 | 06:45 PM | LESS THAN 25,000 |  |  | JETTED MAIN SEWER AND RELIEVED BLOCKAGE | West Hartford | 78 LaSalle Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 11:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | HOMEOWNER | < 100 | MDC PERSONNEL | No | 9190 |  | 2025-03-06 | 11:15 AM | <100 |  |  | Main sewer flushed by jet truck and stoppage relieved | West Hartford | 66-68 Levesque Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 11:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Homeowner | < 100 | MDC Personnel | No | 9191 |  | 2025-03-06 | 11:15 AM | <100 |  |  | Main sewer flushed by jet truck and blockage relieved | West Hartford | 67-69 Levesque Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 12:15 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Homeowner | <100 | MDC Personnel | No | 9193 |  | 2025-03-07 | 07:30 AM | <100 |  |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | West Hartford | 43 Wyndwood Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-06 | 01:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 1000 | SCADA | Yes | 9178 | TROUT BROOK | 2025-03-06 | 09:45 AM | 2.61 MG |  |  | BYPASS IS ELIMINITED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 09:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | HOMEOWNER | < 100 GALLON | MDC PERSONNEL | No | 9188 |  | 2025-03-06 | 09:45 AM | < 100 GALLONS |  |  | MAIN SEWER FLUSHED BY JET TRUCK AND STOPPAGERELIEVED | Hartford | 37 Chadwick Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 10:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | PER OUR SCADA SYSTEM | 1000 Gallons | SCADA SYSTEM | Yes | 9170 | PIPER BROOK | 2025-03-06 | 10:30 PM | 5.6 MG |  |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 83 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 11:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | null | PER OUR SCADA SYTEM | 1000 GALS | PER OUR SCADA | Yes | 9171 | TROUT BROOK | 2025-03-06 | 09:45 AM | 2.61 MG |  | null | Bypass is eliminated once flows drop below overflow | West Hartford | Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-02-03 | 01:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | SCADA | < 10,000 GALLONS | SCADA | Yes | 9070 | PARK RIVER CONDUIT | 2025-02-03 | 02:15 PM | 2,000 TOTAL GALLONS |  |  | FLUSHED SEWER MAIN WITH A JET TRUCK | Hartford | Capitol Ave, Hartford, CT
MERIDEN | Closed | Sewage Bypass | Dry | 2025-02-05 | 09:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease and rag buildup in manhole | Called in by homeowner of 90 Old Gate RD. Manhole is located in her backyard. | approx 75 gallons escaped. | Visual estimation | No | 9074 |  | 2025-02-05 | 10:30AM | approx 75 gallons |  |  | Line was jetted to relieve blockage | Meriden | 90 Old Gate Rd, Meriden, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2025-11-24 | 12:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | null | Call from Milford Building maintenance | 100 gal | estimate | No | 10134 | null | 2025-11-24 | 01:00 PM | 100 gallons |  | null | Jetted easement off Bird Lan to clear blockage and then drove onto easement to clear from Pond Point to French Drive. Follow up on Tues and Wed with CCTV of sewer main. | Milford | 66 Bird Ln, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2025-05-20 | 07:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Roots | null | Phone Message | 50 gallons | Estimated quantity was estimated. | No | 9564 | NA | 2025-05-20 | 09:00 AM | 50 gallons |  | null | Jet Truck cleared blockage | Milford | 16 Earle St, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2025-03-25 | 10:30AM | Basement | Raw Sewage | Select... |  | resident call | undetermined | undetermined | No | 9324 |  | 2025-03-25 | 01:00 PM | 20 gallons |  |  | roots cut and cleared | Milford | 39 Minute Man Dr, Milford, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2025-07-28 | 08:15 AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Poor bedding (i.e. cobbles, gravel) for the force main has caused several problems in this area before. FY 2026 CIP addressing issue. | CTDOT paving contractor (American Industry) notified the Montville WPCA. Reported to CTDEEP overnight. | 200 g | Estimated passed on flow observed. | No | 9755 | n/a | 2025-07-28 | 10:00 AM | 200 g |  | null | Pump Station bypass via Montville WPCF pumper truck then emergency contractor (B & W Paving & Landscaping, Waterford, CT) repair of FM line break. FY 2026 CIP project to repair line. | Montville | 2549 CT-32, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2025-04-02 | 01:30 PM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | n/a | Collections Operator check of previous release area. | 100 g | Estimated by visual inspection. Quick response due to routine inspection by Coll Operator of this previous release spot- FM from Kitemaug PS. | Yes | 9331 | Mohegan Brook | 2025-04-02 | 01:45 PM | 200 g |  |  | Pump Station pumps turned off- pumper truck draining wetwell with delivery to WPCF (for bypass of FM breached pipe). Emergency contractor onsite overnight for excavation/pipe repair. | Montville | 1 Kitemaug Rd, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2025-01-28 | 01:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | n/a | Public Works called to report odor in the vicinity of the surcharged manhole. | 200 g | Estimated quantity based on direct inspection. Responded immediately to vacuum/jet line and clean up toilet paper and released raw wastewater and spread lime. | No | 9062 | n/a | 2025-01-28 | 02:30 AM | 250 g |  |  | Jetting/Flushing line with vacuuming to remove rags in sewer main through cross-country. Flow re-established and confirm on both Jan 28 and 29. | Montville | 19 Brewer St, Montville, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2025-05-06 | 05:30 PM | Lateral - Private | Raw Sewage | Sewage Line Broken by Contractor or other utility | Work done by Contractor was thought to be the issue | Resident made call | Minimal in garage | Visual | No | 9651 | null | 2025-05-06 | 07:30 PM | Minimal |  | null | Line was jetted to clear out debris & resolve issue for homeowner / Contractor repair the damaged line the next day | Naugatuck | 65 May Ave, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-06 | 05:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | By operator | Between 15-17 MGD | Flow meter | No | 9473 | Naugatuck River | 2025-05-07 | 07:30 AM | Rain stopped, Flow stabilized around 10-11mgd |  |  | Solids stopped overflowing, flow slowed down.Clear effluent. | Naugatuck | 500 Cherry St, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-31 | 00:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | A previous lateral repair downstream caused rocks to fall into the main. | Homeowner discovered it | Approximately 300 gallons. | Estimated quantity was based off of the damage done to the basement. | No | 9306 |  | 2025-03-31 | 02:00 AM | 300 gallons |  |  | Jetting main sewer line. | Naugatuck | 118 Ward St, Naugatuck, CT
NEW BRITAIN | Open | Sewage Bypass | Dry | 2025-08-04 | 09:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease - Rags | Property owner called. | 90 gallons | Visual | No | 9781 | null | 2025-08-04 | 00:00 AM | 90 Gallons |  | null | Jet rod main sewer line. | New Britain | 205 Bingham St, New Britain, CT
NEW BRITAIN | Closed | Sewage Bypass | Dry | 2025-04-15 | 06:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags | Rags/Grease | Renter at 166 Broad St | 1500 Gallons | Visual | No | 9387 |  | 2025-04-15 | 07:00 PM | 1500 Gallons |  |  | Jet Rod Main Sewer Line | New Britain | 166 Broad St, New Britain, CT
NEW BRITAIN | Open | Sewage Bypass | Dry | 2025-04-10 | 10:30AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease |  | Property Owner | 500 gallons | Visual | No | 9362 |  | 2025-04-10 | 11:00 AM | 500 gallons |  |  | Jet Rod Main Line | New Britain | 178 Winfield Dr, New Britain, CT
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2025-10-25 | 00:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | 2 manholes were reported to customer service department as backed up. Upon the crews arrival they determined the sewer main (owned by the utility) was flowing fine but two manholes (privately owned by business) were clogged and causing the back up inside | Called in to the customer service line by the business owner of Popeyes Chicken. DPH Ledgelight Health was also notified of the situation. | Unknown, bypass on a private line. | N/A | No | 10062 | null | 2025-10-29 | 06:00 PM | Unknown, not reported to us by business owneer |  | null | Business owner hired an outside company to jetrod the blockages. | New London | 455 Colman St, New London, CT
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2025-10-03 | 12:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Excess build up an other debri in the large (30") gravity line feeding the STP. | Call in by local business owner reporting sewage smell in cove. | 673,920 gallons is estimated to have been bypassed to the environment since we were notified on 10/3/2025 | By using attached pipe flow sheet and assuming a velocity of 2 ft/sec | Yes | 9968 | Shaw Cove via underground storm culvert fed by storm catch basins and a storm pump station located on Howard Street NLCT. | 2025-10-05 | 01:30 AM | estimated 673,920 gallons |  | null | By clearing a blockage in a large sewer interceptor entering the STP | New London | 150 Howard St, New London, CT
NEW MILFORD | Closed | Sewage Bypass | Dry | 2025-02-18 | 09:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Homeowner called Sewer Department. | 500 Gallons | Visual Assessment. | No | 9124 |  | 2025-02-18 | 10:00 PM | 500 Gallons |  |  | Jetted main line and cleared grease blockage. | New Milford | 181 Wellsville Ave, New Milford, CT
NEWTOWN W P C F | Closed | Sewage Bypass | Dry | 2025-11-20 | 09:30 AM | Sewer Main | Raw Sewage | Other | Fitting went bad | A call was made to Public Works Office | 500 gallons | estimate | Yes | 10132 | On map it looks like Tom Brook - some flow (low) | 2025-11-20 | 02:00 PM | 500 gallons |  | null | repaired/replaced failed fitting | Newtown | 11 Edmond Rd, Newtown, CT
NORTH HAVEN WPCF | Open | Sewage Bypass | Dry | 2025-12-01 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Debris, gravel and roots | Resident called | 50 gallons total. This manhole only served one house | Visual | No | 10157 | null |  | null | null |  | null | null | North Haven | Kent Dr, North Haven, CT
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2025-08-13 | 05:30 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | the bypass was caused by severely eroded pipe in the downstream section of Carlson Ave. We installed a smart cover to alert us of any impending overflows and that cover has prevented several SSO's but in this case, the smart cover system did not send a t | App notification on the Iphone. | 500 gallons | Visual Observation | No | 9791 | null |  | null | Approx 500 gallons |  | null | the line was jetted. Construction to replace pipe will begin in early September. | Orange | Carlson Rd, Orange, CT
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2025-06-15 | 00:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | The pipe is severely deteriorating on the bottom, so debris is catching and plugging the pipe. There is some kind of defect at 200 ft that we cant visually locate. | Resident reported | <500 gallons | Visual estimate | No | 9657 | null | 2025-06-15 | 03:00 PM | < 500 gallons |  | null | We jet cleaned the pipe. We are going to jet clean this location weekly until the required repairs are made. We are also going to install a SMART COVER on 6/18/25 so that if the pipe backs up, we will get notification from the system that the pipe has a | Orange | Carlson Rd, Orange, CT
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2025-05-28 | 10:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease | STAFF PERFORMED A FOG INSPECTION ON 5/27/2025 AND FOUND SEVERE GREASE BUILD UP IN THE RESTAURANT DISCHARGE MANHOLE. I NOTIFIED BOTH THE RESAURANT MANAGER AND ALSO THE PROPERTY MANAGER. I ADVISED HIM TO HIRE A DRAIN CLEANER AND TO DO IT IMMEDIATELY BECAU | STAFF RECEIVED A PHONE CALL FROM THE "AT HOME" FURNISHINGS STORE TO REPORT THIER TOILETS WOULD NOT FLUSH. | 500-1000 GALLONS. DIFFICULT TO DETERMINE. | VISUAL OBSERVATION. | No | 9596 | null | 2025-05-28 | 10:30AM | estimated at 500 - 1000 gallons |  | null | United Sewer cleaning was called by the restaurant owner to clear all grease, the town issued a NOV per the grease regulations. We will follow up to ensure their equipment is properly maintained going forward. We found their AGRU was not being maintaine | North Haven | 350 Universal Dr N, North Haven, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-10-31 | 09:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | null | A resident called into the City of Norwalk's customer service. | Around 185 gallons. | Visual | Yes | 10091 | Norwalk River | 2025-10-31 | 10:00 AM | 185 gallons |  | null | Collections team cleared the blockage downstream . | Norwalk | 12 Lexington Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-07-23 | 07:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | The bottom of the manhole has failed/crumbled. | Nearby Stormwater inspection and dye testing | <0.5 GPM | CCTV footage of the Stormwater Line | Yes | 9744 | Norwalk River | 2025-07-24 | 12:00 PM | 870 Gals |  | null | A construction company rehabilitated the bottoms of the affected manholes with concrete. | Norwalk | 6 Gordon St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-07-11 | 07:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Failure of sewer main | Routine MS4 inspection of nearby Stormwater lines | ~0.25 GPM | Visually from CCTV footage | Yes | 9709 | Norwalk River | 2025-07-11 | 01:45 PM | ~101 Gal |  | null | A contractor replaced the broken section of clay pipe with PVC pipe. | Norwalk | 8 W Rocks Rd, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-02-16 | 09:00 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure |  | It was discovered during a maintenance mechanic daily check of the station. | 48,800 gallons | Previous flow trends and time of day | Yes | 9104 | Keeler Brook | 2025-02-16 | 10:15 AM | 48,800 gallons |  |  | Equipment was restored to full capacity. | Norwalk | 467 Connecticut Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-02-14 | 12:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | The basement at 12 Bouton St got backed up due to a blockage in the line. Causing the sump to discharge into a catch basin on Bouton St. | A Smart Cover alert. | 200 gallons | Vactor Truck | No | 9095 |  | 2025-02-14 | 12:15 PM | 200 gallons |  |  | Cleared blockage in Sanitry Sewer Main | Norwalk | 12 Bouton St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-01-15 | 07:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | First District called it in. | 5 gal/min, 30 minutes | Vactor Truck | Yes | 9029 | Betts Brook | 2025-01-15 | 07:30 AM | 110 gallons |  |  | Collection system crew was able free the blockage in the main sewer line | Norwalk | Park, Norwalk, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-10-15 | 03:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags | Manhole was blocked | Customer Call | 100 gallons | Visual Estimate | No | 10021 | null | 2025-10-15 | 04:00 PM | 100 gallons |  | null | NPU assisted with raking rags out of manhole, getting it to drain. Advised calling a plumber to jet and clean lines | Norwich | 181 W Town St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-08-29 | 11:45 AM' | Sewer Main | Raw Sewage | Other | On August 29, 2025, at approximately 11:40 AM, NPU was notified of a sanitary sewer overflow (SSO). The overflow was attributed to heavy rainfall combined with the tie over from a temporary force main to the newly lined force main. During the tie-in proce | During construction | 50000 Gallons | CSO-Amount from CSO 4 Plus Estimate | Yes | 9853 | Thames River | 2025-08-29 | 03:30 PM | 50000 Gallons |  | null | Force main returned to service. | Norwich | 190 S Thames St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-06-23 | 10:45 AM | Treatment Plant | Sludge Spill | Sewage Line Blockage - Rags | supernatant overflow line blocked wit rags | Operator working in area discovered | 300-500 gallons | Visual estimate. | Yes | 9671 | Yantic River West | 2025-06-23 | 12:00 PM | 500 gallons |  | null | blocked line was cleared. Bypass was directed to sump pumps pumping to headowrks. | Norwich | 44 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-06-03 | 07:00 AM | Treatment Plant | Sludge Spill | Mechanical Equipment Failure | Sludge carrier (HI STONE) had mechanical failure with cake dumpster latches | Hauler called NPU | approximately 4 yards of digester sludge cake | visual estimate | No | 9622 | null | 2025-06-03 | 07:15 AM | 4 Yards of cake, shoveled back into dumpster. NO CAKE ON GROUND |  | null | Picked up cake and cleaned area | Norwich | 44 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-06-03 | 07:15 AM | Sewer Main | Raw Sewage | Other | Excessive flows from fire hydrant flushing near CSO | Flow Meter | 3813 | Flow Meter | Yes | 9623 | Shetucket | 2025-06-03 | 07:15 AM | 3813 |  | null | stopped hydrant flushing | Norwich | 119 N Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-05-21 | 11:30 AM | Treatment Plant | Raw Sewage | Sewage Line Break, Crack or Failure | null | water bubbling from ground near junction chamber for both force mains entering the plant | none-water was leaking into vault.Flow Meter discharge for making repair on pipe. | Visual | No | 9567 | Shetucket | 2025-05-21 | 11:30 AM | 489031 |  | null | cleaned pipe and encased in concrete | Norwich | 52 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-05-19 | 10:00 AM | Sewer Main | Raw Sewage | Unknown | Possible malfunction of meter, or animal passed over sensor. No visible overflow in diversion structure. | Flow Meter report | 218 Total Gallons | Flow Meter | No | 9563 | Shetucket |  | 00:00 AM | 218 |  | null | Visual inspection of weir wall | Norwich | 385 N Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-05-07 | 09:45 AM | Sewer Main | Select... | Other | See Comments | Water leaking into the road | 53529 | Flow meter | Yes | 9482 | Shetucket | 2025-05-07 | 12:00 PM | 53529 |  |  | Water shut off, and repairs made | Norwich | 119 N Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-04-01 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Crack in the top of the pipe, it appears to have been an issue with the casting of the pipe from the manufacture. All other sections looked to be in great shape. | Customer call | 200gpm when pumping | 1600 gallons. Only leaks when pump was on. 200 gpm x 8 pump cycles. Plus some leaking while making repairs. 3000 Gallons | Yes | 9328 | Thames River | 2025-04-03 | 12:15 PM | 4600 |  |  | Replaced sections of pipe. 155inches=12' 10'' replaced | Norwich | 22 Thames Terrace, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-24 | 02:00 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Broken concrete distribution box. | Operators discovered while working | 500 gal | Visual rate | No | 9279 | N/A | 2025-03-24 | 02:15 AM | 500 gal |  |  | Used pump to pump back to headworks. | Norwich | 52 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 06:15 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Customer call | 665013 | Flow Meter plus visual estimate | Yes | 9158 | Yantic River/ Shetucket | 2025-03-06 | 03:45 PM | 659013+6000 (50 gpmx2 hrs)=665013 |  |  | Replace 230'' of 20'' DIP | Norwich | 46 W Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-01-30 | 02:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags |  | Call from plumber | 100 Gallons | Visual Estimate | No | 9065 |  | 2025-01-30 | 03:30 PM | 100 gals |  |  | plumber jetted line to clear blockage. Told he must clean up area around cleanout. | Norwich | 49 Boswell Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-01-16 | 06:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Customer call | No overflowing upon arrival- evidence of a small overflow | Visual estimate | No | 9036 |  | 2025-01-16 | 07:00 PM | 100 Gallons |  |  | Jetted main | Norwich | 413 E Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-01-10 | 03:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Partial blockage- evidence of spill- not actively overflowing | Customer Call | 200 gallons | Visual estimate | No | 9023 |  | 2025-01-10 | 03:30 PM | 200 Gallons |  |  | Sucked out manhole and jetted main. | Norwich | 48 Woodside Ave, Norwich, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-11-26 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 10147 | NEW HAVEN HARBOR | 2025-11-26 | 01:45 AM | 1.2128 MG Diverted |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-11-25 | 09:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 10142 | NEW HAVEN HARBOR | 2025-11-26 | 00:00 AM | 1.1167 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-31 | 00:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 10087 | NEW HAVEN HARBOR | 2025-10-31 | 06:00 AM | 6.0985 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-30 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual Observation | N/A | N/A | Yes | 10066 | Bridgeport Harbor Long Island Sound | 2025-10-31 | 04:30 AM | 5.78mg |  | null | Event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-30 | 05:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 10073 | NEW HAVEN HARBOR | 2025-10-31 | 00:00 AM | 1.7 in Rain |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-30 | 05:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual observation | N/A | N/A | Yes | 10065 | Cedar Creek Long Island sound |  | null | null |  | null | null | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-22 | 09:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 10050 | New Haven Harbor | 2025-10-22 | 10:00 AM | 0.1453 MG Diverted |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-20 | 05:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 10027 | NEW HAVEN HARBOR | 2025-10-20 | 06:00 AM | 0.2771 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-13 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 10007 | NEW HAVEN HARBOR | 2025-10-13 | 03:00 PM | 5.6650 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-12 | 07:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | Ongoing | Ongoing | Yes | 10002 | New haven Harbor | 2025-10-12 | 11:45 PM' | 2.1106 MG Diverted |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-08 | 09:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 9984 | NEW HAVEN HARBOR | 2025-10-08 | 10:00 AM | 0.3289 MG Diverted |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-09-24 | 06:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 9945 | NEW HAVEN HARBOR | 2025-09-24 | 07:30 AM | 0.1045 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-09-07 | 09:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9890 | NEW HAVEN HARBOR | 2025-09-07 | 11:30 AM | 1.1864 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-09-06 | 05:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 9876 | NEW HAVEN HARBOR | 2025-09-06 | 07:00 PM | 1.8868 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-09-06 | 05:00 PM | Select... | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual observation | N/A | N/A | Yes | 9871 | Cedar creek Long Island sound | 2025-09-06 | null | 2.21 MG |  | null | Rain Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
null | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-09-05 | 03:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 9860 | NEW HAVEN HARBOR | 2025-09-05 | 04:00 AM | 0.3413 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-08-21 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | Ongoing | Ongoing | Yes | 9825 | New Haven Harbor | 2025-08-21 | 01:30 AM | 1.8515 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-08-21 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual Observation | N/A | N/A | Yes | 9929 | Cedar Creek Long Island Sound | 2025-08-21 | 04:00 AM | 3.47 MG |  | null | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
null | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-08-20 | 11:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 9820 | NEW HAVEN HARBOR | 2025-08-21 | 00:00 AM | 1.2705 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-08-01 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Rain event | SCADA | 0.4886 MGD | SCADA | Yes | 9777 | NEW HAVEN HARBOR | 2025-08-01 | 00:45 AM | 0.1886 MGD |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-07-31 | 11:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Same as above | scada | 0.9389 MGD | SCADA | Yes | 9768 | New Haven Harbor | 2025-07-31 | 11:45 PM' | 0.9389 MGD |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-07-27 | 07:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | Same as above | SCADA | 0.9406 MGD | SCADA | Yes | 9754 | NEW HAVEN HARBOR | 2025-07-27 | 08:45 AM | 0.9406 MGD |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-07-20 | 09:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 9739 | NEW HAVEN HARBOR | 2025-07-20 | 10:45 PM | 0.5037 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-07-14 | 09:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 9720 | New Haven Harbor | 2025-07-14 | 11:00 PM | 1.3563 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 2-3" per hour | 2025-06-10 | 10:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | Ongoing | Ongoing | Yes | 9649 | New Haven Harbor | 2025-06-10 | 01:30 PM | 1.1724 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-31 | 03:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | SCADA | ONGOING | ONGOING | Yes | 9607 | NEW HAVEN HARBOR | 2025-05-31 | 06:00 AM | 2.9778 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-22 | 07:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | 9574 | NEW HAVEN HARBOR | 2025-05-22 | 12:30 PM | 2.2535 MG |  | null | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-09 | 01:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual Observation | N/A | N/A | Yes | 9498 | Cedar Creek Long Island Sound |  | null | null |  | null | null | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
null | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-09 | 01:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual Observation | N/A | N/A | Yes | 9566 | Cedar Creek Long Island Sound | 2025-05-09 | 04:15 PM | 4.06 MG |  | null | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-08-25 | 04:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | probable line break or previous construction debris. Upon arrival, we found construction stone 3/4 inch in the pipe which was likely allowed into the pipe during a recent new connection upstream. | reported by customer | 500 gallons | visual observation | No | 9835 | null | 2025-09-25 | 06:00 PM | ESTIMATED AT 500 GALLONS |  | null | VISUAL OBSERVATION | Orange | Boston Post Rd, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-06-30 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Responding technicians found that a large ball of rags has collected in the pipe. I reviewed the CCTV for this pipe section and there are no defects in the pipe. | Reported by a contractor working in the area. | 15-20 gallons | Visual observation | No | 9683 | null | 2025-06-30 | 12:00 PM | 20 gallons |  | null | jetting the sewer pipe. | Orange | 80 Boston Post Rd, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-06-12 | 12:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Blockage is due to deteriorating pipe. This pipe is in poor shape so rocks and aggregate are in the line. We cleared it the best we could during the last incident, in early February. | Resident reported to Bob Brinton, DPW director | <500 gallons | Visual estimate. | No | 9654 | null | 2025-06-12 | 02:00 PM | <500 gallons |  | null | Pipe Jetting | Orange | Bull Hill Ln, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-02-18 | 11:30 AM | Lateral - Public | Raw Sewage | Mechanical Equipment Failure | Private Pump station automatic operation failed. We are still following up with the property owner to determine the cause. | Staff discovered it when we were doing grease trap inspections. | <50 gallons | visual observation | No | 9122 |  | 2025-02-18 | 03:00 PM | less than 50 gallons |  |  | Building owner contacted to repair pump station. Robert Sacks was his name. He manually pumped the station down, and reported to us that the stations automatic operation had been restored by 3:00PM. We will follow up with him on recommended pump replac | Orange | 500 Boston Post Rd, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-02-14 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | 8 INCH ASBESTOS CONCRETE SEWER COLLAPSED DUE TO A SEVERELY COMPROMISED PIPE SECTION. | WE WERE NOTIFIED BY THE HIGHWAY DEPARTMENT SUPERINTENDENT. | LESS THAN 1,000 GALLONS | VISUAL OBSERVATION | No | 9094 |  | 2025-02-14 | 11:00 AM | <1,000 GALLONS |  |  | WE DUG UP THE CLOGGED PIPE, REMOVED ROCKS AND REPAIRED THE PIPE. MEETING WITH ORANGE DPW TO DETERMINE BEST COURSE OF ACTION TO REPLACE THAT PIPE ON 2/19/2025 | Orange | Carlson Rd, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-02-10 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | THE SEWER MAIN COLLAPSED AT 57 FT TO 70 FT. THE PIPE IS OLD ASBESTOS CEMENT, AND THE BOTTOM HAS WORN OUT OF IT. | Reported by Orange DPW. | Less than 100 gallons | Visual observation | No | 9084 |  | 2025-02-10 | 01:00 PM | ESTIMATED AT LES THAN 500 GALLONS |  |  | BRENNAN CONSTUCTION REPAIRED THE FAILED PIPE SECTION. | Orange | Carlson Rd, Orange, CT
PLAINFIELD NORTH WPCF | Closed | Sewage Bypass | Dry | 2025-08-18 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | resident called in to report issue. | 20-30 gallons | onsite estimation | No | 9801 | null | 2025-08-18 | 10:30AM | 20 gallons |  | null | Rodded and flushed line. | Plainfield | 19 Gorman St, Plainfield, CT
PLAINFIELD NORTH WPCF | Closed | Sewage Bypass | Dry | 2025-08-11 | 09:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | WPCA staff driving by location. | 50-100 gallons | onsite estimation | No | 9790 | null | 2025-08-11 | 09:45 AM | 50-100 gallons |  | null | sewer line was jetted about 100ft. | Plainfield | 19 Gorman St, Plainfield, CT
PLAINFIELD NORTH WPCF | Closed | Sewage Bypass | Dry | 2025-07-04 | 05:00 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | level control | routine station checks | 500gal | onsite evaluation, trickling out from manhole | Yes | 9691 | Moosup river | 2025-07-04 | 08:15 AM | 500gal |  | null | repaired level control | Plainfield | 376 Main St, Plainfield, CT
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2025-07-27 | 06:30 PM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure | Brown out blew motor starter. | Employee reported to work this morning and found it. | 500 gallons or less | Rate from telescope valve | Yes | 9757 | Mill Brook | 2025-07-28 | 04:45 AM | 500 Gallons or less |  | null | Replaced motor starters | Plainfield | 100 Birch St, Plainfield, CT
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2025-04-29 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | rags and wipes were found in the sewer main. | call from a local resident | 25-100 gallons | estimated gallons based on visual inspection. | No | 9427 |  | 2025-04-29 | 12:30 PM | 50 gallons |  |  | WPCA used a sewer rodder to clear out the blockage. | Plainfield | 19 Gorman St, Plainfield, CT
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2025-02-19 | 02:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | A blockage was found in sewer main. Some rock and debris was removed. | A plumber called WPCA to investigate sewer blockage | 300-1000 gallons | estimation based on a visual inspection of the manhole | No | 9135 |  | 2025-02-19 | 07:30 PM | 300-1000 gallons |  |  | The WPCA used a sewer rodder and a jet truck to break up the blockage. Any large debris found was removed. | Plainfield | 10 Terrace Dr, Plainfield, CT
PLAINVILLE WPCF | Open | Sewage Bypass | Dry | 2025-09-26 | 07:00 AM | Pump Station | Raw Sewage | Other | Shuttle Meadow Pump station being replaced with an upgraded station | Planned Station Replacement | 450,000 | Previous operation of station with flow meter attached | No | 9948 | null |  | 00:00 AM | null |  | null | null | Plainville | 66 Shuttle Meadow Rd, Plainville, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-30 | 08:15 PM | Manhole | Raw Sewage | Unknown | null | Called in to On-call operator | Unknown will updateestimated at 1/4 gpm. Less than 50 gallons | estimation of time and flow | Yes | 10082 | Spill did enter catch basin | 2025-10-30 | 10:00 PM | less than 50 gallons |  | null | cleared with jet truck | Plymouth | 42 Beach Ave, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2025-07-10 | 06:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Called in to PD | less than 50 gallons | Estimated by operator at less than 0.5 GPM | No | 9705 | Did not reach waterbody | 2025-07-11 | 02:00 AM | less than 200 gallons |  | null | Had to hire contractor to jet line | Plymouth | 12 Burr Rd, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2025-04-16 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags |  | called in | less than 50 gallons | Very low flow area, Flow just trickling out of manhole | No | 9394 |  | 2025-04-16 | 11:15 AM | less than 50 gallons |  |  | WPCA Operators cleared line with jet truck | Plymouth | 16 Dewey Ave, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2025-01-03 | 08:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags | Rags and Grit | On-call operator was called in | Some sewage entered home owners basement.Less than 10 gallons | Was only told sewer entered residents basementReceived pictures from Resident | No | 9012 |  | 2025-01-03 | 10:30 PM | less than 10 gallons |  |  | Plymouth WPCA staff jetted and cleared blockage. Contractor scheduled to clean and vac lines Friday 1/10/2025 | Plymouth | 11 Dewey Ave, Plymouth, CT
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2025-03-06 | 11:00 AM | Sewer Main | Raw Sewage | Other | Looks to be a broken force main pipe from our Copps Hill Pump Station. | Called in by nearby homeowner. | > 2000 gallons | visual estimate | Yes | 9192 | Great Swamp | 2025-03-06 | 11:30 AM | Approximately 2500 gallons. |  |  | The break in the force main was located after digging up the road. The pipe was repaired. | Ridgefield | 30 Island Hill Ave, Ridgefield, CT
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2025-03-06 | 11:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Pump Station force main was found to have a hole in the 8-inch force main. | The force main break was called into us by homeowner. | We are estimating approximately 2000 to 3000 gallons. | Visual estimate, upon finding the broken force main we shut down the pump station. | Yes | 9216 | Great Swamp/Ridgefield Brook | 2025-03-06 | 11:30 AM | Approximately 2000 - 3000 gallons |  |  | Pump Station was shut down. Local contractor located the broken force main and made repairs to the pipe. | Ridgefield | 30 Island Hill Ave, Ridgefield, CT
SEYMOUR WPCF, TOWN OF | Open | Sewage Bypass | Dry | 2025-10-08 | 01:00 PM | Treatment Plant | Sludge Spill | Other | Today We cleaned a siphon, we disposed the rags and debris at the dumpster located at the wastewater plant headwork. However the dumpster got full and some liquid runoff to the ground then slowly got into on of the small creek or may me is just a ditch n | As soon the dumpster got overfilled, and wastewater was running out of the dumpster, at this time operator notice it. | About 500 ml.. see pictures | Just visualize and from runoff until it got stopped. | No | 9991 | Dont know it is a very small creek outside the wastewater plant. Does not have a name, it may be just a ditch. |  | null | null |  | null | null | Seymour | 723 Derby Ave, Seymour, CT
SHELTON | Closed | Sewage Bypass | Dry | 2025-03-13 | 04:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | Also blockage with grease, rags, and roots. | Resident called with potential back-up. Could not flush toilet. No overflow into house. | 0 gallons | No actual overflow. | No | 9228 | N/A | 2025-03-14 | 04:30 PM | 0 - blockage in main was cleared of all debris |  |  | Televised, jetted, vacuumed, all debris, grease, rags, roots cleared. | Shelton | 159 Division Ave, Shelton, CT
SHELTON | Closed | Sewage Bypass | Dry | 2025-03-13 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | Resident called. | 200 gallons | Visual | No | 9226 | N/A | 2025-03-13 | 04:00 PM | 250 gallons |  |  | Main line jetted. Grease removed. | Shelton | 11 Meadow St, Shelton, CT
SHELTON | Closed | Sewage Bypass | Snowmelt | 2025-02-14 | 11:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | UI utility observed bubbling in easement and notified Sewer department. | 400 gallons | Visual | No | 9123 | N/A | 2025-02-15 | 02:00 PM | 500 |  |  | Vac truck on site and main line jetted. | Shelton | Shelton, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2025-05-10 | 12:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Siphon restricted with debris | HOA President called about multiple basement backing up | Less than 500 gallons | Visual estimation by operator | Yes | 9518 | Farmington River | 2025-05-10 | 03:30 PM | 900 gallons |  |  | jetted syphon to clear restricted pipe | Simsbury | 32 White Water Turn, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:15 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Main line at capacity flowing through syphon | Homeowner called in | 250 gallons | estimated by amount of water on floor | No | 9517 |  | 2025-05-09 | 08:15 PM | 250 gallons |  |  | Rain event ended | Simsbury | 38 White Water Turn, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2025-05-01 | 12:00 PM | Select... | Raw Sewage | Other | Influent bar screen was impacted by rags from septage haulers which created a back up into the dewatering room drain. water exited the dewatering room onto pavement area. | Operator rounds | 25 gallons | area covered | No | 9431 |  | 2025-05-01 | 12:15 PM | 25 gallons |  |  | placed influent bar screens in hand to remove debris that was restricting flow. | Simsbury | 36 Drake Hill Rd, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-06 | 11:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags |  | Resident reported | 15 gallons | estimated by on material on ground | No | 9017 |  | 2025-01-06 | 11:15 AM | 15 Gallons |  |  | Vacuumed manhole and jetted lateral, disinfected area | Simsbury | 933 Hopmeadow St, Simsbury, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-13 | 10:30AM | Sewer Main | Raw Sewage | Other | Excessive flow caused by CT Water flushing hydrants into the sanitary sewer* No bypass this was a CT Water manhole | Parks employee called in for manhole cover off of frame | 0 | We determined the water that was coming out of the CT Water manhole was flushing water not sewage | No | 10016 | null | 2025-10-13 | 10:30AM | Zero gallons |  | null | Discovered this was a CT Water manhole | South Windsor | 178 Foster St, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2025-08-14 | 07:30 AM | Treatment Plant | Fully treated raw sewage except disinfection | Mechanical Equipment Failure | null | We were there when it happened | 777 gallons | We lost UV for 1 minute at 1.19 mgd which is equal to 777 gpm | Yes | 9794 | Connecticut River | 2025-08-14 | 07:30 AM | 777 gallons |  | null | Turned other bank on | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2025-06-30 | 11:45 AM' | Treatment Plant | Fully treated raw sewage except disinfection | Other | Power outage | I knew as soon as we lost power | Approximately 1100 gallons | Based on flow rate at the time of the power loss | Yes | 9682 | Connecticut River | 2025-06-30 | 01:15 PM | Around 1100 gallons |  | null | Generator power kicked on, commercial power restored by 1:15 pm | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2025-06-05 | 09:30 AM | Treatment Plant | Fully treated raw sewage except disinfection | Electrical Equipment Failure | null | Operators who were resetting the PLC noted that the UV lamps all turned off for about 15 seconds | 520 gallons | By looking at flow data in correlation with the amount of time the UV was down | Yes | 9625 | Connecticut River | 2025-06-05 | 09:30 AM | 520 gallons |  | null | Lamps relit on their own after 15 seconds | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2025-06-25 | 12:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | null | Resident at 115 Howard Avenue noticed water in their basement. | 25 gallons | Estimated | No | 9679 | null | 2025-06-25 | 02:30 PM | 25 gallons |  | null | Southington WPC staff jetted the line to relieve the blockage. | Southington | 115 Howard Ave, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2025-02-01 | 04:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Town of Southington WPC staff noticed a surcharged manhole. Town of Southington WPC staff began jetting the sewer main to relieve the blockage, but ran into an unusual amount of rocks, gravel, and dirt. | 2 gallons | Estimate | No | 9068 |  | 2025-02-01 | 05:00 PM | 2 gallons |  |  | Section of broken pipe was replaced by contractors. | Southington | 868 Meriden-Waterbury Turnpike, Southington, CT
STAFFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 04:00 AM | Treatment Plant | Fully treated raw sewage except disinfection | Mechanical Equipment Failure | RAS pump failure caused by power loss. | Start of shift at 6:30 am | 10,000 gallons | calculation of flow | Yes | 9180 | Willimantic River | 2025-03-06 | 07:00 AM | 10,000 gallons |  |  | Power returned to RAS pumps, polymer add to tanks for faster settling. | Stafford | 50 River Rd, Stafford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2025-10-20 | 08:30 AM | Sewer Main | Raw Sewage | Other | Sewer line was surcharged and leak occurred via open sewer line joint. | WPCA staff were conducting routine flow inspections and observed the surface discharge. | 5-gallons | Wetted area was estimated. | No | 10039 | null |  | null | null |  | null | null | Stamford | 75 W Broad St, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2025-09-10 | 02:15 PM | Treatment Plant | Fully treated raw sewage except disinfection | Other | Power Failure | Arching on pole outside plant | 7,291 | Flow rate at the time of power failure multiplied by time it took UV disinfection to come back on line. | Yes | 9914 | Stamford Harbor, East Branch | 2025-09-10 | 02:15 PM | 7291gallons |  | null | Emergency generation | Stamford | 111 Harbor View Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2025-02-10 | 09:00 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Force main break. | Another agency reported the incident. | Approximately, 300 gals. | Volume was determined based on pump capacity and run-time. | No | 9083 | Unknown at this point in time. | 2025-02-10 | 09:30 AM | Approximately, 300 gals. |  |  | Crews are responding to contain wastewater, while contractor has mobilized to begin the repair work. | Stamford | 110 Burwood Ave, Stamford, CT
STONINGTON-PAWCATUCK WPCF | Open | Sewage Bypass | Dry | 2025-06-09 | 01:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | null | Passer by called it in. | <10 gallons | Estimated from observance | No | 9639 | null |  | null | null |  | null | null | Stonington | Mary Hall Rd, Stonington, CT
SUFFIELD | Closed | Sewage Bypass | Dry | 2025-08-10 | 02:00 PM | Manhole | Raw Sewage | Mechanical Equipment Failure | The force main air release valve was leaking | Calls were reported about water in the road | 5 gallons per minute or less for approximately 2.5 hours, 750 gallons or less. | visual estimate of it bubbling up through a hole in the manhole cover. | Yes | 9788 | Rawlins brook. The overflow went into a catch basin and storm pipes that ultimately lead to Rawlins brook. The storm sewer outfall was checked but no obvious discharge was noticed going into the brook (picture) | 2025-08-10 | 04:30 PM | 750 gallons |  | null | The air release valve was able to be shut off and isolated. | Suffield | 703 East Street N, Suffield, CT
THOMASTON WPCF | Closed | Sewage Bypass | Dry | 2025-09-18 | 12:00 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Broken force main | leak in road called in by public works dept. | 500 gallons | pump rates | No | 9928 | null | 2025-09-18 | 06:30 PM | 500 gallons |  | null | broken force main was repaired | Thomaston | 95 Kennedy Dr, Thomaston, CT
TOLLAND | In Progress | Sewage Bypass | Snowmelt | 2025-02-03 | 02:15 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Coupler on force main failed causing the leak | Public Works employees called Director to notify him of "water" in the road. | Undetermined | Undetermined | Yes | 9073 | Paulk Hill Brook We're not sure how much, if any, made it to the brook after it ran off into the abutting grass, wood line areas. There was significant snow melt occurring during the day, so there was already running water in the gutters / edge of roadwa | 2025-02-03 | 04:15 PM | Bypass pumping was discharged back into our system down flow from where the issue had taken place. Captured effluent from immediate work area was hauled away by septic hauler. |  |  | Removed broken clamps, cut out 2' section of ductile iron pipe and installed two new 6" lug coupling clamps | Tolland | 111 Old Post Rd, Tolland, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2025-08-10 | 10:30 PM | Treatment Plant | Raw Sewage | Other | Septic tank overflowed -High Level Alarm not triggered | When staff arrived, 8/11/2025 at 7am | less than 100 gallons | visual -didn't enter catch basin | No | 9789 | null |  | null | null |  | null | null | Harwinton | 252 Bogue Rd, Harwinton, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-06 | 12:15 PM | Sewer Main | Raw Sewage | Unknown | cause of blockage unknown. cleared with vactor rather easily | homeowner noticed sewage coming from manhole cover in sidewalk | 40 gallons per min | estimated visually | No | 9477 | null | 2025-05-06 | 12:45 PM | 1800 gal. |  | null | cleared blockage with jetter truck | Torrington | 991 E Main St, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2025-03-07 | 06:30 AM | Manhole | Raw Sewage | Unknown | null | call from public, that manhole was overflowing | 10gph | estimated | No | 9195 | null |  | null | null |  | null | null | Torrington | 140 Main St, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2025-03-02 | 03:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | unknown probably rag buildup | private person noticed it | 2 gallons per minute | visual estimation | Yes | 9151 | troy brook |  | null | null |  | null | null | Torrington | 200 Kennedy Dr, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2025-02-25 | 12:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | null | We received a call from the public | quantity unknown. rate estimated 5 gallons per minute | guestimate by visual observation | Yes | 9143 | gulfstream |  | null | null |  | null | null | Torrington | 1143 New Litchfield St, Torrington, CT
TRUMBULL | Open | Sewage Bypass | Dry | 2025-10-09 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Forcemain failure | Drive by inspection by WPCA employee | 3 gallons per hour | Visual of the leak and associated puddling. | No | 9994 | null |  | null | null |  | null | null | Trumbull | 6528 Main St, Trumbull, CT
TRUMBULL | In Progress | Sewage Bypass | Dry | 2025-05-27 | 10:45 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Unknown reason for failure at this time | Resident notification by phone | 1 gallon an hour +- | Visually estimated the flow | No | 9593 | null |  | null | null |  | null | null | Trumbull | 6466 Main St, Trumbull, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2025-10-09 | 05:00 PM | Lateral - Private | Raw Sewage | Mechanical Equipment Failure | Submarine/sewer Pipe connection | Watch stander reported it during operation | 30 gallons on the pier, possibly some into the water via scuppers...nothing visible | Operator estimate based on pump rate and immediate shutdown when notified of condition. | Yes | 9995 | Thames river; nothing seen but probable that some cleared the pier--Fire Department and base Public works personnel reported nothing visible. | 2025-10-09 | 05:00 PM | 30 gallons |  | null | Stopped pumping, disconnected hoses for Public works utilitty inspection | Groton | Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | In Progress | Sewage Bypass | Dry | 2025-08-07 | 07:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Broken pipe/damaged equipment. | Visual and dye-test performed. | 5-10 gallons, initial release. Unknown amount through small leak (secured). | Visual, based on rough time of when pipe break was discovered, up until it was secured. | Yes | 9786 | Thames River |  | null | null |  | null | null | Groton | Military Hwy, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2025-01-22 | 08:15 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Drydock pumping line break. | CHT spill at Pier 15 noticed by crew. CHT pumped from ship leaking to pier. More to follow. | 10 Gallons to water. | Visual from drydock crew who seized operations as soon as they noticed the leak after initially beginning pumping. | Yes | 9047 | Thames River | 2025-01-23 | 08:30 AM | 10 Gallons |  |  | Pumping stopped and line repaired. | Groton | 173 Dorado Rd, Groton, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-11-18 | 09:30 AM | Lateral - Private | Raw Sewage | Other | Blockage in a private curb box | DPH received a call | 50-60 gallons | Visual | Yes | 10131 | Naugatuck River | 2025-11-22 | 01:30 PM | DPH reports 75 gallons |  | null | • Case was assigned to Inspector Eddy on 11/18/2025.• Inspector Eddy spoke with the landlord on 11/18/2025 and the landlord stated that he would have the blockage abated and cleaned • On 11/22/2025, the re-inspection was conducted and the sewage bac | Waterbury | 82-84 Fairview St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-10-31 | 05:15 PM | Lateral - Private | Raw Sewage | Other | Blockage in private lateral | Qalert system | 20-30 gallons | visual | Yes | 10092 | Naugatuck river | 2025-11-04 | 10:00 AM | DPH reports 40 gallons |  | null | • Case was assigned to Inspector Eddy on 10/31/2025.• Inspector Eddy spoke with the landlord on 11/1/2025 and the landlord stated that he would have the blockage abated and cleaned • On 11/4/2025, the re-inspection was conducted and the sewage backu | Waterbury | 52 Washington St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-10-29 | 11:15 AM | Lateral - Private | Raw Sewage | Unknown | This is a private curb box | Qalert system | 5-10 gallons | Visual | No | 10061 | N/A | 2025-10-31 | 09:00 AM | DPH reports 50 gallons as the final quantity |  | null | • Case was assigned to Inspector Wood on 10/29/2025.• Inspector Wood spoke with the landlord on 10/29/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 10/31/2025, the re-inspection was conducted and | Waterbury | 319 Cooke St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-10-06 | 12:30 PM | Lateral - Private | Raw Sewage | Unknown | Unknown Private lateral | Qalert system | 15 gallons | Visual | No | 9971 | N/A | 2025-10-10 | 06:00 PM | DPH reports 100 gallons |  | null | • Case was assigned to Inspector Simoes on 10/06/2025.• Inspector Simoes spoke with the landlord on 10/06/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • 10/09/2025 Landlord stopped accepting my calls | Waterbury | 54 Niagara St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-09-04 | 02:15 PM | Lateral - Private | Raw Sewage | Unknown | Not known. DPH to monitor | Qalert system | 30 gallons | Visual | Yes | 9854 | Naugatuck river | 2025-09-08 | 10:00 AM | DPH reports 75 Gallons |  | null | • Case was assigned to Inspector Simoes on 09/04/2025.• Inspector Simoes spoke with the landlord on 09/04/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 09/08/2025, the re-inspection was conducted | Waterbury | 727 Baldwin St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-08-09 | 06:15 AM | Lateral - Private | Raw Sewage | Unknown | Unknown | WTB police Dept contacted manager | 35 gallons | Visual | No | 9787 | N/A | 2025-08-11 | 11:00 AM | DPH estimated 75 gallons |  | null | • Case was assigned to Inspector Wood on 08/09/2025.• Inspector Wood spoke with the landlord on 08/09/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 08/11/2025, the re-inspection was conducted and | Waterbury | 225 Bishop St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-07-25 | 07:45 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | UPS failure | SCADA system alarm | 25 gallons | Visual using SSO calculator | No | 9749 | null | 2025-07-25 | 08:00 PM | 25 gallons |  | null | Backup float put in manual | Waterbury | 46 Terrell Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-07-17 | 12:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | Qalert system | 20 Gallons | Visual by DPH | Yes | 9723 | Mad river | 2025-07-19 | 03:00 PM | DPH Reports 50 gallons |  | null | • Case was assigned to Inspector Ortiz on 07/17/2025.• Inspector Ortiz spoke with the landlord on 07/17/2025 and the landlord stated that he would have a sanitation company to pump out the septic tank and address any issues.• On 07/19/2025, the re-i | Waterbury | 484 Waterville St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-07-17 | 12:15 PM | Lateral - Private | Raw Sewage | Other | Curb box blockage | Qalert system | 20 | Visual | Yes | 9743 | Mad River | 2025-07-21 | 03:00 PM | 55 gallons |  | null | Remediation Action: • Case was assigned to Inspector Watson on 07/17/2025.• Inspector Watson spoke with the landlord on 07/17/2025 and the landlord stated that he would have the blockage abated and cleaned. • On 07/21/2025, the re-inspection was con | Waterbury | 285 Cooke St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-07-14 | 02:00 PM | Lateral - Private | Raw Sewage | Other | Septic system failure | Resident called customer service | 30-40 gallons | Visually | No | 9714 | null | 2025-07-16 | 03:00 PM | DPH reports 50 gallons |  | null | • Case was assigned to Inspector Watson on 07/14/2025.• Inspector Watson spoke with the landlord on 07/14/2025 and the landlord stated that he would have a sanitation company to pump out the septic tank and address any issues.• On 07/16/2025, the re | Waterbury | 363 Berkeley Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-06-09 | 11:00 AM | Lateral - Private | Raw Sewage | Other | blockage in private lateral/curb box | tenant called customer service | 5 gallons | Visually | No | 9640 | N/A | 2025-06-10 | 06:00 PM | DHP estimates 50 gallons |  | null | • Case was assigned to Inspector Wood on 06/09/2025.• Inspector Wood spoke with the landlord on 06/09/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 06/10/2025, the re-inspection was conducted and | Waterbury | 126 Cherry St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-05-25 | 11:45 AM' | Manhole | Raw Sewage | Unknown | Blockage at the manhole | Water Dept employee noticed the manhole discharging | 750 gallons | Sewer manhole overflow chart. 50 gpm X 15 minutes = 750 gallons | No | 9591 | Mad river | 2025-05-25 | 12:00 PM | 750 gallons |  | null | Jetter truck released blockage and flow returned to normal. | Waterbury | 418 Pine St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-04-22 | 01:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | CCTV camerawork determined that roots were the cause of the blockage in the city line | Qalert system | Jacobs estimates 30 gallons | Visual | No | 9401 |  | 2025-04-22 | 02:15 PM | 30 gallons |  |  | A jetter truck was dispatched to clear the blockage. Also added to the maintenance plain to root cut once per year. | Waterbury | 89 Clowes Terrace, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-04-11 | 12:15 PM | Lateral - Private | Raw Sewage | Sewage Line Break, Crack or Failure | private lateral is compromised | Health Department reported the issue | 30 gallons | Visually of affected area | No | 9361 | N/A | 2025-04-14 | 10:30AM | DPH reports 60 gallons |  |  | Remediation Action: • Case was assigned to Inspector Eddy on 04/11/2025.• Inspector Eddy spoke with the landlord on 04/11/2025 and the landlord did stop the flow by putting the plug back in the lateral pipe. Landlord is in the process of finding out | Waterbury | 567 S Leonard St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-04-10 | 02:15 PM | Lateral - Private | Raw Sewage | Other | potential blockage in private manhole | Resident called customer service | 40 gallons | visually | Yes | 9360 | Mad river interceptor | 2025-04-14 | 05:45 AM | DPH reports 50 gallons |  |  | • Case was assigned to Inspector Eddy on 04/10/2025.• Inspector Eddy spoke with the Property Manager on 04/10/2025 and he stated that he would have the blockage abated and cleaned. • On 04/14/2025, the re-inspection was conducted and the sewage back | Waterbury | 950 Wolcott St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-26 | 06:15 PM | Lateral - Private | Raw Sewage | Other | Blockage in Private lateral | Qalert system | 40 gallons | Visual | Yes | 9297 | Mack Brook | 2025-03-30 | 02:30 PM | DPH estimates the final quantity to be 60 gallons |  |  | • Case was assigned to Inspector Nelson Simoes on 03/28/2025.• Inspector Nelson Simoes spoke with the landlord on 03/28/2025 and the landlord stated that he would have the blockage abated and cleaned. • On 03/30/2025, the re-inspection was conducted | Waterbury | 543 Chase Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-20 | 09:30 AM | Lateral - Private | Raw Sewage | Unknown | Blockage | Qalert system | 10-15 gallons | Visual | No | 9262 |  | 2025-03-25 | 03:30 PM | DPH reports 20 gallons |  |  | • Case was assigned to Inspector Manuel on 03/20/2025.• Inspector Manuel spoke with the Tenants on 03/20/2025 and the Tenant stated that he would have the blockage abated and cleaned. • On 03/25/2025, the re-inspection was conducted and the sewage b | Waterbury | 228 Wood St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-12 | 09:30 AM | Lateral - Private | Raw Sewage | Unknown | This is a private by-pass | Field crew notice while doing CBYD | 100 gallons | visual | Yes | 9220 | Naugatuck river | 2025-03-13 | 09:30 AM | DPH reports 150 gallons |  |  | • Case was assigned to Inspector Tom Watson on 03/12/2025.• Inspector Tom Watson spoke with the property management on 03/12/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 03/13/2025, the re-inspec | Waterbury | 31 Nottingham Terrace, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-03 | 02:15 PM | Lateral - Private | Raw Sewage | Unknown |  | A Passerby called in | 15 gallons | Visual | No | 9152 | N/A | 2025-03-07 | 08:00 AM | DPH reports 50 gallons |  |  | • Case was assigned to Inspector Manuel on 03/03/2025.• Inspector Manuel spoke with the landlord on 03/03/2025 and the landlord stated that he would have the blockage abated and cleaned. • On 03/12/2025, the re-inspection was conducted and the sewag | Waterbury | 603 N Main St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-02-01 | 05:30 PM | Lateral - Private | Raw Sewage | Unknown | Unknown | WTB fire Dept contacted Jacobs | 30 gallons | visual | No | 9069 |  | 2025-02-11 | 03:00 PM | DPH reports the final quantity to be 40 gallons |  |  | • Case was assigned to Inspector Eddy on 02/1/2025.• Inspector Eddy issued a Notice of Violation on 02/3/2025• On 2/7/25 Inspector Eddy spoke to the property owner and he stated that he would abate the sewage backup. • On 02/11/2025, the re-inspec | Waterbury | 84 Fairview St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-24 | 10:45 AM | Lateral - Private | Raw Sewage | Unknown | This is a septic system failer at 156 Perkins Ave | Call from the Water Dept. | 75 gallons | Visual | No | 9051 |  | 2025-01-28 | 03:00 PM | DPH reports 50 gallons |  |  | • Case was assigned to Inspector Eddy on 01/24/2025.• Inspector Eddy spoke with the landlord on 01/24/2025 and the landlord stated that he would have Wolcott Sanitation pump out the septic tank and address any issues.• On 01/28/2025, the re-inspecti | Waterbury | 156 Perkins Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-21 | 01:45 PM | Lateral - Private | Raw Sewage | Other | Unknown | Qalert system | 10-15 gallons | Visual | No | 9046 |  | 2025-01-27 | 12:00 PM | DPH reports total quantity to be 75 gallons |  |  | • Case is assigned to Inspector Simoes on 01/21/2025.• Inspector Simoes got in touch with the landlord on 01/23/25. The landlord stated that he would have the blockage abated. • On 01/27/2025, the re-inspection was conducted and the sewage backup wa | Waterbury | 38 High St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-19 | 03:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | debris found in manhole | Water Department contacted Jacobs | 1,250 gallons | SSO calculator | Yes | 9042 | Beaver Brook | 2025-01-19 | 03:45 PM | 1,250 gallons |  |  | A jetter truck Released the blockage and regained normal flow. | Waterbury | 106 Arline Dr, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-08 | 09:45 AM | Lateral - Private | Raw Sewage | Other | Unknown. This is a private lateral issue | Qalert system | 25 gallons | Visual by field tech | No | 9021 | N/A | 2025-01-09 | 03:00 PM | DPH reports 50 gallons |  |  | • Case was assigned to Inspector Watson on 01/07/2025.• Inspector Watson spoke with the landlord on 01/07/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 01/09/2025, the re-inspection was conducted | Waterbury | 603 N Main St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-06 | 08:15 AM | Lateral - Private | Raw Sewage | Other | Blockage in private lateral | Field crew | 20 gallons | Visual by field crew | Yes | 9015 | Mad River interceptor | 2025-01-07 | 03:00 PM | DPH reports 15 gallons |  |  | • Case was assigned to Inspector Manuel on 01/06/2025.• Inspector Manuel spoke with the landlord on 01/06/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 01/07/2025, the re-inspection was conducted | Waterbury | 376 Walnut St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-02 | 11:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Jacobs field crew during daily maintenance in city noticed the surging manhole. | 50 gallons | Visual | Yes | 9002 | Mad river interceptor | 2025-01-02 | 11:45 AM' | 50 gallons |  |  | Jacobs WPC cleared blockage | Waterbury | 174 Orange St, Waterbury, CT
WATERFORD | Closed | Sewage Bypass | Dry | 2025-08-23 | 08:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Crack in 45 elbow | Surface water | Less than 100 gallons | Visual inspection | No | 9833 | null | 2025-08-25 | 05:00 PM | Approximately 100 gallons |  | null | Cracked 45 was removed and replaced by contractor | Waterford | 253A Shore Rd, Waterford, CT
WEST HAVEN | Open | Sewage Bypass | Rain less than 1" per hour | 2025-11-25 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | line upstream collapsed causing mh# 13-193 to bypass during peak flow times. | called in from dpw | approx 30 to 50 gallons intermittently during peak flow times | visual inspection | Yes | 10154 | drainage is upstream from west river |  | 00:00 AM | null |  | null | null | West Haven | 4 Spring St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2025-11-07 | 09:00 AM | Lateral - Private | Raw Sewage | Unknown | null | property owner called in a backup , but blockage is in the private system | 50 gallons | visual inspection | Yes | 10112 | cove river | 2025-11-07 | 11:00 AM | 50 to 60 gallons |  | null | property owner had plumber jet the blockage | West Haven | 125 Coleman St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-09-25 | 04:00 AM | Manhole | Raw Sewage | Mechanical Equipment Failure | main pumping station had excessive flow from rain | alarm system high well alert | approx 100 gallons | visual inspection | Yes | 9947 | old field creek | 2025-09-25 | 05:15 AM | approx 100 gallons |  | null | station came back into control when flows slowed down | West Haven | 98 Blohm St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2025-09-15 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage | Property owner | 50 gallons | Visual | No | 9921 | null | 2025-09-15 | 12:00 PM | 50 gallons |  | null | Jetted blockage and vacumed out debris | West Haven | 20 Industry Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2025-08-22 | 10:00 AM | Manhole | Raw Sewage | Other | Contractor used flow through plug to work on manhole lining and surcharged the main | Homeowner called in | 100 gallons | Visual | Yes | 9831 | Lake phipps, to cover river | 2025-08-22 | 10:30AM | 100 gallons |  | null | Pulled contractor off project released his flow.through plug | West Haven | 21 Phipps Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-31 | 12:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | grease blockage in sanitary main | property manager | 150 gallons | visual inspection | No | 9620 | null | 2025-05-31 | 01:00 PM | 150 gallons |  | null | jetted grease blockage | West Haven | 282 Terrace Ave, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-17 | 08:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | by phone from customer (Shala Lindsay) | 100 gal | Visually | No | 9249 |  | 2025-03-17 | 09:00 AM | 100 gal |  |  | AMH 2-54 was unplugged w/ Vacall truck. Service Master was called for basement cleanup. | West Haven | 23 Batt Ln, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2025-01-17 | 02:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | heavy grease and property owners do not do maintenance on a routine basis | resident | 80 gallons | visual | Yes | 9041 | possibly made it to waterbody this storm drainage system makes it way to cove river at some point downstream | 2025-01-17 | 08:00 PM | 80 gallons |  |  | jetted the private main and vacuumed out debris ,washed down street while vacuuming cleanup | West Haven | 23 Treat St, West Haven, CT
WINDSOR LOCKS WPCF | Closed | Sewage Bypass | Dry | 2025-10-21 | 01:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | null | Property owner where the Sewer main is located discovered a shifted manhole riser. | approx. 3600 | Volume of VAC Truck debris body. | No | 10049 | null | 2025-10-21 | 03:00 PM | Approx. 3600 gal |  | null | Blockage clearedSSO cleaned by VAC truckMH/ riser repaired | Windsor Locks | 500 North St, Windsor Locks, CT
WODDLAKE TAX DISTRICT | Closed | Sewage Bypass | Dry | 2025-03-21 | 09:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Roots |  | Treatment plant operator Joe Barrios arrived at the plant earlier than scheduled today at approximately 9:30am. He noticed wastewater flowing down the hill from behind the sewage treatment plant. He notified Woodlake Tax District maintenance office, and t | See below | See below | Yes | 9275 | Radey Pond | 2025-03-21 | 10:00 AM | 30000 |  |  | The pipe clogged at the manhole invert at the final manhole before entering the sewage treatment plant occurred. Estimated as a 30,000 Gallon release that started approximately at noon on Thursday 03/20/25. During the clog over the past ~20 hours, a disch | Woodbury | 57 Clubhouse Dr, Woodbury, CT
| Open | Sewage Bypass | Dry | 2025-02-13 | 01:45 PM | Treatment Plant | Partially Treated Raw Sewage | Sewage Line Break, Crack or Failure | This is a UI permit # 0000434 issued to Jandin Reality LLC.The treatment plant averages 12,000 – 15,000 gpd and is located at 7 North Main St in Old Saybrook.The operator noticed a small sink hole next to an underground anoxic tank. The hole is approxim | Operator on site for daily operations and maintenance approximately 1,000 gallons | approximately 1,000 gallons | based on daily flow averages and estimated surcharge amount per system cycle | No | 9096 |  | 2025-02-13 | 03:00 AM | 1,000 gallons |  |  | A temporary fix was installed to bypass the affected broken plumbing | Old Saybrook | 7 N Main St, Old Saybrook, CT

## Bridgeport
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-01-01 | 00:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observation | N/A | N/A | Yes | 8979 | Cedar Creek Long Island Sound | 2025-01-01 | 03:30 AM | 2.99 mg | 2990000 |  | event eneded | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-01-27 | 01:30 PM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | D&D Construction cracked Lakeside Pump Station force main, pump station shut down while repair made, sufficient wet well capacity, can bypass to sanitary gravity manhole Contractor conducting repair | Contractor notified WPCA | Estimated 500 gals | estimated prior to station shutdown | No | 9057 | Lake Forest Creek | 2025-01-27 | 05:15 PM | 500 gal estimated | 500 |  | force main repaired by contractor, used 2 vactor trucks to keep excavation empty when PS on line during repair | Bridgeport | 395 Lakeside Dr, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-02-13 | 02:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | homeowner | unknown | NA | No | 9093 |  | 2025-02-13 | 02:45 PM | 100 gallons | 100 |  | Mainline cleaned with high pressure jetting | Bridgeport | 175 High Ridge Dr, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-02-16 | 02:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | rain with snowmelt and high tide | permitted flow meter | pending | certified flow meter | Yes | 9108 | Bridgeport Harbor | 2025-02-16 | 05:30 PM | 1.71 MG | 1710000 |  | event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-02-16 | 01:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observation | N/A | N/A | Yes | 9107 | Cedar creek Long Island sound | 2025-02-16 | 10:45 PM | 11.2 mg | 11200000 |  | event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-02-18 | 09:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | some rocks and rags | visual on site | 6000 gals | visual | Yes | 9120 | Rooster River | 2025-02-18 | 12:00 PM | 6000 gals | 6000 |  | cleared main line with high pressure jetter | Bridgeport | 149 Rooster River Blvd, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 11:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Plant flow meter | 1.21 MG | plant flow meter | Yes | 9172 | Bridgeport Harbor | 2025-03-06 | 01:45 AM | 1.21MG 1.45" rain | 1210000 |  | weather event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 09:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | plant flow meter | 5.18MG | plant flow meter | Yes | 9169 | Bridgeport Harbor | 2025-03-06 | 04:00 AM | 5.18 MG - 1.43" rain | 5180000 |  | weather event ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-03-11 | 11:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Homeowner notified | unknown | NA | No | 9219 |  | 2025-03-11 | 12:45 PM | 100 gallons | 100 |  | Main line was cleared by high pressure jetting | Bridgeport | 383 Arctic St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-17 | 03:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Visual observation | N/A | N/A | Yes | 9235 | Cedar Creek Long Island Sound | 2025-03-17 | 09:30 AM | 5.05 MG | 5050000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-03-17 | 04:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other |  | Notified by resident | 30 gallons | visual observation | No | 9251 |  | 2025-03-17 | 05:15 PM | 30 | 30 |  | High pressure jetting cleared line | Bridgeport | Iranistan Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-04-25 | 08:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Rags, Roots | Called in by Bridgeport Public Works | Unknown | N/A | Yes | 9403 | 7103 Yellow Mill Channel | 2025-04-25 | 09:45 AM | 100 gallons | 100 |  | Line was jetted and cleaned out | Bridgeport | 1680 Reservoir Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-04-25 | 10:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Other | Rags, Wipes and Grease | Homeowner report | Unknown | N/A | No | 9404 |  | 2025-04-25 | 10:45 AM | 100 gallons | 100 |  | Main Line was Jetted | Bridgeport | 426 Savoy St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-04-28 | 09:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Called in by a resident | 500 | Visual | Yes | 9414 | Ash Creek | 2025-04-28 | 11:00 PM | 500 | 500 |  | Line was cleared | Bridgeport | 280 Scofield Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-05 | 10:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | operations | N/A | N/A | Yes | 9455 | Long Island Sound Cedar Creek | 2025-05-06 | 00:45 AM | 2.5 mg | 2500000 |  | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 09:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Call from resident | unknown | n/a | No | 9474 |  | 2025-05-06 | 09:15 AM | 100 gallons | 100 |  | Line jetted | Bridgeport | 369 Hawley Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-09 | 01:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual Observation | N/A | N/A | Yes | 9498 | Cedar Creek Long Island Sound | 2025-05-09 | 16:15 | 4.06 million gallons | 4060000 | null | null | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-05-15 | 12:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | na | called in by resident | 20gal | visual | Yes | 9558 | Pequannock River | 2025-05-15 | 01:45 PM | 20 gal es | 20 | null | high pressure jetting main line | Bridgeport | 129 Huntington Rd, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-05-16 | 07:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | NA | Resident call | Unknown | NA | No | 9560 |  | 2025-05-16 | 08:30 PM | 100 gallons | 100 | null | high pressure jetting main line | Bridgeport | 97 Alfred St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-05-20 | 01:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Rags, Wipes | Homeowner Called it in | Unknown | N/A | Yes | 9565 | Bruce Brook | 2025-05-20 | 02:30 PM | 100 gallons | 100 | null | Line was cleared | Bridgeport | 49 Sage Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-05-30 | 04:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | plumber on site earlier potential source of problem | called in by resident | Unknown | NA | No | 9601 |  | 2025-05-30 | 04:30 PM | 100 gallons | 100 | null | Mainline cleared with high velocity jetting | Bridgeport | 330 French St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-06-13 | 09:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Bridgeport PD | 750 | Visual | Yes | 9655 | Bruce Brook | 2025-06-14 | 10:45 AM | 750 | 750 | null | line jetted and cleared | Bridgeport | Boston Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-06-18 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Called in by resident | approx. 10,000 gallons | visual estimate | Yes | 9665 | Pequonneck River | 2025-06-18 | 03:00 PM | approx. 10,000 gallons | 10000 | null | Line jetted and cleared | Bridgeport | 20 Crescent Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-07-14 | 07:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Reported by resident | unknown | n/a | No | 9715 |  | 2025-07-14 | 09:00 PM | 100 gallons | 100 | null | Main line cleared | Bridgeport | 774 Capitol Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-08-06 | 08:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Reported By Homeowner | N/A | N/A | No | 9782 |  | 2025-08-06 | 09:45 AM | 100 gallons | 100 | null | Line was cleaned | Bridgeport | 132 Burnsford Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-08-21 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | reported by operators | 30 MGD | flow meter | No | 9826 |  | 2025-08-21 | 04:00 AM | estimated 3 MG | 3000000 | null | storm ended | Bridgeport | Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-08-21 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual Observation | N/A | N/A | Yes | 9929 | Cedar Creek Long Island Sound | 2025-08-21 | 04:00 AM | 3.47 MG | 3470000 | null | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-05 | 11:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Call in report from Fire Department | less than 500 gallons | visual | No | 9868 |  | 2025-09-05 | 11:45 PM' | less than 500 gallons | 450 | null | line jetted and cleared | Bridgeport | 476 Woodlawn Ave Ext, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain 2-3" per hour | 2025-09-06 | 04:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Operators on site | total flow 27 MGD | flow meter | Yes | 9870 | Bridgeport Harbor | 2025-09-06 | 11:00 PM | 2.51 MG | 2510000 | null | Storm event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-09-06 | 05:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual observation | N/A | N/A | Yes | 9871 | Cedar creek Long Island sound | 2025-09-06 | 11:00 PM | 2.21 MG | 2210000 | null | Rain Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-08 | 09:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Resident called and reported back up. | n/a | n/a | No | 9892 |  | 2025-09-08 | 09:30 AM | 50 gallons | 50 | null | line jetted and cleared | Bridgeport | 426 Savoy St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-14 | 08:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Reported by homeowner | Unknown | Unknown | No | 9920 |  | 2025-09-14 | 10:00 PM | 100 gallons | 100 | null | Line jetted and cleared | Bridgeport | 133 Clark St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-17 | 02:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Reported by resident | 100 gallons | visual observation | Yes | 9926 | Bruce Brook | 2025-09-17 | 02:30 PM | 100 gallons | 100 | null | Line jetted and cleared | Bridgeport | 1905 Barnum Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-09-18 | 11:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Resident reported. | unknown | N/A | No | 9927 |  | 2025-09-18 | 12:30 PM | 100 gallons | 100 | null | Line jetted and cleared | Bridgeport | 410 Dexter Dr, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Dry | 2025-10-03 | 09:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Called in by homeowner | N/A | N/A | No | 9966 |  | 2025-10-03 | 10:15 AM | 100 gallons | 100 | null | Line was cleared of Grease | Bridgeport | 307 Texas Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-10-16 | 02:15 PM | Basement | Raw Sewage | Unknown | null | Reported by resident | unknown | na | No | 10020 |  | 2025-10-16 | 02:30 PM | 100 gallons | 100 | null | Line jetted in street, no obstruction encountered. Unknown if main line was cause of back up. | Bridgeport | 213 Harral Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-30 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual Observation | N/A | N/A | Yes | 10066 | Bridgeport Harbor Long Island Sound | 2025-10-31 | 04:30 AM | 5.78mg | 5780000 | null | Event ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-30 | 05:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual observation | N/A | N/A | Yes | 10065 | Cedar Creek Long Island sound | 2025-10-31 | 3:00 | 13.0MGD | 13000000 | null | null | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-11-09 | 01:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Call from resident | 500 | visual | Yes | 10116 | Island Brook | 2025-11-09 | 02:00 PM | 500 gallons | 500 | null | Line was jetted and cleared | Bridgeport | 455 Trumbull Ave, Bridgeport, CT
BRIDGEPORT EASTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-12-02 | 04:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual observation | N/A | N/A | Yes | 10166 | 4 | 2025-12-02 | 06:00 PM | 1.5 MG | 1500000 | null | Storm Event Ended | Bridgeport | 695 Seaview Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-12-02 | 04:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Visual observation | N/A | N/A | Yes | 10165 | Cedar Creek Long Island sound | 2025-12-02 | 07:00 PM | 2.77 MG | 2770000 | null | Event Ended | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-12-12 | 10:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Called in by tenant | Unknown | N/A | No | 10179 |  | 2025-12-12 | 11:30 AM | 100 gallons | 100 | null | Line was jetted | Bridgeport | 509 E Main St, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-12-25 | 01:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Called in by Fire Department | N/A | N/A | No | 10218 |  | 2025-12-25 | 02:00 PM | 100 gallons | 100 | null | Cleared Line | Bridgeport | 170 Alba Ave, Bridgeport, CT
BRIDGEPORT WESTSIDE | Closed | Sewage Bypass | Dry | 2025-12-26 | 05:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Called in by Police | 20 Gal | Visual | No | 10220 |  | 2025-12-26 | 07:00 PM | 20 gallons | 20 | null | Line was cleared | Bridgeport | 205 Bostwick Ave, Bridgeport, CT
[18 empty] | TOTAL VOLUME | 68160520

## Bristol
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-30 | 02:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | Buildup of mostly rags and grease in main sewer line | 1) Department received a possible stoppage call from Ryan Mallet from GW property management on 10/30 and 11/1. | According to Ryan there is roughly 2 feet of sewage in the basement of 189 Divinity street. Ryan stated at least two thousand gallons. | Based on what the property management company relayed to staff. | No | 10064 |  | 2025-10-30 | 03:30 PM | estimated final quantity is between 4,000 and 8,000 gallons. | 6500 | null | On both occasions the jet cleaned to removed blockage. On 11/1 line was also video inspected to confirm no debris, roots or sections of compromised pipe. | Bristol | 190 Divinity St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2025-09-02 | 08:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Roots | Blockage was a combination of grease, rags and grease. | Sewer department received possible stoppage call from homeowner at 24 Roberge Road. | 5 gallons. | Based on conversation with the homeowner (Sharon) | No | 9851 |  | 2025-09-02 | 09:45 AM | 5 gallons | 5 | null | Staff jet cleaned the line. | Bristol | 24 Roberge Rd, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2025-04-28 | 04:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags | Buildup of rags and grease in the main sewer line. | Received a call form resident at 242 High Street | less than 50 gallons | Based on description from resident. | No | 9416 |  | 2025-04-28 | 04:30 PM | 50 gallons or less | 50 |  | Staff jet cleaned the line. | Bristol | 214 High St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Snowmelt | 2025-03-01 | 07:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | Rags and some grease. | Resident called in. | 500-1,000 gallons estimated on roadway. | Estimate. | No | 9150 |  | 2025-03-01 | 09:00 PM | 500-1,000 gallons | 900 |  | Jetted main line to clear stoppage | Bristol | 328 South St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2025-02-10 | 12:00 PM | Sewer Main | Raw Sewage | Other | Discharge from an unidentified 6" line not mapped. Discharge is clean and clear without odor. | The City is performing bridge rehabilitation at this location. During preliminary field work a line was discovered penetrating through the bridge abutment discharging water into the Pequabuck River | 15-20 gpm | Through CCTV footage. | Yes | 9086 | Pequabuck River | 2025-02-13 | 08:00 AM | 60,000-80,000gallons of clear/clean water | 70000 |  | Installing line plug. | Bristol | 9 East St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2025-01-06 | 10:00 AM | Lateral - Private | Raw Sewage | Other | compromised private lateral. | Homeowner notified the City of Bristol with a culvert issue. City investigated culvert and was notified during inspection of a sewage back up in house 211 Park Street. A contractor was hired by property owner to clear the blockage. City requested camera f | 280 gpd | Water usage records. | Yes | 9035 | Pequabuck River | 2025-01-31 | 01:15 PM | 7000 gallons | 7000 |  | Contractor repaired. | Bristol | 211 Park St, Bristol, CT
BRISTOL WATER RECLAMATION FAC. | Closed | Sewage Bypass | Dry | 2025-12-18 | 01:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Possible Rags also. Hard to tell. | Contractor called possible stoppage in. Issue flushing toilet. | At arrival, roughly 50 gallons. | Estimated. | No | 10183 |  | 2025-12-18 | 04:15 PM | 50 Gallons. | 50 | null | Jetted the line upstream and downstream. That line is a cross lot between streets and takes very few homes. | Bristol | 189 Oakridge Rd, Bristol, CT
[18 empty] | TOTAL VOLUME | 84505

## Brookfield
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
BROOKFIELD | Closed | Sewage Bypass | Dry | 2025-11-18 | 04:00 AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Bad connection made by contractor. | Daily pump station check. | 20,000 gallons | Flow numbers/SCADA system. | No | 10130 | null | 2025-11-18 | 07:45AM | 10,500 gallions | SCADA system monitoring. | Proper fitting installed with right size gasket per contractor who made error installing. | Brookfield | 120 Junction Rd, Brookfield, CT
BROOKFIELD | Closed | Sewage Bypass | Dry | 2025-04-05 | 04:00 AM | Sewer Main | Raw Sewage | Unknown | Possible sewer force main break. Investigation underway.* Force Main break | Brookfield Police call to BWPCA. | 40,000 gallons. | Peak flow vs low flow. Pump starts and stops/runtimes via scada system.Visual of discharge. | No | 9337 |  | 2025-04-05 | 11:30 AM | 40,000 Gallons |  | Pumps turned off at Pump Station upon acknowledgement of bypass.Pump trucks on site to handle in coming flow at pump station.Contractor exposed broken force main and repaired.2 catch basins IAO bypass pumped and cleaned.Site affected cleaned/restored. | Brookfield | 64 Federal Rd, Brookfield, CT

## Canton
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
CANTON | Closed | Sewage Bypass | Dry | 2025-11-16 | 08:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Seemed to find grease upon clearing of stoppage | Operator received notification from Canton dispatch that a manhole appeared it was overflowing. | <1000 | Visual estimate of 5 gpm for 2 or so hours. | No | 10128 | null | 2025-11-16 | 09:30 PM | <1000 | 950 | null | Sewer jetter cleared stoppage | Canton | 47-49 Sunset Terrace, Canton, CT
[18 empty] | TOTAL VOLUME | 950

## Cheshire
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
CHESHIRE | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-12 | 05:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Excessive grease blocking our drop manhole | police | 10GPM | visual | Yes | 9366 | Quinnipiac River | 2025-04-12 | 09:45 PM | 2000 gallons | 2000 | null | jetted blocked line. | Cheshire | 1728 Highland Ave, Cheshire, CT
[18 empty] | TOTAL VOLUME | 2000

## Danbury
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2025-06-20 | 12:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | buildup of rags | homeowner at 19 Allen discovered | 100 gallons | based off of flow coming out of drain pipe for ~ 1 hr | Yes | 9672 | Lake Wackawana | 2025-06-20 | 01:00 PM | 100 gallons | 100 | null | Public utilities jetted the line and cleared the blockage | Danbury | 21 Alan Ave, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2025-05-27 | 02:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | null | Reported to Public Utilities by a City worker | 500 Gallons | Estimated based on duration of bypass | No | 9595 | null | 2025-05-27 | 03:00 PM | 500 Gallons | 500 | null | The sewer line was jetted to clear the obstruction and normal sewer flow resumed at 3PM on 5/27/25 | Danbury | 1 Patriot Dr, Danbury, CT
DANBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-25 | 04:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Grease and Rags | Condo tenant woke up and found floor covered in sewage | 1,000 gallons | Estimated based on square footage of area containing the sewage | No | 9298 | null | 2025-03-25 | 11:00 AM | 1,000 gallons | 1000 | null | Jetted sewer main and cleared blockage. Treated with Potassium Permanganate | Danbury | 7 Padanaram Rd, Danbury, CT
[18 empty] | TOTAL VOLUME | 1600

## Darien
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
DARIEN | Closed | Sewage Bypass | Snowmelt | 2025-02-27 | 10:45 AM | Lateral - Private | Raw Sewage | Sewage Line Broken by Contractor or other utility | Construction activity on site, low pressure sewer lateral valve box impacted by equipment (dumpster), box was marked in earth area with flags in earth area and paint on road surfaces. | Contractor call it in, 1 Swifts Lane, Darien, CT | 1 gallon per minute for 10 minutes and 0 gallons per minute for 10 minutes estimated. Flow is intermittent and related to pump activation within the system. | Visual observation of flow from area of break into containment excavation. | No | 9146 |  | 2025-02-27 | 12:45 PM | 60 gallons - zero gallons reached waterbody. | 60 |  | broken pipe repaired and new valve assembly installed. | Darien | 1 Swifts Ln, Darien, CT
DARIEN | Closed | Sewage Bypass | Dry | 2025-02-04 | 01:30 PM | Manhole | Raw Sewage | Unknown | looking for clogged pipe. will confirm.This was the result of a clog in sewer pipe. | DPW crew member observed and called sewer dept. | to be determined upon correction60 to 100 gallons total | 3 gpm | Yes | 9072 | Goodwives River via CB. CB cleaned out. | 2025-02-04 | 02:00 PM | Actually ended at 1:50 PM. 3 to 5 gallons per minute for 20 minutes. 60 to 100 gallons total volume estimated. | 90 |  | jet rodder and vactor truck utilized to clear pipe. | Darien | 36 Old Kings Hwy S, Darien, CT
[18 empty] | TOTAL VOLUME | 150

## Derby
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
DERBY | Closed | Sewage Bypass | Dry | 2025-09-08 | 04:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Electrical Equipment Failure | Line power outage. One if the insulators of the three phase line power feeding the treatment plant failed. Due to this event we still had two phase power feeding the plant which caused the secondary control building generator to run intermittently while t | Upon initial walk around the plant at 4:45am I noticed the secondary building generator running. | We are estimating 0.583MG were discharged | The on call operator was called in Sunday 9/7/25 at 3pm for a fire alarm trouble call. As he checked the plant no generators were running and all equipment was operational. Because the auto dialer did not call out, we are going to use the time the on call | Yes | 9895 | Housatonic River | 2025-09-08 | 05:45 AM | 0.583MG | 583000 | null | Plant mechanics manually started main plant generator 9/8/25 by 5:45am. United Illuminating changed all the insulators and we were back on line power by 8:00am 9/8/25 | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Dry | 2025-06-09 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Unknown | We are currently investigating the cause of why the blower had shut off. We are also investigating why no plant alarms went off calling in our stand-by crew. | Upon visual walk around the plant. | Quantity undetermined at this time. Best guess 100,000 - 500,000 gallons. | Plant mechanic was called out to the plant on Saturday 6/7/25 at 4:07pm for a high wet well level alarm. Upon leaving the plant at approximately 7:00pm the plant blower was still in operation. Once the blower was back in operation the color and foam in th | Yes | 9635 | Housatonic River | 2025-06-09 | 05:30 AM | Approximately 2.25MG | 2250000 | null | At approximately 5:30am the main plant blower was back in operation. | Derby | 1 Caroline St, Derby, CT
DERBY | Closed | Sewage Bypass | Dry | 2025-04-21 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Backpressure from using the Jet truck to clear a clogged sewer main. | Call from homeowner. | 30 gallons total | Visual estimation | No | 9397 | null | 2025-04-21 | 10:15 AM | 30 Gallons | 30 | null | The sewer main was unclogged, relieving the back pressure in this manhole, and allowing the sewage to flow again. | Derby | 210 Emmett Ave, Derby, CT
[18 empty] | TOTAL VOLUME | 2833030

## East Hampton
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
EAST HAMPTON WPCA | Closed | Sewage Bypass | Dry | 2025-03-26 | 08:00 AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Assumed break in 4" ductile iron pipe. | During a routine pump station inspection. | The leak appears to be about 15 gallons per minute and pump station runtime data suggests that it may have been leaking for approximately 650 minutes. I would estimate the discharge at approximately 9,750 gallons. | The estimated rate was determined by visually inspecting the leak while the pump was running, reviewing pump station runtimes, and confirming that water was pumped to the next pump station and it was not all coming out of the break. | No | 9295 | null | 2025-03-26 | 08:00 AM | 9,750 | 9750 | null | The pump was shut off and the pipe was isolated by closing valves and installing blind flanges in the piping. There is a second pump at the pump station that is still up and running with no issues. | East Hampton | 30 Pine Trail, East Hampton, CT
EAST HAMPTON WPCA | Closed | Sewage Bypass | Dry | 2025-12-15 | 10:00 AM | Manhole | Raw Sewage | Unknown | The cause is currently being investigated. | The incident was discovered when Operators were doing pump station inspections. | 1,000 gallons total at 3 gpm. | The rate was determined based on the amount of services upstream and what was visually estimated onsite. | Yes | 10180 | Muddy Gutter Brook | 2025-12-15 | 12:30 PM | ~1,200 gallons | 1200 | Visual inspection of the flow coming into the manhole, and using a bucket and stop watch to calculate the average flow from this gravity sewer at its entry point to the Spice Hill pump station. | Our Operators used the Vac Truck to remove the water from the manhole and gravity sewer. They then used a jet truck to clear the blockage in the gravity line restoring flow. | East Hampton | 19 Sherry Dr, East Hampton, CT
[18 empty] | TOTAL VOLUME | 10950

## East Windsor
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
EAST WINDSOR WPCF | Closed | Sewage Bypass | Other | 2025-04-04 | 08:00 AM | Sewer Main | Raw Sewage | Other | Wash out of main truck line due to storm water drainage | Loss of flow at plant. Went to visually check the sewer line and found broken gravity main | 300,000 to 400,000 gallons per day | flow meter at plant | Yes | 9336 | Connecticut River | 2025-04-04 | 11:45 PM' | around 300,000 to 400,000 gallons | 380000 |  | Currently bypass pumping is in place to work around the broken pipe. Permeant repairs plans are being worked on. | East Windsor | 249 S Water St, East Windsor, CT
[18 empty] | TOTAL VOLUME | 380000

## Enfield
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
ENFIELD POTW | Closed | Sewage Bypass | Dry | 2025-06-05 | 12:15 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | The hole was located under the pipe possibly sitting on a rock that wore through overtime or perhaps it had a hair line fracture during installation that finally wore through | Routine lift station inspection | We calculated 33,000 gallons had reached the Scantic River | Pump run times from SCADA | Yes | 9626 | Scantic River | 2025-06-05 | 03:00 PM | 33,000 gallons | 33000 | null | Repaired pipe on 6/9/25, tested on 6/10/25 and put back online 6/10/25 | Enfield | 73 Simon Rd, Enfield, CT
[18 empty] | TOTAL VOLUME | 33000

## Fairfield
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
FAIRFIELD WPCF | Closed | Sewage Bypass | Dry | 2025-04-22 | 09:45 AM | Pump Station | Raw Sewage | Sewage Line Broken by Contractor or other utility | Town's contracted Engineer's drilling subcontractor drilled into the force Main. | Contractor called . | 750 gallons per pump cycle. | Best guest per pump gpm discharge | Yes | 9400 | Long Island Sound | 2025-04-22 | 02:30 PM | @1500 gallons | 1500 |  | Contractor excavated the road and repaired pipe with an Adams clamp. | Fairfield | 1610 Fairfield Beach Rd, Fairfield, CT
FAIRFIELD WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-01-01 | 04:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Called in by resident | 150 Gallons | Visual estimate | Yes | 8999 | Pine Creek Marsh | 2025-01-01 | 04:45 PM | 150 Gallons | 150 |  | Jet line to break blockage | Fairfield | 11 Rugby Rd, Fairfield, CT
[18 empty] | TOTAL VOLUME | 1650

## Farmington
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
FARMINGTON | Closed | Sewage Bypass | Dry | 2025-07-28 | 01:30 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Crack in Ductile Iron pipe, material found in trench not suitable for compaction. | Sewage coming out from crack in roadway | Under 200 gpm | 5 gallon buckets over the course of a minute | No | 9760 | null | 2025-07-28 | 11:45 PM' | Under 5,000 | 4500 | null | 5 foot Force main section of line was replaced | Farmington | 38 Patrick H Flood Rd, Farmington, CT
[18 empty] | TOTAL VOLUME | 4500

## Glastonbury
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GLASTONBURY | Closed | Sewage Bypass | Dry | 2025-11-07 | 12:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease | Possible grease trap issue. | Town Fire Marshall, then reported to Town Engineer staff. | Under 25 gallons | WPCF staff estimated. | No | 10113 |  | 2025-11-07 | 02:30 PM | Under 25 gallons | 25 | Estimated | Clean up by Wind River. | Glastonbury | 70-124 Hebron Ave, Glastonbury, CT
GLASTONBURY | Closed | Sewage Bypass | Dry | 2025-09-21 | 06:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Roots | Combination of rags, paper and roots | Citizen | under 500 gallons | Estimated | No | 9931 |  | 2025-09-21 | 10:00 AM | Under 500 gallons | 500 | Estimated by onsite personnel | jetted line with root cutter. | Glastonbury | 76 Mill St, Glastonbury, CT
[18 empty] | TOTAL VOLUME | 525

## GNHWPCA
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GNHWPCA | Closed | Sewage Bypass | Other | 2025-01-06 | 11:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease and rags were removed from the system. | Resident called it in. | Less than 100 gallons were discharged into the basement. | Field estimate by crew. | No | 9018 | N/A | 2025-01-06 | 11:45 AM' | Less than 100 gallons. | 90 |  | Crew flushed the sanitary sewer and restored flow. The GNHWPCA contracted Pro Klean to clean and sanitize the basement. | East Haven | 690 Thompson St, East Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-06-23 | 9:45 | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease in line on Dewey Ave caused the issue. | Property owner called it in. | Crew estimated 20 gallons were discharged into the basement. | Field estimate by crew. When the crew inspected the basement only the floor was damp, no ponding or standing water. | No | 9670 | N/A | 2025-06-23 | 10:45 | Less than 20 gallons was estimated by the crew. | 18 | null | Crew jetted the line and restored flow. Cleaning services were offered to the owner. The crew CCTV and grease cut the line. | East Haven | 144 Coe Ave, East Haven, CT
[18 empty] | TOTAL VOLUME | 108
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-02-25 | 14:00 | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Called in by property owner | Approx 300 gallons | Field estimate by road crew | No | 9140 |  | 2025-02-25 | 14:30 | 375 gallons | 375 |  | sewer main was jetted and flow was restored | Hamden | 80 Skiff St, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-07-28 | 11:30 | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease was blocking the sewer main. | Resident called it in. | Less than 10 Gallons | Field estimate by crew. | No | 9759 | N/A | 2025-07-28 | 12:00 | Less than 10 gallons. | 9 | null | Crew jetted the line and restored flow. The area around the manhole was washed down with the Vac truck. | Hamden | Pine Rock Ave, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-09-11 | 11:30 | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | A break in the sanitary sewer was causing the flow to drop out of the sanitary system and make its way to the storm system. | Odor complaint from the Whitney Museum at the back of the museum parking lot. GNHWPCA staff found flow at the storm discharge to the Mill River. | 300 gal based on 5 gallons / minute for 1 hour. | Field estimate by crew. | Yes | 9915 | Mill River | 2025-09-11 | 11:45 AM' | 300 Gallons | 300 | null | A vac truck was set up to hold flow, contractor coming out to repair line. | Hamden | 65 Armory St, Hamden, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-11-08 | 3:00 | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease and rags caused the backup. Crew jetted the line and restored flow. | Called in by homeowner. | Less than 50 gallons were discharged into the basement. | Field estimate by crew. | No | 10115 | N/A | 2025-11-08 | 3:30 | Less than 50 gallons | 45 | null | Crew jetted the line and restored flow. Pro Klein was contracted to clean and sanitize. | Hamden | 361 Belden Rd, Hamden, CT
[18 empty] | TOTAL VOLUME | 729
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-01-01 | 00:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | 8985 | NEW HAVEN HARBOR | 2025-01-01 | 02:45 AM | 2.7239 MG Diverted | 2723900 |  | Rain Event Ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Other | 2025-01-19 | 04:30 PM | Manhole | Raw Sewage | Unknown | Unknown cause, manhole had debris in it. | Property owner or manager called it in. | Less than 75 gallons. | Field estimate by crew. | No | 9043 | N/A | 2025-01-19 | 05:15 PM | Less than 75 gallons were discharged from the sanitary sewer. | 70 |  | Crew jetted the sanitary sewer and restored flow. The area was washed down and all visible debris was picked up. The parking lot drains run to the sanitary sewer. | New Haven | 130 Winchester Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-02-06 | 03:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease |  | Called in by property owner | less than 50 gallons | Feild estimate by crew | No | 9077 |  | 2025-02-06 | 03:30 PM | less than 50 gallons | 45 |  | Sewer main was jetted and flow restored | New Haven | 180 Main Street Anx, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-02-11 | 08:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | There was grease blocking the gravity line near the pump station. | Called in by contractor. | 75-80 gallons were spilled to the road surface. The area was washed down after the line was cleared. | Field estimate by crew. | No | 9091 | N/A | 2025-02-11 | 09:00 PM | 75-80 gallons | 79 |  | Crew jetted the line and restored flow. The area around the spill was washed back into the MH. | New Haven | 1024 Quinnipiac Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-02-12 | 10:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage on Middletown Ave in front of the 91 Diner. | Homeowners called it in. | 560 Middletown Ave had approximately 100 gallons at the time of inspection.641-643 Middletown Ave had approximately 1600 gallons at the time of inspection. This sewage was throughout the basement.The combined total gallons is approximately 1700 | Square footage times inches of water times1 7.48. | No | 9092 | N/A | 2025-02-12 | 11:15 PM | 1700 gallons were discharged into the basements. | 1700 |  | Crew jetted the line and restored flow. Pro Klein was contracted to clean and sanitize both basements. | New Haven | 560 Middletown Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-02-16 | 08:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | 9101 | NEW HAVEN HARBOR | 2025-02-16 | 10:00 PM | 8.8483 MG Diverted | 8848300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-02-25 | 01:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | After further investigation it was determined that the property owners' lateral was broken causing the basement back up, Surcharge in the street was coincidental and not the cause of the discharge in basement. | Called in by property owner | Less than 50 Gallons | Feild estimate by road crew | No | 9139 |  | 2025-02-25 | 01:45 PM | Less Than 50 Gallons | 45 |  | sewer main was jetted and flow was restored | New Haven | 25-27 Lander St, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 07:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | N/A | SCADA Flow monitoring | Yes | 9163 | NEW HAVEN HARBOR | 2025-03-06 | 00:00 AM | 5.5941 MG | 5594100 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-06 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | N/A | Undetermined | Yes | 9177 | NEW HAVEN HARBOR | 2025-03-06 | 03:00 AM | 3.6002 MG | 3600200 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-17 | 01:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | rain event | SCADA | n/a | undetermined | Yes | 9233 | NEW HAVEN HARBOR | 2025-03-17 | 08:30 AM | 4.7370 MG | 4737000 |  | rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-21 | 02:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | Undetermined | Undetermined | Yes | 9272 | NEW HAVEN HARBOR | 2025-03-21 | 03:30 AM | 0.8089 MG | 808900 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-24 | 03:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9284 | NEW HAVEN HARBOR | 2025-03-24 | 06:00 PM | 1.6080 MG | 1608000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-31 | 09:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9312 | NEW HAVEN HARBOR | 2025-04-01 | 00:00 AM | 0.0244 MG | 24400 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-04-01 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | 9322 | NEW HAVEN HARBOR | 2025-04-01 | 01:00 AM | 0.4395 MG | 439500 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-04-01 | 07:00 PM | Basement | Raw Sewage | Sewage Line Break, Crack or Failure | Crew found rocks and fresh dirt coming back during the jetting process. Bypass pumps are being set up. Repairs are being scheduled. | Homeowner had a backup in the basement. | 75 gallons were discharged into the basement. | Field estimate by crew. | No | 9327 | N/A | 2025-04-01 | 08:00 PM | 75 gallons were discharged into the basement. | 75 |  | Crew pumped the line down, a bypass pump will be set up. | New Haven | 126 Cedar Hill Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-04-06 | 03:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9347 | NEW HAVEN HARBOR | 2025-04-06 | 03:30 AM | 0.9887 MG Diverted | 988700 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-15 | 05:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | 0.6136 mgd | SCADA | Yes | 9384 | NEW HAVEN HARBOR | 2025-04-15 | 06:00 AM | 0.6136 mgd | 613600 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-26 | 06:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9411 | NEW HAVEN HARBOR | 2025-04-26 | 10:15 PM | 5.3301 MG | 4330100 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-04 | 08:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9439 | NEW HAVEN HARBOR | 2025-05-05 | 00:00 AM | 0.4181 MG | 418100 |  | Flow event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-05 | 06:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | Crew found the sewer full of grass clippings. The line was partially blocked. During heavy rain the sewer backed up. This sewer is combined. | Homeowner called it in. | Less than 20 gallons.field estimate by crew. | There was a small puddle of water at the cleanout in the basement. | No | 9454 | N/A | 2025-05-05 | 07:30 PM | Less than 20 gallons | 19 |  | Crew jetted the sewer and cleared the grass clipping. Flow was restored. | New Haven | 1 W Park Ave, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-05 | 02:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | . | SCADA | ONGOING | ONGOING | Yes | 9453 | NEW HAVEN HARBOR | 2025-05-05 | 10:00 PM | 7.3000 MG | 7300000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 00:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9460 | NEW HAVEN HARBOR | 2025-05-06 | 09:00 AM | 12.400 MG | 12400 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-09 | 10:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | .Rain event 0.7" | SCADA | 6.3 mgd | SCADA | Yes | 9494 | NEW HAVEN HARBOR | 2025-05-09 | 10:00 PM | 6.3 mgd | 6300000 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-14 | 09:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | UNDETERMINED | Yes | 9533 | NEW HAVEN HARBOR | 2025-05-15 | 00:00 AM | 0.9623 MG | 962300 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-15 | 02:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | SCADA | ONGOING | ONGOING | Yes | 9539 | NEW HAVEN HARBOR | 2025-05-15 | 03:45 AM | 0.8318 MG Diverted | 831800 |  | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-22 | 07:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9574 | NEW HAVEN HARBOR | 2025-05-22 | 12:30 PM | 2.2535 MG | 2253500 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-31 | 03:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9607 | NEW HAVEN HARBOR | 2025-05-31 | 06:00 AM | 2.9778 MG | 2977800 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 2-3" per hour | 2025-06-10 | 10:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | Ongoing | Ongoing | Yes | 9649 | New Haven Harbor | 2025-06-10 | 01:30 PM | 1.1724 MG | 1172400 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-07-14 | 09:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9720 | New Haven Harbor | 2025-07-14 | 11:00 PM | 1.3563 MG | 1356300 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-07-20 | 09:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9739 | NEW HAVEN HARBOR | 2025-07-20 | 10:45 PM | 0.5037 MG | 503700 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-07-27 | 07:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | 0.9406 MGD | SCADA | Yes | 9754 | NEW HAVEN HARBOR | 2025-07-27 | 08:45 AM | 0.9406 MGD | 940600 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-07-31 | 11:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | 0.9389 MGD | SCADA | Yes | 9768 | New Haven Harbor | 2025-07-31 | 11:45 PM' | 0.9389 MGD | 938900 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-08-01 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | 0.4886 MGD | SCADA | Yes | 9777 | NEW HAVEN HARBOR | 2025-08-01 | 00:45 AM | 0.1886 MGD | 188600 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-08-20 | 11:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9820 | NEW HAVEN HARBOR | 2025-08-21 | 00:00 AM | 1.2705 MG | 1270500 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-08-21 | 00:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | Ongoing | Ongoing | Yes | 9825 | New Haven Harbor | 2025-08-21 | 01:30 AM | 1.8515 MG | 1851500 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-09-05 | 03:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9860 | NEW HAVEN HARBOR | 2025-09-05 | 04:00 AM | 0.3413 MG | 341300 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-09-06 | 05:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9876 | NEW HAVEN HARBOR | 2025-09-06 | 07:00 PM | 1.8868 MG | 1886800 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-09-07 | 09:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9890 | NEW HAVEN HARBOR | 2025-09-07 | 11:30 AM | 1.1864 MG | 1186400 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-09-24 | 06:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9945 | NEW HAVEN HARBOR | 2025-09-24 | 07:30 AM | 0.1045 MG | 104500 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-09-26 | 10:30AM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | This is a combined line, and it was full of plastic and debris from storm basins. | Prperty manager called first, then the property owner called. | Less than 100 gallons | Field estimate by crew. | No | 9959 | N/A | 2025-09-26 | 11:15 AM | less than 100 gallons. | 90 | null | Crew jetted the line on Stanley St and restored flow.Pro Klean was contracted to clean and sanitize the building. | New Haven | 68 Norton St, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-08 | 09:00 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 9984 | NEW HAVEN HARBOR | 2025-10-08 | 10:00 AM | 0.3289 MG Diverted | 328900 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-12 | 07:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | Ongoing | Ongoing | Yes | 10002 | New haven Harbor | 2025-10-12 | 11:45 PM' | 2.1106 MG Diverted | 2110600 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-13 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 10007 | NEW HAVEN HARBOR | 2025-10-13 | 03:00 PM | 5.6650 MG | 5665000 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-20 | 05:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 10027 | NEW HAVEN HARBOR | 2025-10-20 | 06:00 AM | 0.2771 MG | 277100 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-22 | 09:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 10050 | New Haven Harbor | 2025-10-22 | 10:00 AM | 0.1453 MG Diverted | 145300 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-30 | 05:30 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 10073 | NEW HAVEN HARBOR | 2025-10-31 | 00:00 AM | 7.2638 MG Diverted | 7263800 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-31 | 00:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 10087 | NEW HAVEN HARBOR | 2025-10-31 | 06:00 AM | 6.0985 MG | 6098500 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-11-25 | 09:45 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 10142 | NEW HAVEN HARBOR | 2025-11-26 | 00:00 AM | 1.1167 MG | 1116700 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-11-26 | 00:45 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 10147 | NEW HAVEN HARBOR | 2025-11-26 | 01:45 AM | 1.2128 MG Diverted | 1212800 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-12-02 | 03:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | Ongoing | Ongoing | Yes | 10160 | New Haven Harbor | 2025-12-02 | 09:00 PM | 3.9449 MG | 3944900 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-12-19 | 09:15 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 10193 | NEW HAVEN HARBOR | 2025-12-19 | 12:30 PM | 3.9663 MG | 3966300 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
GNHWPCA | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-12-29 | 01:15 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | EXCESSIVE FIOWS -STORM EVENT | SCADA | ONGOING | ONGOING | Yes | 10223 | NEW HAVEN HARBOR | 2025-12-29 | 03:00 PM | 1.5452 MG | 1545200 | SCADA | Rain event ended | New Haven | 345 E Shore Pkwy, New Haven, CT
[18 empty] | TOTAL VOLUME | 100791323
GNHWPCA | Closed | Sewage Bypass | Dry | 2025-01-21 | 11:30 | Pump Station | Raw Sewage | Mechanical Equipment Failure | By-pass pumps failed causing construction site to flood. Sewage was contained in the work site. | Contractor called it in. | over 3000 gallons of sewage was discharged into the construction site.Holzner estimated 30,000 gallons of sewage were discharged into the construction site. | One vac truck has been filled removing the sewage. The contractor is still working on the spill. | No | 9045 | N/A | 2025-01-22 | 9:00 | 30,000 gallons were estimated by Holzner. | 30000 |  | Contractor hired McVac to remove the sewage from the site. | Woodbridge | 2 Brookside Dr, Woodbridge, CT
[18 empty] | TOTAL VOLUME | 30000

## Greenwich
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2025-05-01 | 01:15 PM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | Holes found in the base of an existing sewer manhole structure | Routine inspection by Sewer Division for a utility markout | Unknown | N/A | Yes | 9448 | Byram River | 2025-05-01 | 02:00 PM | Unknown | 3000 |  | Holes in sewer manhole patched with hydraulic cement | Greenwich | 21 Byram Rd, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2025-04-14 | 09:00 AM | Lateral - Private | Raw Sewage | Unknown |  | Phone call from neighbor | Unkown | N/A | Yes | 9378 | Unkown | 2025-04-21 | 12:00 PM | Unknown - it was from one home - estimate 300 gpd so total could have been approximately 2,100 gallons | 2100 |  | Property owner had plumber come and snake their lateral on April 21st. | Greenwich | 32 Chapel St, Greenwich, CT
GREENWICH (GRASS ISLAND WPCF) | Closed | Sewage Bypass | Dry | 2025-03-06 | 10:30AM | Treatment Plant | Fully treated raw sewage except disinfection | Sewage Line Break, Crack or Failure | This is treated wastewater prior to UV disinfection that has additional chlorine added to it. It is a 2-inch diameter plant effluent line. A break occurred in a pipe coupling connection. | Visually observed water coming to the surface of the ground | Estimated approximately a total discharge of 2,500 gallons. | Based on visual observations, and comparison to the Sewer Spill Estimation Guide (by Orange County, CA) that the USEPA has previously provided as a reference. | Yes | 9189 | Greenwich Harbor | 2025-03-06 | 11:15 AM | Estimated approximately a total discharge of 2,500 gallons. | 2500 |  | We shut the water off, hand excavated and repaired the pipe. | Greenwich | 250A Shore Rd, Greenwich, CT
[18 empty] | TOTAL VOLUME | 7600

## Groton
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2025-01-26 | 03:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | Gravity line is clogged | Resident called it in | .5 gpm | Visual | No | 9053 |  | 2025-01-26 | 05:30 AM | 60 gallons | 60 |  | Jetted line | Groton | 5 Riverview Ave, Groton, CT
GROTON, CITY OF | Closed | Sewage Bypass | Dry | 2025-01-15 | 04:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | resident called in | 100 gallons | Estimation from volume coming out of manhole about 3 gallons a minute for 30 minutes | No | 9033 |  | 2025-01-15 | 04:45 AM | 100 gallons | 100 |  | Jetted gravity line | Groton | 5 Riverview Ave, Groton, CT
GROTON, TOWN OF | Closed | Sewage Bypass | Dry | 2025-01-14 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | routine inspection | 100 Gallons | estimate | No | 9028 |  | 2025-01-14 | 12:15 PM | 100 gallons | 100 |  | Clear sewer blockage by hydro jet | Groton | 144 Pamela Ave, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2025-10-09 | 05:00 PM | Lateral - Private | Raw Sewage | Mechanical Equipment Failure | Submarine/sewer Pipe connection | Watch stander reported it during operation | 30 gallons on the pier, possibly some into the water via scuppers...nothing visible | Operator estimate based on pump rate and immediate shutdown when notified of condition. | Yes | 9995 | Thames river; nothing seen but probable that some cleared the pier--Fire Department and base Public works personnel reported nothing visible. | 2025-10-09 | 05:00 PM | 30 gallons | 30 | null | Stopped pumping, disconnected hoses for Public works utilitty inspection | Groton | Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2025-08-07 | 07:30 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Broken pipe/damaged equipment. | Visual and dye-test performed. | 5-10 gallons, initial release. Unknown amount through small leak (secured). | Visual, based on rough time of when pipe break was discovered, up until it was secured. | Yes | 9786 | Thames River | 2025-08-08 | 1:00 | 5 | 5 | Visual | Sewage flow stopped/shut off by Utilities personnel. While waiting for parts to repair/replace portions of the piping, the pier's sewage line was shut down and offline completely. Piping fully replaced/repaired and up and running in the first week of September. | Groton | Military Hwy, Groton, CT
US NAVAL SUB BASE (DEPT OF NAVY) | Closed | Sewage Bypass | Dry | 2025-01-22 | 08:15 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Drydock pumping line break. | CHT spill at Pier 15 noticed by crew. CHT pumped from ship leaking to pier. More to follow. | 10 Gallons to water. | Visual from drydock crew who seized operations as soon as they noticed the leak after initially beginning pumping. | Yes | 9047 | Thames River | 2025-01-23 | 08:30 AM | 10 Gallons | 10 |  | Pumping stopped and line repaired. | Groton | 173 Dorado Rd, Groton, CT
[18 empty] | TOTAL VOLUME | 305

## Harwinton
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2025-08-10 | 10:30 PM | Treatment Plant | Raw Sewage | Other | Septic tank overflowed -High Level Alarm not triggered | When staff arrived, 8/11/2025 at 7am | less than 100 gallons | visual -didn't enter catch basin | No | 9789 | null | 2025-08-10 | 11:00:00 PM | 100 gallons | 100 | visual | cleaned | Harwinton | 252 Bogue Rd, Harwinton, CT
[18 empty] | TOTAL VOLUME | 100

## Jewett City
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
JEWETT CITY WPCA | Open | Sewage Bypass | Dry | 2025-09-15 | 12:30 PM | Manhole | Raw Sewage | Electrical Equipment Failure | null | Call from customer | 5 gallons | visual | No | 9922 | null |  |  |  | null | null | Griswold | 302 E Main St, Griswold, CT

## Killingly
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
KILLINGLY | Closed | Sewage Bypass | Dry | 2025-03-13 | 01:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Maintenance worker at the school | 50-75 gallons | 1 inch opening in manhole leaking slowly for 45-60 minutes until we unclogged the pipe. | No | 9224 |  | 2025-03-13 | 02:30 PM | 50 gallons | 50 |  | Blockage in manhole was cleared by sewer jet. | Killingly | 60 Soap St, Killingly, CT
KILLINGLY | Closed | Sewage Bypass | Dry | 2025-01-18 | 02:15 AM | Treatment Plant | Sludge Spill | Mechanical Equipment Failure | Sludge hauler was removing trailer from facility when tailgate opened dumping sludge cake on the roadway | State Police notified us of some water on the road at the intersection of Wauregan St. and Dyer St. at 2:15am. | 100 gallons of soupy sludge on the top of the regular sludge. | By the size of 3 piles of sludge that was picked up. | No | 9037 |  | 2025-01-18 | 02:45 AM | 120 gallons | 120 |  | Kropp Environmental Cleanup 1/18/2025 | Killingly | 39 Wauregan Rd, Killingly, CT
[18 empty] | TOTAL VOLUME | 170

## Lisbon
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
LISBON | Closed | Sewage Bypass | Dry | 2025-01-30 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Customer Call | 1000 Gallons | Visual Estimate | No | 9064 |  | 2025-01-30 | 02:30 PM | 1000 | 1000 |  | Repaired force main | Lisbon | 16 River Rd, Lisbon, CT
[18 empty] | TOTAL VOLUME | 1000

## Manchester
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2025-11-28 | 04:00 PM | Basement | Raw Sewage | Unknown | While jetting the main line, we found nothing indicative of a sewer main blockage. Homeowner said after we jetted the main, the water subsided, but nothing was in the line that indicated there was a sewer back up. | Property owner called answering service | Approximately 300 gallons | Estimated based on description of property owner- Event was over by the time of my arrival. | No | 10155 |  | 2025-11-28 | 04:30 AM | 300 Gallons | 300 | null | Jetted sewer main with combination Jet/Vac truck | Manchester | 53 Niles Dr, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2025-06-24 | 07:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Roots | null | Homeowner called | Approximately 500 gal | Visual estimation | No | 9676 |  | 2025-06-24 | 07:30 AM | 500 Gal | 500 | null | Crew responded with Sewer combination truck and jetted and cleared the line. | Manchester | 156 Kennedy Rd, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-07 | 05:30 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Property owner contacted Manchester Fire Dept- Manchester Fire Dept contacted Water Dept. | 3200 Gal | Sq footage x Depth | No | 9353 |  | 2025-04-07 | 07:00 PM | 3200 gal | 3200 |  | Water Dept. personnel responded to scene with combination sewer truck and cleared the line w/ jet. Line is functioning normally | Manchester | 107 Vernon St, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2025-03-20 | 07:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Rags accumulated in linej | Called in by passerby | Approximately 300 Gallons | Visual estimation | No | 9266 |  | 2025-03-20 | 08:45 PM | Approximately 300 gallons | 300 |  | Collection system operators responded to location with combination sewer jet/vac truck. They jetted the line, cleared the blockage and removed remaining rags from the upstream manhole. | Manchester | 68 Woodbridge St, Manchester, CT
MANCHESTER (Hockanum River WPCF) | Closed | Sewage Bypass | Dry | 2025-01-05 | 05:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Manchester Police Department | 500 Gallons | Visual estimate | Yes | 9014 | Union Pond | 2025-01-05 | 06:15 PM | 500 Gallons | 500 |  | Crew cleared sewer blockage with combination jet/vac truck | Manchester | 107 N School St, Manchester, CT
[18 empty] | TOTAL VOLUME | 4800

## Mattabassett
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 06:00 PM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Operator opened bypass gate | Plant influent was approximately 62MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | 9511 | Connecticut River | 2025-05-10 | 06:15 AM | 1,919,167 gallons of partially treated effluent, combined with 30,936,354 gallons of fully treated effluent during the 12.25 hour event. | 1919167 | null | When flows subsided under 55 MGD, operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 11:45 AM' | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event | null | Operator opened bypass gate. | Plant influent was approximately 60 MGD at time of opening bypass gate. | Using the difference between the calibrated influent and effluent parshall flumes. | Yes | 9476 | Connecticut River | 2025-05-06 | 03:00 PM | 339,999 gallons of partially treated effluent, combined with 9,741,336 gallons of fully treated effluent during the 4.25 hour event. | 33999 | null | When flows subsided under 55 MGD, operator closed the bypass gate. | Cromwell | 245 Main St, Cromwell, CT
MATTABASSETT DISTRICT | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-06 | 05:00 AM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | Operator opened bypass gate | Plant influent was approximately 63 MGD at the time of opening bypass gate | Using the difference between the calibrated influent and effluent parshall flumes | Yes | 9179 | Connecticut River | 2025-03-06 | 09:45 AM | 219,722 gallons of partially treated effluent, combined with 10,667,198 gallons of fully treated effluent during the 4.66 hour event. | 219722 |  | When flows subsided under 55 MGD, operator closed bypass gate. | Cromwell | 245 Main St, Cromwell, CT
[18 empty] | TOTAL VOLUME | 2172888

## MDC
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-05-29 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Broken by Contractor or other utility | EVERSOURCE DRILLED A POLE THROUGH THE SEWER MAIN | HOMEOWNER | >1000 GALLONS | MDC PERSONNEL | No | 9600 | null | 2025-05-30 | 12:30 PM | 17000 GALLONS PUMPED - BYPASS OF M/S ONLY - NO SPILL | 0 | null | SEWER MAIN WAS REPAIRED | Bloomfield | 1067 Blue Hills Ave, Bloomfield, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-07-16 | 07:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Also paper | Homeowner | <100 | Visual observation by MDC personnel | No | 9722 | null | 2025-07-16 | 10:00 AM | <100 Gallons | 100 | null | Main sewer flushed by jet truck and stoppage relieved | East Hartford | 26 Rector St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-04-07 | 10:30AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | MDC personnel | <100 | MDC personnel | No | 9350 |  | 2025-04-07 | 11:30 AM | <100 | 100 |  | Main sewer flushed by jet truck and stoppage relieved | East Hartford | 345 Main St, East Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-03-21 | 10:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | MDC personnel | <100 | Visual by MDC personnel | No | 9274 |  | 2025-03-21 | 11:30 AM | <100 | 100 |  | Main sewer flushed by jet truck and stoppage relieved | East Hartford | 49 King St, East Hartford, CT
[18 empty] | TOTAL VOLUME | 300
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-10-08 | 11:45 AM' | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | PAPERS CAUSING BLOCKAGE | MDC PERSONNEL | < 10,000 GALLONS | SCADA | Yes | 9993 | CONNECTICUT RIVER | 2025-10-09 | 08:30 AM | 7700 GALLONS | 7700 | null | Main sewer flushed by jet truck and stoppage relieved | Hartford | 2370 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-30 | 09:00 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | null | Railroad worker | <1000 | MDC Personnel visual observation | No | 9962 | null | 2025-09-01 | 03:15 PM | <1000 | 900 | null | Crews responded to by-pass with equipment to stop the overflow. Contractor responding to repair collapsed section | Hartford | Albany Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-30 | 03:15 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | SEWER MAIN COLLAPSE | RAILROAD PERSONNEL | < 1000 | MDC PERSONNEL | No | 9970 | null | 2025-10-03 | 02:00 PM | 1000 GALLONS | 1000 | null | CONTRACTOR REPAIRED SEWER MAIN | Hartford | 1419 1/2 Main St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-29 | 04:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | OVERFLOW MAIN SEWER BACKED UP | PASSER BY | <100G | MDC PERSONNEL | Yes | 9961 | FOLLY BROOK DIKE | 2025-09-30 | 02:30 PM | < 1000 GALLONS | 900 | null | BYPASS ELIMINATED ONCE COLLAPSED SEWER MAIN WAS REPAIRED | Hartford | 1010 Wethersfield Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-07-12 | 10:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | PARTIAL BLOCKAGE DUE TO GREASE. | MDC SCADA | LESS THAN 500 GAL | MDC SCADA | Yes | 9710 | PARK RIVER CONDUIT | 2025-07-12 | 11:45 PM' | 800 GAL | 800 | null | JET TRUCK RELIEVED. | Hartford | Capitol Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-07-08 | 11:30 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | WET WEATHER EVENT EXCESSIVE FLOWS | HOMEOWNER | <100G | MDC PERSONEL | No | 9695 | null | 2025-07-09 | 07:30 AM | <100g | 90 | null | WET WEATHER EVENT ENDED | Hartford | Morningside St W, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-04-20 | 07:30 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | MAIN SEWER BACKUP | MDC PERSONNEL | < 100 GALLONS | MDC PERSONNEL | No | 9396 |  | 2025-04-20 | 10:45 PM | < 100 GALLONS | 90 |  | JET-TRUCK RELIEVED SEWER BLOCKAGE | Hartford | 129 Woodland Dr, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-12 | 10:30AM | Basement | Raw Sewage | Sewage Line Blockage - Other | BYPASS DUE TO MAIN SEWER BACKED UP | HOMEOWNER | <100GALLONS | MDC PERSONNEL | No | 9365 |  | 2025-04-12 | 12:00 PM | <100GALLONS | 90 |  | JET TRUUCK RELIEVED MAIN SEWER | Hartford | 900 West Blvd, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-04-12 | 07:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | MAIN SEWER BACKED UP | CITY HARTFORD PUBLIC WORKS PASSER BY | <100GALLONS | MDC PERSONNEL | No | 9364 |  | 2025-04-12 | 12:00 PM | <100GALLONS | 90 |  | MAIN SEWER RELIEVED BY JET TRUCK | Hartford | S Whitney St, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 09:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | HOMEOWNER | < 100 GALLON | MDC PERSONNEL | No | 9188 |  | 2025-03-06 | 09:45 AM | < 100 GALLONS | 90 |  | MAIN SEWER FLUSHED BY JET TRUCK AND STOPPAGERELIEVED | Hartford | 37 Chadwick Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-02-03 | 01:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | SCADA | < 10,000 GALLONS | SCADA | Yes | 9070 | PARK RIVER CONDUIT | 2025-02-03 | 02:15 PM | 2,000 TOTAL GALLONS | 2000 |  | FLUSHED SEWER MAIN WITH A JET TRUCK | Hartford | Capitol Ave, Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-12-26 | 00:00 AM | Manhole | Raw Sewage | Other | WATER MAIN BREAK | SCADA ALARM | <100GALLONS | SCADA SYSTEM | Yes | 10219 | GULLY BROOK CONDUIT | 2025-12-26 | 02:00 PM | .003MG | 3000 | null | BROKEN WATER MAIN WAS SHUT DOWN | Hartford | 266 Capen St, Hartford, CT
[18 empty] | TOTAL VOLUME | 16750
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-05 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | null | MDC OPERATIONS CREW | LESS THAN 100 GAL | MDC PERSONEL | No | 9867 |  | 2025-09-05 | 07:30 PM | LESS THAN 100 GAL | 90 | null | MDC OPERATIONS FIXED BREAK ON FORCE SEWER MAIN | Rocky Hill | 235 Dividend Rd, Rocky Hill, CT
[18 empty] | TOTAL VOLUME | 90
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONEL | LESS THAN 500 GAL | MDC PERSONEL | Yes | 9513 | TROUT BROOK | 2025-05-10 | 12:30 PM | LESS THAN 1,000 GAL | 900 |  | EXTRANEOUS FLOWS RECEDED IN MAIN LINE SEWER | West Hartford | 1 Linbrook Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-06-24 | 02:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | MDC Personnel | <100 | Visual observation by MDC personnel | No | 9677 |  | 2025-06-24 | 03:00 PM | <100 | 90 | null | Main sewer flushed by jet truck and stoppage relieved | West Hartford | 10 Trotwood Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-31 | 04:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event | null | MDC SCADA | 0.012 MG | MDC SCADA | Yes | 10088 | PIPER BROOK | 2025-10-31 | 06:30 AM | 0.017 MG | 17000 | null | RAIN EVENT ENDED. | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 02:00 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | Heavy rain | SCADA | 2.3 MG | SCADA | Yes | 9507 | PIPER BROOK | 2025-05-11 | 02:30 PM | 9.13 MG | 9130000 |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 03:00 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 6.307 MG | MDC SCADA | Yes | 9463 | PIPER BROOK | 2025-05-07 | 02:30 AM | 6.461 MG | 6461000 |  | Bypass is eliminated once flows drop below overflow | West Hartford | 115 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 03:15 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | .010 MG | MDC SCADA | Yes | 9462 | TROUT BROOK | 2025-05-06 | 01:15 PM | 2.041 MG | 2041000 |  | RAIN EVENT ENDED FLOWS RECEDED | West Hartford | 121 Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:00 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | HOMEOWNER CALLED MDC | LESS THAN 100 GAL | MDC PERSONEL | No | 9515 |  | 2025-05-10 | 07:30 AM | LESS THAN 100 GAL | 90 |  | EXTRANEOUS FLOWS IN MAIN SEWER RECEDED | West Hartford | 152 N Main St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 03:00 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | HEAVY RAIN | SCADA | 400,000 GAL | SCADA | Yes | 9509 | TROUT BROOK | 2025-05-10 | 04:15 AM | 0.44 MG | 440000 |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-06 | 05:45 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | .020 MG | MDC SCADA | Yes | 9464 | TROUT BROOK | 2025-05-06 | 10:15 AM | .007MG | 7000 |  | RAIN EVENT ENDED FLOWS RECEDED | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-06 | 01:30 AM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC SCADA | 1000 | SCADA | Yes | 9178 | TROUT BROOK | 2025-03-06 | 09:45 AM | 2.61 MG | 2610000 |  | BYPASS IS ELIMINITED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 212 Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:30 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONEL | LESS THAN 500 GAL | MDC PERSONEL | Yes | 9514 | TROUT BROOK | 2025-05-10 | 12:30 PM | LESS THAN 1,000 GAL | 900 |  | EXTRANEOUS FLOWS RECEDED | West Hartford | 3 Linnard Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 12:15 PM | Basement | Raw Sewage | Excessive Flows - Storm Event |  | Homeowner | <100 | MDC Personnel | No | 9193 |  | 2025-03-07 | 07:30 AM | <100 | 90 |  | Surcharge backups are eliminated once elevated sewer flows recede back to normal | West Hartford | 43 Wyndwood Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 11:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | HOMEOWNER | < 100 | MDC PERSONNEL | No | 9190 |  | 2025-03-06 | 11:15 AM | <100 | 90 |  | Main sewer flushed by jet truck and stoppage relieved | West Hartford | 66-68 Levesque Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 11:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Homeowner | < 100 | MDC Personnel | No | 9191 |  | 2025-03-06 | 11:15 AM | <100 | 90 |  | Main sewer flushed by jet truck and blockage relieved | West Hartford | 67-69 Levesque Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-03-14 | 03:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | WHFD CALLED MDC COMMAND CENTER | LESS THAN 1000 | MDC PERSONELL | Yes | 9227 | TROUT BROOK | 2025-03-14 | 06:45 PM | LESS THAN 25,000 | 24000 |  | JETTED MAIN SEWER AND RELIEVED BLOCKAGE | West Hartford | 78 LaSalle Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 10:15 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | PER OUR SCADA SYSTEM | 1000 Gallons | SCADA SYSTEM | Yes | 9170 | PIPER BROOK | 2025-03-06 | 10:30 PM | 5.6 MG | 5600000 |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | 83 Hillcrest Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event |  | MDC PERSONEL | LESS THAN 500 GAL | MDC PERSONEL | Yes | 9512 | TROUT BROOK | 2025-05-10 | 12:30 PM | LESS THAN 1,000 GAL | 9000 |  | RAIN EVENT ENDED EXTRANEOUS FLOWS RECEDED IN MAIN SEWER | West Hartford | N Main St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-07-30 | 09:30 PM | Basement | Raw Sewage | Unknown | MAIN SEWER BACKED UP JET TRUCK IN ROUTE | HOMEOWNER / PROPERTY MANAGER | <100GALLONS | MDC PERSONELL | No | 9761 |  | 2025-07-30 | 11:15 PM | <100GALLONS | 90 | null | JET TRUCK RELIEVED BLOCKAGE. | West Hartford | New Britain Ave, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 02:15 PM | Sewer Main | Raw Sewage | Excessive Flows - Storm Event | Heavy Rain | SCADA | 3.5 MG | SCADA | Yes | 9508 | TROUT BROOK | 2025-05-10 | 04:00 PM | 7.112 MG | 7112000 |  | BYPASS IS ELIMINATED ONCE FLOWS DROP BELOW OVERFLOW | West Hartford | Talcott Rd, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 11:00 PM | Manhole | Raw Sewage | Excessive Flows - Storm Event | null | PER OUR SCADA SYTEM | 1000 GALS | PER OUR SCADA | Yes | 9171 | TROUT BROOK | 2025-03-06 | 09:45 AM | 2.61 MG | 2610000 | null | Bypass is eliminated once flows drop below overflow | West Hartford | Trout Brook Dr, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-12-11 | 02:45 PM | Lateral - Private | Raw Sewage | Sewage Line Broken by Contractor or other utility | POLE INSTALED THROUGH SEWER LATERAL CAUSING BACK UP | PRIVATE PROPERTY MANAGEMENT | < 100 | MDC PERSONNEL | No | 10178 |  | 2025-12-12 | 12:00 PM | <100g | 90 | null | Utility pole was removed and repaired damaged lateral | West Hartford | 237 Fern St, West Hartford, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-12-18 | 06:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | CUSTOMER REPORTED BACKUP | LESS THAN 100 GAL | MDC PERSONEL | No | 10184 |  | 2025-12-18 | 08:15 PM | LESS THAN 100 GAL | 90 | null | MDC CREWS JETTED MAIN SEWER | West Hartford | 52 Boulanger Ave, West Hartford, CT
[18 empty] | TOTAL VOLUME | 36063520
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-09-02 | 08:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | null | Homeowner/Resident | <100 Gallons | MDC Personnel | No | 9850 |  | 2025-09-02 | 09:30 AM | <100 Gallons | 90 | null | Main sewer flushed by jet truck and stoppage relieved | Windsor | 120 Preston St, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Dry | 2025-05-14 | 01:00 PM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Mechanical Issues at pump stationSSO bypass started approx. 2:00pm | MDC PERSONNEL | > 5000 | MDC PERSONNEL | Yes | 9526 | Farmington River | 2025-05-14 | 08:45 PM | 25000gal | 25000 | null | Pump bypass was setup to downstream manhole | Windsor | 34 Ridge St, Windsor, CT
MDC COLLECTIONS ONLY | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-17 | 10:15 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | MDC personnel | <100 | MDC personnel | No | 9248 |  | 2025-03-17 | 10:45 AM | <100 | 90 |  | Main sewer flushed by jet truck and stoppage relieved | Windsor | 103 Poquonock Ave, Windsor, CT
[18 empty] | TOTAL VOLUME | 25180
NPDES PERMITTED BYPASS OF SECONDARY TREATMENT DATA COLLECTED FROM MONTHLY MORS | [19 empty] | DURATION
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-01-01 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-01-01 |  | 7.00 MGD | 7000000 | 4.78 Hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-01-31 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-01-31 |  | 2.54 MGD | 2540000 | 2.54 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-02-16 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-02-16 |  | 24.7 MGD | 24700000 | 9.75 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-02-17 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-02-17 |  | 2.57 MGD | 2570000 | 2.85 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-03-05 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-03-05 |  | 12.3 MGD | 12300000 | 4.26 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-03-06 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-03-06 |  | 52.43 MGD | 52430000 | 24 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-03-07 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-03-07 |  | 1.5 MGD | 1500000 | 1.5 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-03-17 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-03-17 |  | 21.73 MGD | 21730000 | 12.78 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-03-21 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-03-21 |  | 1.73 MGD | 1730000 | 1.62 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-03-24 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-03-24 |  | 20.55 MGD | 20550000 | 9.62 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-04-01 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-04-01 |  | 5.2 MGD | 5200000 | 3.83 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-04-05 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-04-05 |  | 4.74 MGD | 4740000 | 3.08 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-04-12 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-04-12 |  | 11.51 MGD | 11510000 | 15.48 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-04-26 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-04-26 |  | 9.62 MGD | 9620000 | 6.09 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-03 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-03 |  | 4.62 MGD | 4620000 | 5.48 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-05 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-05 |  | 18.33 MGD | 18330000 | 15.25 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-06 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-06 |  | 66.58 MGD | 66580000 | 24 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-07 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-07 |  | 9.96 MGD | 9960000 | 24 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-08 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-08 |  | 4.42 MGD | 4420000 | 12.19 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-09 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-09 |  | 48.56 MGD | 48560000 | 12.12 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-10 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-10 |  | 48.98 MGD | 48980000 | 24 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-11 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-11 |  | 10.47 MGD | 10470000 | 24 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-12 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-12 |  | 0.07 MGD | 70000 | 5.2 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-22 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-22 |  | 8.73 MGD | 8730000 | 13.62 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-23 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-23 |  | 2.21 MGD | 2210000 | 3.88 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-05-31 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-05-31 |  | 16.73 MGD | 16730000 | 15.23 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-06-10 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-06-10 |  | 1.18 MGD | 1180000 | 2.57 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-07-02 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-07-02 |  | 0.54 MGD | 540000 | 4.68 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-07-09 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-07-09 |  | 7.03 MGD | 7030000 | 5.65 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-07-10 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-07-10 |  | 9.39 MGD | 9390000 | 5.58 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-07-14 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-07-14 |  | 1.67 MGD | 1670000 | 1.93 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-07-20 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-07-20 |  | 4.27 MGD | 4270000 | 3.53 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-07-31 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-07-31 |  | 7.31 MGD | 7310000 | 3.46 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-08-01 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-08-01 |  | 4.17 MGD | 4170000 | 7.89 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-08-20 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-08-20 |  | 18.89 MGD | 18890000 | 7.01 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-08-21 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-08-21 |  | 9.46 MGD | 9460000 | 5.09 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-09-05 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-09-05 |  | 2.81 MGD | 2810000 | 1.96 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-09-06 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-09-06 |  | 6.41 MGD | 6410000 | 3.05 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2026-09-07 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2026-09-07 |  | 8.12 MGD | 8120000 | 16.09 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-09-24 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-09-24 |  | 3.17 MGD | 3170000 | 2.05 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-09-25 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-09-25 |  | 1.7 MGD | 1700000 | 1.67 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-10-08 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-10-08 |  | 1.84 MGD | 1840000 | 2.79 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-10-12 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-10-12 |  | 2.55 MGD | 2550000 | 3.73 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-10-13 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-10-13 |  | 10.23 MGD | 10230000 | 8.26 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-10-20 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-10-20 |  | 0.52 MGD | 520000 | 1.14 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-10-30 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-10-30 |  | 17.75 MGD | 17750000 | 4.92 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-10-31 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-10-31 |  | 21.75 MGD | 21750000 | 10.92 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-11-15 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-11-15 |  | 1.85 MGD | 1850000 | 1.72 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-11-16 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-11-16 |  | 1.03 MGD | 1030000 | 1.07 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-12-02 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-12-02 |  | 13.15 MGD | 13150000 | 7.15 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-12-19 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-12-19 |  | 28.14 MGD | 28140000 | 13.27 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
MDC TREATMENT PLANT |  | NPDES PERMITTED BYPASS OF SECONDARY TREATMENT |  | 2025-12-29 |  | Treatment Plant |  | Excessive Flows - Storm Event |  | SCADA | REPORTED THROUGH MOR |  | Yes |  | CT River | 2025-12-29 |  | 9.58 MGD | 9580000 | 5.33 hours | Rain stopped | Hartford | 231 Brainard Road, Hartford, CT
[18 empty] | TOTAL VOLUME | 612290000
[18 empty] | MDC TOTAL VOLUME | 648395840

## Meriden
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MERIDEN | Closed | Sewage Bypass | Dry | 2025-02-05 | 09:45 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease and rag buildup in manhole | Called in by homeowner of 90 Old Gate RD. Manhole is located in her backyard. | approx 75 gallons escaped. | Visual estimation | No | 9074 |  | 2025-02-05 | 10:30AM | approx 75 gallons | 75 |  | Line was jetted to relieve blockage | Meriden | 90 Old Gate Rd, Meriden, CT
[18 empty] | TOTAL VOLUME | 75

## Milford
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2025-11-24 | 12:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | null | Call from Milford Building maintenance | 100 gal | estimate | No | 10134 | null | 2025-11-24 | 01:00 PM | 100 gallons | 100 | null | Jetted easement off Bird Lan to clear blockage and then drove onto easement to clear from Pond Point to French Drive. Follow up on Tues and Wed with CCTV of sewer main. | Milford | 66 Bird Ln, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2025-05-20 | 07:45 AM | Basement | Raw Sewage | Sewage Line Blockage - Roots | null | Phone Message | 50 gallons | Estimated quantity was estimated. | No | 9564 | NA | 2025-05-20 | 09:00 AM | 50 gallons | 50 | null | Jet Truck cleared blockage | Milford | 16 Earle St, Milford, CT
MILFORD - HOUSATONIC WPCF | Closed | Sewage Bypass | Dry | 2025-03-25 | 10:30AM | Basement | Raw Sewage | Sewage Line Blockage - Roots |  | resident call | undetermined | undetermined | No | 9324 |  | 2025-03-25 | 01:00 PM | 20 gallons | 20 |  | roots cut and cleared | Milford | 39 Minute Man Dr, Milford, CT
[18 empty] | TOTAL VOLUME | 170

## Montville
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
MONTVILLE | Closed | Sewage Bypass | Dry | 2025-07-28 | 08:15 AM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Poor bedding (i.e. cobbles, gravel) for the force main has caused several problems in this area before. FY 2026 CIP addressing issue. | CTDOT paving contractor (American Industry) notified the Montville WPCA. Reported to CTDEEP overnight. | 200 g | Estimated passed on flow observed. | No | 9755 | n/a | 2025-07-28 | 10:00 AM | 200 g | 200 | null | Pump Station bypass via Montville WPCF pumper truck then emergency contractor (B & W Paving & Landscaping, Waterford, CT) repair of FM line break. FY 2026 CIP project to repair line. | Montville | 2549 CT-32, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2025-04-02 | 01:30 PM | Sewer Main | Raw Sewage | Mechanical Equipment Failure | n/a | Collections Operator check of previous release area. | 100 g | Estimated by visual inspection. Quick response due to routine inspection by Coll Operator of this previous release spot- FM from Kitemaug PS. | Yes | 9331 | Mohegan Brook | 2025-04-02 | 01:45 PM | 200 g | 200 |  | Pump Station pumps turned off- pumper truck draining wetwell with delivery to WPCF (for bypass of FM breached pipe). Emergency contractor onsite overnight for excavation/pipe repair. | Montville | 1 Kitemaug Rd, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2025-01-28 | 01:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | n/a | Public Works called to report odor in the vicinity of the surcharged manhole. | 200 g | Estimated quantity based on direct inspection. Responded immediately to vacuum/jet line and clean up toilet paper and released raw wastewater and spread lime. | No | 9062 | n/a | 2025-01-28 | 02:30 AM | 250 g | 250 |  | Jetting/Flushing line with vacuuming to remove rags in sewer main through cross-country. Flow re-established and confirm on both Jan 28 and 29. | Montville | 19 Brewer St, Montville, CT
MONTVILLE | Closed | Sewage Bypass | Dry | 2025-12-21 | 04:45 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Original construction of force main had improper bedding (i.e. stones, cobbles) and has led to abrasions of cast iron pipe. | Public call in to dispatch and then to on-call operator. | 300 g along pavement on Route 32. Untreated sewage was cleaned up. PS bypass with pumper truck almost immediately. Spill stopped after 15 minutes. | Trickle observed on roadway surface. PS stopped- no pumping 15 minutes after release found. PS Bypass with pumper truck | No | 10205 | n/a | 2025-12-21 | 05:00 PM | 300 g | 300 | null | Pump Station shut down and then bypassed with Pumper Truck 15 minutes after initial report of wastewater spillage. Emergency response contractor excavated to force main for repair. Pressure tested line/repair. | Montville | 2549 Norwich-New London Turnpike, Montville, CT
[18 empty] | TOTAL VOLUME | 950

## Naugatuck
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NAUGATUCK WPCF | Closed | Sewage Bypass | Dry | 2025-05-06 | 05:30 PM | Lateral - Private | Raw Sewage | Sewage Line Broken by Contractor or other utility | Work done by Contractor was thought to be the issue | Resident made call | Minimal in garage | Visual | No | 9651 |  | 2025-05-06 | 07:30 PM | Minimal | 10 |  | Line was jetted to clear out debris & resolve issue for homeowner / Contractor repair the damaged line the next day | Naugatuck | 65 May Ave, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-06 | 05:30 AM | Treatment Plant | Disinfected Partially Treated Raw Sewage | Excessive Flows - Storm Event |  | By operator | Between 15-17 MGD | Flow meter | Yes | 9473 | Naugatuck River | 2025-05-07 | 07:30 AM | Rain stopped, Flow stabilized around 10-11mgd | 10500000 |  | Solids stopped overflowing, flow slowed down.Clear effluent. | Naugatuck | 500 Cherry St, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-31 | 00:00 AM | Basement | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | A previous lateral repair downstream caused rocks to fall into the main. | Homeowner discovered it | Approximately 300 gallons. | Estimated quantity was based off of the damage done to the basement. | No | 9306 |  | 2025-03-31 | 02:00 AM | 300 gallons | 300 |  | Jetting main sewer line. | Naugatuck | 118 Ward St, Naugatuck, CT
NAUGATUCK WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-12-19 | 07:00 AM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure | null | Plant loos the power. | 4MGD effluent flow | Flow meter. | Yes | 10188 | Naugatuck river | 2025-12-19 | 11:15 PM | Approximately 6MGD | 6000000 | null | Power restored to the plant, air restored to the aeration tanks. | Naugatuck | 500 Cherry St, Naugatuck, CT
[18 empty] | TOTAL VOLUME | 16500310

## New Britain
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW BRITAIN | Closed by DEEP | Sewage Bypass | Dry | 2025-08-04 | 09:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease | Grease - Rags | Property owner called. | 90 gallons | Visual | No | 9781 |  | 2025-08-04 | 00:00 AM | 90 Gallons | 90 | Visual | Jet rod main sewer line. | New Britain | 205 Bingham St, New Britain, CT
NEW BRITAIN | Closed | Sewage Bypass | Dry | 2025-04-15 | 06:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags | Rags/Grease | Renter at 166 Broad St | 1500 Gallons | Visual | No | 9387 |  | 2025-04-15 | 07:00 PM | 1500 Gallons | 1500 | Visual | Jet Rod Main Sewer Line | New Britain | 166 Broad St, New Britain, CT
NEW BRITAIN | Closed by DEEP | Sewage Bypass | Dry | 2025-04-10 | 10:30AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease |  | Property Owner | 500 gallons | Visual | No | 9362 |  | 2025-04-10 | 11:00 AM | 500 gallons | 500 |  | Jet Rod Main Line | New Britain | 178 Winfield Dr, New Britain, CT
[18 empty] | TOTAL VOLUME | 2090

## New London
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2025-10-25 | 00:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | 2 manholes were reported to customer service department as backed up. Upon the crews arrival they determined the sewer main (owned by the utility) was flowing fine but two manholes (privately owned by business) were clogged and causing the back up inside | Called in to the customer service line by the business owner of Popeyes Chicken. DPH Ledgelight Health was also notified of the situation. | Unknown, bypass on a private line. | N/A | No | 10062 | null | 2025-10-29 | 06:00 PM | Unknown, not reported to us by business owneer | 50 | null | Business owner hired an outside company to jetrod the blockages. | New London | 455 Colman St, New London, CT
NEW LONDON STP | Closed | Sewage Bypass | Dry | 2025-10-03 | 12:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease | Excess build up an other debri in the large (30") gravity line feeding the STP. | Call in by local business owner reporting sewage smell in cove. | 673,920 gallons is estimated to have been bypassed to the environment since we were notified on 10/3/2025 | By using attached pipe flow sheet and assuming a velocity of 2 ft/sec | Yes | 9968 | Shaw Cove via underground storm culvert fed by storm catch basins and a storm pump station located on Howard Street NLCT. | 2025-10-05 | 01:30 AM | estimated 673,920 gallons | 673920 | null | By clearing a blockage in a large sewer interceptor entering the STP | New London | 150 Howard St, New London, CT
[18 empty] | TOTAL VOLUME | 673970

## New Milford
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEW MILFORD | Closed | Sewage Bypass | Dry | 2025-02-18 | 09:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | Homeowner called Sewer Department. | 500 Gallons | Visual Assessment. | No | 9124 |  | 2025-02-18 | 10:00 PM | 500 Gallons | 500 |  | Jetted main line and cleared grease blockage. | New Milford | 181 Wellsville Ave, New Milford, CT
[18 empty] | TOTAL VOLUME | 500

## Newtown
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NEWTOWN W P C F | Closed | Sewage Bypass | Dry | 2025-11-20 | 09:30 AM | Sewer Main | Raw Sewage | Other | Fitting went bad | A call was made to Public Works Office | 500 gallons | estimate | Yes | 10132 | On map it looks like Tom Brook - some flow (low) | 2025-11-20 | 02:00 PM | 500 gallons | 500 | null | repaired/replaced failed fitting | Newtown | 11 Edmond Rd, Newtown, CT
[18 empty] | TOTAL VOLUME | 500

## North Haven
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2025-08-13 | 05:30 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | the bypass was caused by severely eroded pipe in the downstream section of Carlson Ave. We installed a smart cover to alert us of any impending overflows and that cover has prevented several SSO's but in this case, the smart cover system did not send a t | App notification on the Iphone. | 500 gallons | Visual Observation | No | 9791 |  | 2026-01-13 | 9:30 | Approx 500 gallons | 500 | Visual observation | the line was jetted. Construction to replace pipe will begin in early September. | Orange | Carlson Rd, Orange, CT
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2025-06-15 | 00:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Other | The pipe is severely deteriorating on the bottom, so debris is catching and plugging the pipe. There is some kind of defect at 200 ft that we cant visually locate. | Resident reported | <500 gallons | Visual estimate | No | 9657 |  | 2025-06-15 | 03:00 PM | < 500 gallons | 450 | Visual observation | We jet cleaned the pipe. We are going to jet clean this location weekly until the required repairs are made. We are also going to install a SMART COVER on 6/18/25 so that if the pipe backs up, we will get notification from the system that the pipe has a | Orange | Carlson Rd, Orange, CT
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2025-05-28 | 10:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Grease | STAFF PERFORMED A FOG INSPECTION ON 5/27/2025 AND FOUND SEVERE GREASE BUILD UP IN THE RESTAURANT DISCHARGE MANHOLE. I NOTIFIED BOTH THE RESAURANT MANAGER AND ALSO THE PROPERTY MANAGER. I ADVISED HIM TO HIRE A DRAIN CLEANER AND TO DO IT IMMEDIATELY BECAU | STAFF RECEIVED A PHONE CALL FROM THE "AT HOME" FURNISHINGS STORE TO REPORT THIER TOILETS WOULD NOT FLUSH. | 500-1000 GALLONS. DIFFICULT TO DETERMINE. | VISUAL OBSERVATION. | No | 9596 |  | 2025-05-28 | 10:30AM | estimated at 500 - 1000 gallons | 900 | Visual observation | United Sewer cleaning was called by the restaurant owner to clear all grease, the town issued a NOV per the grease regulations. We will follow up to ensure their equipment is properly maintained going forward. We found their AGRU was not being maintaine | North Haven | 350 Universal Dr N, North Haven, CT
NORTH HAVEN WPCF | Closed | Sewage Bypass | Dry | 2025-12-01 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Blockage - Roots | roots | Resident emailed the Town Engineer, Veolia Staff responded. | 50 gallons total. This manhole serves 2 homes. | Visual | No | 10157 |  | 2025-12-01 | 11:00 AM | <50 gallons | 45 | Visual observation | We jetted the line initially, and used the root cutter to clear the roots. Roots are from a tree adjacent to the bridge crossing | North Haven | Kent Dr, North Haven, CT
[18 empty] | TOTAL VOLUME | 1895

## Norwalk
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-10-31 | 09:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | null | A resident called into the City of Norwalk's customer service. | Around 185 gallons. | Visual | Yes | 10091 | Norwalk River | 2025-10-31 | 10:00 AM | 185 gallons | 185 | null | Collections team cleared the blockage downstream . | Norwalk | 12 Lexington Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-07-23 | 07:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | The bottom of the manhole has failed/crumbled. | Nearby Stormwater inspection and dye testing | <0.5 GPM | CCTV footage of the Stormwater Line | Yes | 9744 | Norwalk River | 2025-07-24 | 12:00 PM | 870 Gals | 870 | null | A construction company rehabilitated the bottoms of the affected manholes with concrete. | Norwalk | 6 Gordon St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-07-11 | 07:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Failure of sewer main | Routine MS4 inspection of nearby Stormwater lines | ~0.25 GPM | Visually from CCTV footage | Yes | 9709 | Norwalk River | 2025-07-11 | 01:45 PM | ~101 Gal | 101 | null | A contractor replaced the broken section of clay pipe with PVC pipe. | Norwalk | 8 W Rocks Rd, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-02-16 | 09:00 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure |  | It was discovered during a maintenance mechanic daily check of the station. | 48,800 gallons | Previous flow trends and time of day | Yes | 9104 | Keeler Brook | 2025-02-16 | 10:15 AM | 48,800 gallons | 48800 |  | Equipment was restored to full capacity. | Norwalk | 467 Connecticut Ave, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-02-14 | 12:00 PM | Basement | Raw Sewage | Sewage Line Blockage - Other | The basement at 12 Bouton St got backed up due to a blockage in the line. Causing the sump to discharge into a catch basin on Bouton St. | A Smart Cover alert. | 200 gallons | Vactor Truck | No | 9095 |  | 2025-02-14 | 12:15 PM | 200 gallons | 200 |  | Cleared blockage in Sanitry Sewer Main | Norwalk | 12 Bouton St, Norwalk, CT
NORWALK WPCF | Closed | Sewage Bypass | Dry | 2025-01-15 | 07:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | First District called it in. | 5 gal/min, 30 minutes | Vactor Truck | Yes | 9029 | Betts Brook | 2025-01-15 | 07:30 AM | 110 gallons | 110 |  | Collection system crew was able free the blockage in the main sewer line | Norwalk | Park, Norwalk, CT
[18 empty] | TOTAL VOLUME | 50266

## Norwich
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-10-15 | 03:00 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags | Manhole was blocked | Customer Call | 100 gallons | Visual Estimate | No | 10021 | n/a | 2025-10-15 | 04:00 PM | 100 gallons | 100 |  | NPU assisted with raking rags out of manhole, getting it to drain. Advised calling a plumber to jet and clean lines | Norwich | 181 W Town St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-08-29 | 11:45 AM' | Sewer Main | Raw Sewage | Other | On August 29, 2025, at approximately 11:40 AM, NPU was notified of a sanitary sewer overflow (SSO). The overflow was attributed to heavy rainfall combined with the tie over from a temporary force main to the newly lined force main. During the tie-in proce | During construction | 50000 Gallons | CSO-Amount from CSO 4 Plus Estimate | Yes | 9853 | Thames River | 2025-08-29 | 03:30 PM | 50000 Gallons | 50000 | Meter Plus Estimate | Force main returned to service. | Norwich | 190 S Thames St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-06-23 | 10:45 AM | Treatment Plant | Sludge Spill | Sewage Line Blockage - Rags | supernatant overflow line blocked wit rags | Operator working in area discovered | 300-500 gallons | Visual estimate. | Yes | 9671 | Yantic River West | 2025-06-23 | 12:00 PM | 500 gallons | 500 | Visual | blocked line was cleared. Bypass was directed to sump pumps pumping to headowrks. | Norwich | 44 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-06-03 | 07:00 AM | Treatment Plant | Sludge Spill | Mechanical Equipment Failure | Sludge carrier (HI STONE) had mechanical failure with cake dumpster latches | Hauler called NPU | approximately 4 yards of digester sludge cake | visual estimate | No | 9622 | null | 2025-06-03 | 07:15 AM | 4 Yards of cake, shoveled back into dumpster. NO CAKE ON GROUND | 0 | Visual | Picked up cake and cleaned area | Norwich | 44 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-06-03 | 07:15 AM | Sewer Main | Raw Sewage | Other | Excessive flows from fire hydrant flushing near CSO | Flow Meter | 3813 | Flow Meter | Yes | 9623 | Shetucket | 2025-06-03 | 07:15 AM | 3813 | 3813 | Flow Meter | stopped hydrant flushing | Norwich | 119 N Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-05-21 | 11:30 AM | Treatment Plant | Raw Sewage | Sewage Line Break, Crack or Failure | null | water bubbling from ground near junction chamber for both force mains entering the plant | none-water was leaking into vault.Flow Meter discharge for making repair on pipe. | Visual | No | 9567 | Shetucket | 2025-05-21 | 11:30 AM | 489031 | 489031 | Flow Meter | cleaned pipe and encased in concrete | Norwich | 52 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-05-19 | 10:00 AM | Sewer Main | Raw Sewage | Unknown | Possible malfunction of meter, or animal passed over sensor. No visible overflow in diversion structure. | Flow Meter report | 218 Total Gallons | Flow Meter | No | 9563 | Shetucket | 2025-05-19 | 10:15 | 218 | 218 | Flow Meter | Visual inspection of weir wall | Norwich | 385 N Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-05-07 | 09:45 AM | Sewer Main | Select... | Other | See Comments | Water leaking into the road | 53529 | Flow meter | Yes | 9482 | Shetucket | 2025-05-07 | 12:00 PM | 53529 | 53529 |  | Water shut off, and repairs made | Norwich | 119 N Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-04-01 | 06:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Crack in the top of the pipe, it appears to have been an issue with the casting of the pipe from the manufacture. All other sections looked to be in great shape. | Customer call | 200gpm when pumping | 1600 gallons. Only leaks when pump was on. 200 gpm x 8 pump cycles. Plus some leaking while making repairs. 3000 Gallons | Yes | 9328 | Thames River | 2025-04-03 | 12:15 PM | 4600 | 4600 |  | Replaced sections of pipe. 155inches=12' 10'' replaced | Norwich | 22 Thames Terrace, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-24 | 02:00 PM | Treatment Plant | Partially Treated Raw Sewage | Excessive Flows - Storm Event | Broken concrete distribution box. | Operators discovered while working | 500 gal | Visual rate | No | 9279 | N/A | 2025-03-24 | 02:15 AM | 500 gal | 500 |  | Used pump to pump back to headworks. | Norwich | 52 Falls Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-05 | 06:15 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Customer call | 665013 | Flow Meter plus visual estimate | Yes | 9158 | Yantic River/ Shetucket | 2025-03-06 | 03:45 PM | 659013+6000 (50 gpmx2 hrs)=665013 | 665013 |  | Replace 230'' of 20'' DIP | Norwich | 46 W Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-01-30 | 02:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags |  | Call from plumber | 100 Gallons | Visual Estimate | No | 9065 |  | 2025-01-30 | 03:30 PM | 100 gals | 100 |  | plumber jetted line to clear blockage. Told he must clean up area around cleanout. | Norwich | 49 Boswell Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-01-16 | 06:45 PM | Manhole | Raw Sewage | Sewage Line Blockage - Rags |  | Customer call | No overflowing upon arrival- evidence of a small overflow | Visual estimate | No | 9036 |  | 2025-01-16 | 07:00 PM | 100 Gallons | 100 |  | Jetted main | Norwich | 413 E Main St, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-01-10 | 03:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Partial blockage- evidence of spill- not actively overflowing | Customer Call | 200 gallons | Visual estimate | No | 9023 |  | 2025-01-10 | 03:30 PM | 200 Gallons | 200 |  | Sucked out manhole and jetted main. | Norwich | 48 Woodside Ave, Norwich, CT
NORWICH WPCF | Closed | Sewage Bypass | Dry | 2025-12-03 | 06:15 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | null | Called in from operator- saw water bubbling up in the road. | Unknown-Meter is tracking total overflow gallons at the Rose Alley pump station | Flow Meter plus estimate | Yes | 10172 | Shetucket River | 2025-12-03 | 06:00 PM | 394242 | 394242 | null | Replaced just over 20 feet of sewer main | Norwich | 23 Falls Ave, Norwich, CT
[18 empty] | TOTAL VOLUME | 1060155

## Orange
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
ORANGE | Closed | Sewage Bypass | Dry | 2025-08-25 | 04:00 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | probable line break or previous construction debris. Upon arrival, we found construction stone 3/4 inch in the pipe which was likely allowed into the pipe during a recent new connection upstream. | reported by customer | 500 gallons | visual observation | No | 9835 |  | 2025-09-25 | 06:00 PM | ESTIMATED AT 500 GALLONS | 500 |  | VISUAL OBSERVATION | Orange | Boston Post Rd, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-06-30 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | Responding technicians found that a large ball of rags has collected in the pipe. I reviewed the CCTV for this pipe section and there are no defects in the pipe. | Reported by a contractor working in the area. | 15-20 gallons | Visual observation | No | 9683 |  | 2025-06-30 | 12:00 PM | 20 gallons | 20 |  | jetting the sewer pipe. | Orange | 80 Boston Post Rd, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-06-12 | 12:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | Blockage is due to deteriorating pipe. This pipe is in poor shape so rocks and aggregate are in the line. We cleared it the best we could during the last incident, in early February. | Resident reported to Bob Brinton, DPW director | <500 gallons | Visual estimate. | No | 9654 |  | 2025-06-12 | 02:00 PM | <500 gallons | 450 |  | Pipe Jetting | Orange | Bull Hill Ln, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-02-18 | 11:30 AM | Lateral - Public | Raw Sewage | Mechanical Equipment Failure | Private Pump station automatic operation failed. We are still following up with the property owner to determine the cause. | Staff discovered it when we were doing grease trap inspections. | <50 gallons | visual observation | No | 9122 |  | 2025-02-18 | 03:00 PM | less than 50 gallons | 45 |  | Building owner contacted to repair pump station. Robert Sacks was his name. He manually pumped the station down, and reported to us that the stations automatic operation had been restored by 3:00PM. We will follow up with him on recommended pump replac | Orange | 500 Boston Post Rd, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-02-14 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | 8 INCH ASBESTOS CONCRETE SEWER COLLAPSED DUE TO A SEVERELY COMPROMISED PIPE SECTION. | WE WERE NOTIFIED BY THE HIGHWAY DEPARTMENT SUPERINTENDENT. | LESS THAN 1,000 GALLONS | VISUAL OBSERVATION | No | 9094 |  | 2025-02-14 | 11:00 AM | <1,000 GALLONS | 900 |  | WE DUG UP THE CLOGGED PIPE, REMOVED ROCKS AND REPAIRED THE PIPE. MEETING WITH ORANGE DPW TO DETERMINE BEST COURSE OF ACTION TO REPLACE THAT PIPE ON 2/19/2025 | Orange | Carlson Rd, Orange, CT
ORANGE | Closed | Sewage Bypass | Dry | 2025-02-10 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | THE SEWER MAIN COLLAPSED AT 57 FT TO 70 FT. THE PIPE IS OLD ASBESTOS CEMENT, AND THE BOTTOM HAS WORN OUT OF IT. | Reported by Orange DPW. | Less than 100 gallons | Visual observation | No | 9084 |  | 2025-02-10 | 01:00 PM | ESTIMATED AT LES THAN 500 GALLONS | 450 |  | BRENNAN CONSTUCTION REPAIRED THE FAILED PIPE SECTION. | Orange | Carlson Rd, Orange, CT
[18 empty] | TOTAL VOLUME | 2365

## Plainfield
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
PLAINFIELD NORTH WPCF | Closed | Sewage Bypass | Dry | 2025-08-18 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | resident called in to report issue. | 20-30 gallons | onsite estimation | No | 9801 |  | 2025-08-18 | 10:30AM | 20 gallons | 20 | null | Rodded and flushed line. | Plainfield | 19 Gorman St, Plainfield, CT
PLAINFIELD NORTH WPCF | Closed | Sewage Bypass | Dry | 2025-08-11 | 09:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | WPCA staff driving by location. | 50-100 gallons | onsite estimation | No | 9790 |  | 2025-08-11 | 09:45 AM | 50-100 gallons | 90 | null | sewer line was jetted about 100ft. | Plainfield | 19 Gorman St, Plainfield, CT
PLAINFIELD NORTH WPCF | Closed | Sewage Bypass | Dry | 2025-07-04 | 05:00 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | level control | routine station checks | 500gal | onsite evaluation, trickling out from manhole | Yes | 9691 | Moosup river | 2025-07-04 | 08:15 AM | 500gal | 500 | null | repaired level control | Plainfield | 376 Main St, Plainfield, CT
PLAINFIELD NORTH WPCF | Closed | Sewage Bypass | Dry | 2025-12-27 | 09:00 AM | Treatment Plant | Partially Treated Raw Sewage | Other | operator error | Operator routine inspection | 100-300 gallons | on-site estimation | No | 10221 |  | 2025-12-27 | 11:00 AM | about 300 gallons | 300 | null | thin primary effluent was pumped back to the head of the aeration tanks and thicker sludge was pumped out back to the sludge holding well | Plainfield | 26 Black Hill Rd, Plainfield, CT
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2025-07-27 | 06:30 PM | Treatment Plant | Partially Treated Raw Sewage | Electrical Equipment Failure | Brown out blew motor starter. | Employee reported to work this morning and found it. | 500 gallons or less | Rate from telescope valve | Yes | 9757 | Mill Brook | 2025-07-28 | 04:45 AM | 500 Gallons or less | 500 | null | Replaced motor starters | Plainfield | 100 Birch St, Plainfield, CT
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2025-04-29 | 10:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Rags | rags and wipes were found in the sewer main. | call from a local resident | 25-100 gallons | estimated gallons based on visual inspection. | No | 9427 |  | 2025-04-29 | 12:30 PM | 50 gallons | 50 |  | WPCA used a sewer rodder to clear out the blockage. | Plainfield | 19 Gorman St, Plainfield, CT
PLAINFIELD, TOWN OF | Closed | Sewage Bypass | Dry | 2025-02-19 | 02:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | A blockage was found in sewer main. Some rock and debris was removed. | A plumber called WPCA to investigate sewer blockage | 300-1000 gallons | estimation based on a visual inspection of the manhole | No | 9135 |  | 2025-02-19 | 07:30 PM | 300-1000 gallons | 850 |  | The WPCA used a sewer rodder and a jet truck to break up the blockage. Any large debris found was removed. | Plainfield | 10 Terrace Dr, Plainfield, CT
[18 empty] | TOTAL VOLUME | 2310

## Plymouth
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
PLYMOUTH WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-10-30 | 08:15 PM | Manhole | Raw Sewage | Unknown | null | Called in to On-call operator | Unknown will updateestimated at 1/4 gpm. Less than 50 gallons | estimation of time and flow | Yes | 10082 | Spill did enter catch basin / Eugene Pond | 2025-10-30 | 10:00 PM | less than 50 gallons | 50 | null | cleared with jet truck | Plymouth | 42 Beach Ave, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2025-07-10 | 06:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | Called in to PD | less than 50 gallons | Estimated by operator at less than 0.5 GPM | No | 9705 | Did not reach waterbody | 2025-07-11 | 02:00 AM | less than 200 gallons | 200 | null | Had to hire contractor to jet line | Plymouth | 12 Burr Rd, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2025-04-16 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags |  | called in | less than 50 gallons | Very low flow area, Flow just trickling out of manhole | No | 9394 |  | 2025-04-16 | 11:15 AM | less than 50 gallons | 50 |  | WPCA Operators cleared line with jet truck | Plymouth | 16 Dewey Ave, Plymouth, CT
PLYMOUTH WPCF | Closed | Sewage Bypass | Dry | 2025-01-03 | 08:45 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags | Rags and Grit | On-call operator was called in | Some sewage entered home owners basement.Less than 10 gallons | Was only told sewer entered residents basementReceived pictures from Resident | No | 9012 |  | 2025-01-03 | 10:30 PM | less than 10 gallons | 10 |  | Plymouth WPCA staff jetted and cleared blockage. Contractor scheduled to clean and vac lines Friday 1/10/2025 | Plymouth | 11 Dewey Ave, Plymouth, CT
[18 empty] | TOTAL VOLUME | 310

## Ridgefield
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
RIDGEFIELD, TOWN OF (MAIN) | Closed | Sewage Bypass | Dry | 2025-03-06 | 11:00 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Pump Station force main was found to have a hole in the 8-inch force main. | The force main break was called into us by homeowner. | We are estimating approximately 2000 to 3000 gallons. | Visual estimate, upon finding the broken force main we shut down the pump station. | Yes | 9216 | Great Swamp/Ridgefield Brook | 2025-03-06 | 11:30 AM | Approximately 2000 - 3000 gallons | 2500 |  | Pump Station was shut down. Local contractor located the broken force main and made repairs to the pipe. | Ridgefield | 30 Island Hill Ave, Ridgefield, CT
[18 empty] | TOTAL VOLUME | 2500

## Seymour
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | How was Final Volume Determined | How incident was resolved | Municipality | Address
SEYMOUR WPCF, TOWN OF | Open | Sewage Bypass | Dry | 2025-10-08 | 01:00 PM | Treatment Plant | Sludge Spill | Other | Today We cleaned a siphon, we disposed the rags and debris at the dumpster located at the wastewater plant headwork. However the dumpster got full and some liquid runoff to the ground then slowly got into on of the small creek or may me is just a ditch n | As soon the dumpster got overfilled, and wastewater was running out of the dumpster, at this time operator notice it. | About 500 ml.. see pictures | Just visualize and from runoff until it got stopped. | No | 9991 | Dont know it is a very small creek outside the wastewater plant. Does not have a name, it may be just a ditch. | [5 empty] | Seymour | 723 Derby Ave, Seymour, CT

## Shelton
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SHELTON | Closed | Sewage Bypass | Dry | 2025-03-13 | 04:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | Also blockage with grease, rags, and roots. | Resident called with potential back-up. Could not flush toilet. No overflow into house. | 0 gallons | No actual overflow. | No | 9228 | N/A | 2025-03-14 | 04:30 PM | 0 - blockage in main was cleared of all debris | 0 |  | Televised, jetted, vacuumed, all debris, grease, rags, roots cleared. | Shelton | 159 Division Ave, Shelton, CT
SHELTON | Closed | Sewage Bypass | Dry | 2025-03-13 | 10:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Grease |  | Resident called. | 200 gallons | Visual | No | 9226 | N/A | 2025-03-13 | 04:00 PM | 250 gallons | 250 |  | Main line jetted. Grease removed. | Shelton | 11 Meadow St, Shelton, CT
SHELTON | Closed | Sewage Bypass | Snowmelt | 2025-02-14 | 11:00 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) |  | UI utility observed bubbling in easement and notified Sewer department. | 400 gallons | Visual | No | 9123 | N/A | 2025-02-15 | 02:00 PM | 500 | 500 |  | Vac truck on site and main line jetted. | Shelton | 275 Riverview Ave, Shelton, CT
[18 empty] | TOTAL VOLUME | 750

## Simsbury
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2025-05-10 | 12:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Other | Siphon restricted with debris | HOA President called about multiple basement backing up | Less than 500 gallons | Visual estimation by operator | Yes | 9518 | Farmington River | 2025-05-10 | 03:30 PM | 900 gallons | 900 |  | jetted syphon to clear restricted pipe | Simsbury | 32 White Water Turn, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-09 | 07:15 PM | Basement | Raw Sewage | Excessive Flows - Storm Event | Main line at capacity flowing through syphon | Homeowner called in | 250 gallons | estimated by amount of water on floor | No | 9517 |  | 2025-05-09 | 08:15 PM | 250 gallons | 250 |  | Rain event ended | Simsbury | 38 White Water Turn, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2025-05-01 | 12:00 PM | Select... | Raw Sewage | Other | Influent bar screen was impacted by rags from septage haulers which created a back up into the dewatering room drain. water exited the dewatering room onto pavement area. | Operator rounds | 25 gallons | area covered | No | 9431 |  | 2025-05-01 | 12:15 PM | 25 gallons | 25 |  | placed influent bar screens in hand to remove debris that was restricting flow. | Simsbury | 36 Drake Hill Rd, Simsbury, CT
SIMSBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-06 | 11:00 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Rags |  | Resident reported | 15 gallons | estimated by on material on ground | No | 9017 |  | 2025-01-06 | 11:15 AM | 15 Gallons | 15 |  | Vacuumed manhole and jetted lateral, disinfected area | Simsbury | 933 Hopmeadow St, Simsbury, CT
[18 empty] | TOTAL VOLUME | 1190

## South Windsor
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SOUTH WINDSOR | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-10-13 | 10:30AM | Sewer Main | Raw Sewage | Other | Excessive flow caused by CT Water flushing hydrants into the sanitary sewer* No bypass this was a CT Water manhole | Parks employee called in for manhole cover off of frame | 0 | We determined the water that was coming out of the CT Water manhole was flushing water not sewage | No | 10016 |  | 2025-10-13 | 10:30AM | Zero gallons | 0 | null | Discovered this was a CT Water manhole | South Windsor | 178 Foster St, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2025-08-14 | 07:30 AM | Treatment Plant | Fully treated raw sewage except disinfection | Mechanical Equipment Failure | null | We were there when it happened | 777 gallons | We lost UV for 1 minute at 1.19 mgd which is equal to 777 gpm | Yes | 9794 | Connecticut River | 2025-08-14 | 07:30 AM | 777 gallons | 777 | null | Turned other bank on | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2025-06-30 | 11:45 AM' | Treatment Plant | Fully treated raw sewage except disinfection | Other | Power outage | I knew as soon as we lost power | Approximately 1100 gallons | Based on flow rate at the time of the power loss | Yes | 9682 | Connecticut River | 2025-06-30 | 01:15 PM | Around 1100 gallons | 1100 | null | Generator power kicked on, commercial power restored by 1:15 pm | South Windsor | 1 Vibert Rd, South Windsor, CT
SOUTH WINDSOR | Closed | Sewage Bypass | Dry | 2025-06-05 | 09:30 AM | Treatment Plant | Fully treated raw sewage except disinfection | Electrical Equipment Failure | null | Operators who were resetting the PLC noted that the UV lamps all turned off for about 15 seconds | 520 gallons | By looking at flow data in correlation with the amount of time the UV was down | Yes | 9625 | Connecticut River | 2025-06-05 | 09:30 AM | 520 gallons | 520 | null | Lamps relit on their own after 15 seconds | South Windsor | 1 Vibert Rd, South Windsor, CT
[18 empty] | TOTAL VOLUME | 2397

## Southbury
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Dry | 2025-09-11 | 01:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | null | A resident saw sewage coming out of a manhole in a parking lot | 2 to 5 gallons a minute. | Visual estimate | No | 9916 | null | 2025-09-11 | 02:15 PM | 200 to 300 gallons. | 250 | null | Jetted line and used vacuum truck to clean area. | Southbury | 450 Heritage Rd, Southbury, CT
HERITAGE VILLAGE COMPANY | Closed | Sewage Bypass | Dry | 2025-05-27 | 09:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Residents of that area dump grease down the drain into the septic system. This caused a partial blockage of the main sewer line. | Resident sent an email to DEEP and DEEP contacted CT Water. | 20 to 50 gallons per hour | Visual estimation. | Yes | 9594 | Tributary to the Pomperaug River. | 2025-05-27 | 10:45 AM | Between 50 to 75 gallons from the time that the call came in. To when it was cleared. The resident that reported the SSO said that it has been overflowing for four days. | 1920 | null | The main line was jetted to clear the blockage. | Southbury | 339 Grove Pond Ln, Southbury, CT
[18 empty] | TOTAL VOLUME | 2170

## Southington
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2025-06-25 | 12:45 PM | Basement | Raw Sewage | Sewage Line Blockage - Rags |  | Resident at 115 Howard Avenue noticed water in their basement. | 25 gallons | Estimated | No | 9679 |  | 2025-06-25 | 02:30 PM | 25 gallons | 25 | null | Southington WPC staff jetted the line to relieve the blockage. | Southington | 115 Howard Ave, Southington, CT
SOUTHINGTON | Closed | Sewage Bypass | Dry | 2025-02-01 | 04:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure |  | Town of Southington WPC staff noticed a surcharged manhole. Town of Southington WPC staff began jetting the sewer main to relieve the blockage, but ran into an unusual amount of rocks, gravel, and dirt. | 2 gallons | Estimate | No | 9068 |  | 2025-02-01 | 05:00 PM | 2 gallons | 2 |  | Section of broken pipe was replaced by contractors. | Southington | 868 Meriden-Waterbury Turnpike, Southington, CT
[18 empty] | TOTAL VOLUME | 27

## Stafford
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
STAFFORD | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-03-06 | 04:00 AM | Treatment Plant | Fully treated raw sewage except disinfection | Mechanical Equipment Failure | RAS pump failure caused by power loss. | Start of shift at 6:30 am | 10,000 gallons | calculation of flow | Yes | 9180 | Willimantic River | 2025-03-06 | 07:00 AM | 10,000 gallons | 10000 |  | Power returned to RAS pumps, polymer add to tanks for faster settling. | Stafford | 50 River Rd, Stafford, CT
[18 empty] | TOTAL VOLUME | 10000

## Stamford
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
STAMFORD | Closed | Sewage Bypass | Dry | 2025-10-20 | 08:30 AM | Sewer Main | Raw Sewage | Other | Sewer line was surcharged and leak occurred via open sewer line joint. | WPCA staff were conducting routine flow inspections and observed the surface discharge. | 5-gallons | Wetted area was estimated. | No | 10039 | null | 2025-10-20 | 08:45 AM | 5 gallons | 5 | Wetted area was estimated. | WPCA's contractor had to repair damaged sanitary sewer line caused by other contractor working on stormwater infrastructure. | Stamford | 75 W Broad St, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2025-09-10 | 02:15 PM | Treatment Plant | Fully treated raw sewage except disinfection | Other | Power Failure | Arching on pole outside plant | 7,291 | Flow rate at the time of power failure multiplied by time it took UV disinfection to come back on line. | Yes | 9914 | Stamford Harbor, East Branch | 2025-09-10 | 02:15 PM | 7291gallons | 7291 | null | Emergency generation | Stamford | 111 Harbor View Ave, Stamford, CT
STAMFORD | Closed | Sewage Bypass | Dry | 2025-02-10 | 09:00 AM | Pump Station | Raw Sewage | Mechanical Equipment Failure | Force main break. | Another agency reported the incident. | Approximately, 300 gals. | Volume was determined based on pump capacity and run-time. | No | 9083 | Unknown at this point in time. | 2025-02-10 | 09:30 AM | Approximately, 300 gals. | 300 |  | Crews are responding to contain wastewater, while contractor has mobilized to begin the repair work. | Stamford | 110 Burwood Ave, Stamford, CT
[18 empty] | TOTAL VOLUME | 7596

## Stonington
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
STONINGTON-PAWCATUCK WPCF | Open | Sewage Bypass | Dry | 2025-06-09 | 01:15 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Other | null | Passer by called it in. | <10 gallons | Estimated from observance | No | 9639 |  | 2025-06-09 | 03:00:00 PM | <10 Gallons | 9 | Estimated from observance | Leak was repaired | Stonington | Mary Hall Rd, Stonington, CT
[18 empty] | TOTAL VOLUME | 9

## Suffield
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
SUFFIELD | Closed | Sewage Bypass | Dry | 2025-08-10 | 02:00 PM | Manhole | Raw Sewage | Mechanical Equipment Failure | The force main air release valve was leaking | Calls were reported about water in the road | 5 gallons per minute or less for approximately 2.5 hours, 750 gallons or less. | visual estimate of it bubbling up through a hole in the manhole cover. | Yes | 9788 | Rawlins brook. The overflow went into a catch basin and storm pipes that ultimately lead to Rawlins brook. The storm sewer outfall was checked but no obvious discharge was noticed going into the brook (picture) | 2025-08-10 | 04:30 PM | 750 gallons | 750 | null | The air release valve was able to be shut off and isolated. | Suffield | 703 East Street N, Suffield, CT
[18 empty] | TOTAL VOLUME | 750

## Thomaston
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
THOMASTON WPCF | Closed | Sewage Bypass | Dry | 2025-09-18 | 12:00 PM | Pump Station | Raw Sewage | Sewage Line Break, Crack or Failure | Broken force main | leak in road called in by public works dept. | 500 gallons | pump rates | No | 9928 | null | 2025-09-18 | 06:30 PM | 500 gallons | 500 | null | broken force main was repaired | Thomaston | 95 Kennedy Dr, Thomaston, CT
[18 empty] | TOTAL VOLUME | 500

## Tolland
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
TOLLAND | Closed | Sewage Bypass | Snowmelt | 2025-02-03 | 02:15 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Coupler on force main failed causing the leak | Public Works employees called Director to notify him of "water" in the road. | Undetermined | Undetermined | Yes | 9073 | Paulk Hill Brook We're not sure how much, if any, made it to the brook after it ran off into the abutting grass, wood line areas. There was significant snow melt occurring during the day, so there was already running water in the gutters / edge of roadwa | 2025-02-03 | 04:15 PM | Bypass pumping was discharged back into our system down flow from where the issue had taken place. Captured effluent from immediate work area was hauled away by septic hauler. | 200 |  | Removed broken clamps, cut out 2' section of ductile iron pipe and installed two new 6" lug coupling clamps | Tolland | 111 Old Post Rd, Tolland, CT
[18 empty] | TOTAL VOLUME | 200

## Torrington
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
TORRINGTON WPCF | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-05-06 | 12:15 PM | Sewer Main | Raw Sewage | Unknown | cause of blockage unknown. cleared with vactor rather easily | homeowner noticed sewage coming from manhole cover in sidewalk | 40 gallons per min | estimated visually | No | 9477 | null | 2025-05-06 | 12:45 PM | 1800 gal. | 1800 | null | cleared blockage with jetter truck | Torrington | 991 E Main St, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2025-03-07 | 06:30 AM | Manhole | Raw Sewage | Unknown | null | call from public, that manhole was overflowing | 10gph | estimated | No | 9195 | null | 2025-03-07 | 02:45:00 PM | 500 | 500 | visual estimated | Jet vac truck | Torrington | 140 Main St, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2025-03-02 | 03:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | unknown probably rag buildup | private person noticed it | 2 gallons per minute | visual estimation | Yes | 9151 | troy brook | 2025-03-02 | 04:00 PM | 300 gallons | 300 | estimated | jetted to clear blockage | Torrington | 200 Kennedy Dr, Torrington, CT
TORRINGTON WPCF | Closed | Sewage Bypass | Dry | 2025-02-25 | 12:45 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Rags | null | We received a call from the public | quantity unknown. rate estimated 5 gallons per minute | guestimate by visual observation | Yes | 9143 | gulfstream | 2025-02-25 | 04:45 PM | 500 gal | 500 | estimated | jet vac truck | Torrington | 1143 New Litchfield St, Torrington, CT
[18 empty] | TOTAL VOLUME | 3100

## Trumbull
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
TRUMBULL | Closed | Sewage Bypass | Dry | 2025-10-09 | 11:30 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Forcemain failure | Drive by inspection by WPCA employee | 3 gallons per hour | Visual of the leak and associated puddling. | No | 9994 | null | 2025-10-09 | 06:00 PM | less than 50 gallons | 45 | flow vs volume | repairs were made to the forcemanin | Trumbull | 6528 Main St, Trumbull, CT
TRUMBULL | Closed | Sewage Bypass | Dry | 2025-05-27 | 10:45 AM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Unknown reason for failure at this time | Resident notification by phone | 1 gallon an hour +- | Visually estimated the flow | No | 9593 | null | 2025-05-27 | 18:15 | Final volume was approx 15 gallons. All the residual was collected and pumped into the adjacent sewer main. | 50 | distance of runoff vs the approximate volume of flow originating from the ground | The system was shut down and switched to the secondary bypass forcemain. Contrators excated and replaced a section of the affected pipe. | Trumbull | 6466 Main St, Trumbull, CT
[18 empty] | TOTAL VOLUME | 95

## Waterbury
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-19 | 03:15 PM | Manhole | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | debris found in manhole | Water Department contacted Jacobs | 1,250 gallons | SSO calculator | Yes | 9042 | Beaver Brook | 2025-01-19 | 03:45 PM | 1,250 gallons | 1250 |  | A jetter truck Released the blockage and regained normal flow. | Waterbury | 106 Arline Dr, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-07-25 | 07:45 AM | Pump Station | Raw Sewage | Electrical Equipment Failure | UPS failure | SCADA system alarm | 25 gallons | Visual using SSO calculator | No | 9749 | null | 2025-07-25 | 08:00 PM | 25 gallons | 25 | null | Backup float put in manual | Waterbury | 46 Terrell Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-04-22 | 01:15 PM | Basement | Raw Sewage | Sewage Line Blockage - Roots | CCTV camerawork determined that roots were the cause of the blockage in the city line | Qalert system | Jacobs estimates 30 gallons | Visual | No | 9401 |  | 2025-04-22 | 02:15 PM | 30 gallons | 30 |  | A jetter truck was dispatched to clear the blockage. Also added to the maintenance plain to root cut once per year. | Waterbury | 89 Clowes Terrace, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-02 | 11:15 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease |  | Jacobs field crew during daily maintenance in city noticed the surging manhole. | 50 gallons | Visual | Yes | 9002 | Mad river interceptor | 2025-01-02 | 11:45 AM' | 50 gallons | 50 |  | Jacobs WPC cleared blockage | Waterbury | 174 Orange St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-05-25 | 11:45 AM' | Manhole | Raw Sewage | Unknown | Blockage at the manhole | Water Dept employee noticed the manhole discharging | 750 gallons | Sewer manhole overflow chart. 50 gpm X 15 minutes = 750 gallons | Yes | 9591 | Mad river | 2025-05-25 | 12:00 PM | 750 gallons | 750 | null | Jetter truck released blockage and flow returned to normal. | Waterbury | 418 Pine St, Waterbury, CT
[18 empty] | TOTAL VOLUME | 2105
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY'S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-06-09 | 11:00 AM | Lateral - Private | Raw Sewage | Other | blockage in private lateral/curb box | tenant called customer service | 5 gallons | Visually | No | 9640 | N/A | 2025-06-10 | 06:00 PM | DHP estimates 50 gallons |  | null | • Case was assigned to Inspector Wood on 06/09/2025.• Inspector Wood spoke with the landlord on 06/09/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 06/10/2025, the re-inspection was conducted and | Waterbury | 126 Cherry St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-08-09 | 06:15 AM | Lateral - Private | Raw Sewage | Unknown | Unknown | WTB police Dept contacted manager | 35 gallons | Visual | No | 9787 | N/A | 2025-08-11 | 11:00 AM | DPH estimated 75 gallons |  | null | • Case was assigned to Inspector Wood on 08/09/2025.• Inspector Wood spoke with the landlord on 08/09/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 08/11/2025, the re-inspection was conducted and | Waterbury | 225 Bishop St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-06 | 08:15 AM | Lateral - Private | Raw Sewage | Other | Blockage in private lateral | Field crew | 20 gallons | Visual by field crew | Yes | 9015 | Mad River interceptor | 2025-01-07 | 03:00 PM | DPH reports 15 gallons |  |  | • Case was assigned to Inspector Manuel on 01/06/2025.• Inspector Manuel spoke with the landlord on 01/06/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 01/07/2025, the re-inspection was conducted | Waterbury | 376 Walnut St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-08 | 09:45 AM | Lateral - Private | Raw Sewage | Other | Unknown. This is a private lateral issue | Qalert system | 25 gallons | Visual by field tech | No | 9021 | N/A | 2025-01-09 | 03:00 PM | DPH reports 50 gallons |  |  | • Case was assigned to Inspector Watson on 01/07/2025.• Inspector Watson spoke with the landlord on 01/07/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 01/09/2025, the re-inspection was conducted | Waterbury | 603 N Main St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-21 | 01:45 PM | Lateral - Private | Raw Sewage | Other | Unknown | Qalert system | 10-15 gallons | Visual | No | 9046 |  | 2025-01-27 | 12:00 PM | DPH reports total quantity to be 75 gallons |  |  | • Case is assigned to Inspector Simoes on 01/21/2025.• Inspector Simoes got in touch with the landlord on 01/23/25. The landlord stated that he would have the blockage abated. • On 01/27/2025, the re-inspection was conducted and the sewage backup wa | Waterbury | 38 High St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-01-24 | 10:45 AM | Lateral - Private | Raw Sewage | Unknown | This is a septic system failer at 156 Perkins Ave | Call from the Water Dept. | 75 gallons | Visual | No | 9051 |  | 2025-01-28 | 03:00 PM | DPH reports 50 gallons |  |  | • Case was assigned to Inspector Eddy on 01/24/2025.• Inspector Eddy spoke with the landlord on 01/24/2025 and the landlord stated that he would have Wolcott Sanitation pump out the septic tank and address any issues.• On 01/28/2025, the re-inspecti | Waterbury | 156 Perkins Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-02-01 | 05:30 PM | Lateral - Private | Raw Sewage | Unknown | Unknown | WTB fire Dept contacted Jacobs | 30 gallons | visual | No | 9069 |  | 2025-02-11 | 03:00 PM | DPH reports the final quantity to be 40 gallons |  |  | • Case was assigned to Inspector Eddy on 02/1/2025.• Inspector Eddy issued a Notice of Violation on 02/3/2025• On 2/7/25 Inspector Eddy spoke to the property owner and he stated that he would abate the sewage backup. • On 02/11/2025, the re-inspec | Waterbury | 84 Fairview St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-03 | 02:15 PM | Lateral - Private | Raw Sewage | Unknown |  | A Passerby called in | 15 gallons | Visual | No | 9152 | N/A | 2025-03-07 | 08:00 AM | DPH reports 50 gallons |  |  | • Case was assigned to Inspector Manuel on 03/03/2025.• Inspector Manuel spoke with the landlord on 03/03/2025 and the landlord stated that he would have the blockage abated and cleaned. • On 03/12/2025, the re-inspection was conducted and the sewag | Waterbury | 603 N Main St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-12 | 09:30 AM | Lateral - Private | Raw Sewage | Unknown | This is a private by-pass | Field crew notice while doing CBYD | 100 gallons | visual | Yes | 9220 | Naugatuck river | 2025-03-13 | 09:30 AM | DPH reports 150 gallons |  |  | • Case was assigned to Inspector Tom Watson on 03/12/2025.• Inspector Tom Watson spoke with the property management on 03/12/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 03/13/2025, the re-inspec | Waterbury | 31 Nottingham Terrace, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-20 | 09:30 AM | Lateral - Private | Raw Sewage | Unknown | Blockage | Qalert system | 10-15 gallons | Visual | No | 9262 |  | 2025-03-25 | 03:30 PM | DPH reports 20 gallons |  |  | • Case was assigned to Inspector Manuel on 03/20/2025.• Inspector Manuel spoke with the Tenants on 03/20/2025 and the Tenant stated that he would have the blockage abated and cleaned. • On 03/25/2025, the re-inspection was conducted and the sewage b | Waterbury | 228 Wood St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-03-26 | 06:15 PM | Lateral - Private | Raw Sewage | Other | Blockage in Private lateral | Qalert system | 40 gallons | Visual | Yes | 9297 | Mack Brook | 2025-03-30 | 02:30 PM | DPH estimates the final quantity to be 60 gallons |  |  | • Case was assigned to Inspector Nelson Simoes on 03/28/2025.• Inspector Nelson Simoes spoke with the landlord on 03/28/2025 and the landlord stated that he would have the blockage abated and cleaned. • On 03/30/2025, the re-inspection was conducted | Waterbury | 543 Chase Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-04-10 | 02:15 PM | Lateral - Private | Raw Sewage | Other | potential blockage in private manhole | Resident called customer service | 40 gallons | visually | Yes | 9360 | Mad river interceptor | 2025-04-14 | 05:45 AM | DPH reports 50 gallons |  |  | • Case was assigned to Inspector Eddy on 04/10/2025.• Inspector Eddy spoke with the Property Manager on 04/10/2025 and he stated that he would have the blockage abated and cleaned. • On 04/14/2025, the re-inspection was conducted and the sewage back | Waterbury | 950 Wolcott St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-04-11 | 12:15 PM | Lateral - Private | Raw Sewage | Sewage Line Break, Crack or Failure | private lateral is compromised | Health Department reported the issue | 30 gallons | Visually of affected area | No | 9361 | N/A | 2025-04-14 | 10:30AM | DPH reports 60 gallons |  |  | Remediation Action: • Case was assigned to Inspector Eddy on 04/11/2025.• Inspector Eddy spoke with the landlord on 04/11/2025 and the landlord did stop the flow by putting the plug back in the lateral pipe. Landlord is in the process of finding out | Waterbury | 567 S Leonard St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-07-14 | 02:00 PM | Lateral - Private | Raw Sewage | Other | Septic system failure | Resident called customer service | 30-40 gallons | Visually | No | 9714 | null | 2025-07-16 | 03:00 PM | DPH reports 50 gallons |  | null | • Case was assigned to Inspector Watson on 07/14/2025.• Inspector Watson spoke with the landlord on 07/14/2025 and the landlord stated that he would have a sanitation company to pump out the septic tank and address any issues.• On 07/16/2025, the re | Waterbury | 363 Berkeley Ave, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-07-17 | 12:30 PM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | Qalert system | 20 Gallons | Visual by DPH | Yes | 9723 | Mad river | 2025-07-19 | 03:00 PM | DPH Reports 50 gallons |  | null | • Case was assigned to Inspector Ortiz on 07/17/2025.• Inspector Ortiz spoke with the landlord on 07/17/2025 and the landlord stated that he would have a sanitation company to pump out the septic tank and address any issues.• On 07/19/2025, the re-i | Waterbury | 484 Waterville St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-09-04 | 02:15 PM | Lateral - Private | Raw Sewage | Unknown | Not known. DPH to monitor | Qalert system | 30 gallons | Visual | Yes | 9854 | Naugatuck river | 2025-09-08 | 10:00 AM | DPH reports 75 Gallons |  | null | • Case was assigned to Inspector Simoes on 09/04/2025.• Inspector Simoes spoke with the landlord on 09/04/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 09/08/2025, the re-inspection was conducted | Waterbury | 727 Baldwin St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-10-06 | 12:30 PM | Lateral - Private | Raw Sewage | Unknown | Unknown Private lateral | Qalert system | 15 gallons | Visual | No | 9971 | N/A | 2025-10-10 | 06:00 PM | DPH reports 100 gallons |  | null | • Case was assigned to Inspector Simoes on 10/06/2025.• Inspector Simoes spoke with the landlord on 10/06/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • 10/09/2025 Landlord stopped accepting my calls | Waterbury | 54 Niagara St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-10-29 | 11:15 AM | Lateral - Private | Raw Sewage | Unknown | This is a private curb box | Qalert system | 5-10 gallons | Visual | No | 10061 | N/A | 2025-10-31 | 09:00 AM | DPH reports 50 gallons as the final quantity |  | null | • Case was assigned to Inspector Wood on 10/29/2025.• Inspector Wood spoke with the landlord on 10/29/2025 and the landlord stated that he would have the blockage abated and cleaned with in 24hr. • On 10/31/2025, the re-inspection was conducted and | Waterbury | 319 Cooke St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-10-31 | 05:15 PM | Lateral - Private | Raw Sewage | Other | Blockage in private lateral | Qalert system | 20-30 gallons | visual | Yes | 10092 | Naugatuck river | 2025-11-04 | 10:00 AM | DPH reports 40 gallons |  | null | • Case was assigned to Inspector Eddy on 10/31/2025.• Inspector Eddy spoke with the landlord on 11/1/2025 and the landlord stated that he would have the blockage abated and cleaned • On 11/4/2025, the re-inspection was conducted and the sewage backu | Waterbury | 52 Washington St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-11-18 | 09:30 AM | Lateral - Private | Raw Sewage | Other | Blockage in a private curb box | DPH received a call | 50-60 gallons | Visual | Yes | 10131 | Naugatuck River | 2025-11-22 | 01:30 PM | DPH reports 75 gallons |  | null | • Case was assigned to Inspector Eddy on 11/18/2025.• Inspector Eddy spoke with the landlord on 11/18/2025 and the landlord stated that he would have the blockage abated and cleaned • On 11/22/2025, the re-inspection was conducted and the sewage bac | Waterbury | 82-84 Fairview St, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-12-07 | 10:45 AM | Lateral - Private | Raw Sewage | Sewage Line Blockage - Other | Unknown | Street Dept. contacted Ric | 187 Gallons | Puddle calculator 100ft X 1ft X .25 = 187 gallons | No | 10177 | Beaver Pond Brook | 2025-12-09 | 11:15 AM | DPH 187 gallons |  | null | • Case was assigned to Inspector Wood on 12/07/2025. • On 12/07/2025, an inspection was conducted and the sewage backup was cleared and abated.• Inspector Wood spoke to Property Manager of the Home Association and informed them to maintain private s | Waterbury | 168 Mulloy Rd, Waterbury, CT
WATERBURY WPCF | Closed | Sewage Bypass | Dry | 2025-07-17 | 12:15 PM | Lateral - Private | Raw Sewage | Other | Curb box blockage | Qalert system | 20 | Visual | Yes | 9743 | Mad River | 2025-07-21 | 03:00 PM | 55 gallons |  | null | Remediation Action: • Case was assigned to Inspector Watson on 07/17/2025.• Inspector Watson spoke with the landlord on 07/17/2025 and the landlord stated that he would have the blockage abated and cleaned. • On 07/21/2025, the re-inspection was con | Waterbury | 285 Cooke St, Waterbury, CT

## Waterford
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WATERFORD | Closed | Sewage Bypass | Dry | 2025-08-23 | 08:00 PM | Sewer Main | Raw Sewage | Sewage Line Break, Crack or Failure | Crack in 45 elbow | Surface water | Less than 100 gallons | Visual inspection | No | 9833 | null | 2025-08-25 | 05:00 PM | Approximately 100 gallons | 100 | null | Cracked 45 was removed and replaced by contractor | Waterford | 253A Shore Rd, Waterford, CT
[18 empty] | TOTAL VOLUME | 100

## West Haven
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-11-25 | 09:30 AM | Manhole | Raw Sewage | Sewage Line Break, Crack or Failure | line upstream collapsed causing mh# 13-193 to bypass during peak flow times. | called in from dpw | approx 30 to 50 gallons intermittently during peak flow times | visual inspection | Yes | 10154 | drainage is upstream from west river | 2025-12-24 | 07:00:00 AM | approx. 50 to 75 gallons | 65 | visual inspections and reported info from on site workers | pipe was repaired and lined | West Haven | 4 Spring St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain 1-2" per hour | 2025-09-25 | 04:00 AM | Manhole | Raw Sewage | Mechanical Equipment Failure | main pumping station had excessive flow from rain | alarm system high well alert | approx 100 gallons | visual inspection | Yes | 9947 | old field creek | 2025-09-25 | 05:15 AM | approx 100 gallons | 100 | null | station came back into control when flows slowed down | West Haven | 98 Blohm St, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2025-09-15 | 11:00 AM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | Grease blockage | Property owner | 50 gallons | Visual | No | 9921 | null | 2025-09-15 | 12:00 PM | 50 gallons | 50 | null | Jetted blockage and vacumed out debris | West Haven | 20 Industry Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2025-08-22 | 10:00 AM | Manhole | Raw Sewage | Other | Contractor used flow through plug to work on manhole lining and surcharged the main | Homeowner called in | 100 gallons | Visual | Yes | 9831 | Lake phipps, to cover river | 2025-08-22 | 10:30AM | 100 gallons | 100 | null | Pulled contractor off project released his flow.through plug | West Haven | 21 Phipps Dr, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-05-31 | 12:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | grease blockage in sanitary main | property manager | 150 gallons | visual inspection | No | 9620 | null | 2025-05-31 | 01:00 PM | 150 gallons | 150 | null | jetted grease blockage | West Haven | 282 Terrace Ave, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Rain less than 1" per hour | 2025-03-17 | 08:30 AM | Basement | Raw Sewage | Sewage Line Blockage - Grease |  | by phone from customer (Shala Lindsay) | 100 gal | Visually | No | 9249 |  | 2025-03-17 | 09:00 AM | 100 gal | 100 |  | AMH 2-54 was unplugged w/ Vacall truck. Service Master was called for basement cleanup. | West Haven | 23 Batt Ln, West Haven, CT
WEST HAVEN | Closed | Sewage Bypass | Dry | 2025-01-17 | 02:30 PM | Manhole | Raw Sewage | Sewage Line Blockage - Grease | heavy grease and property owners do not do maintenance on a routine basis | resident | 80 gallons | visual | Yes | 9041 | possibly made it to waterbody this storm drainage system makes it way to cove river at some point downstream | 2025-01-17 | 08:00 PM | 80 gallons | 80 |  | jetted the private main and vacuumed out debris ,washed down street while vacuuming cleanup | West Haven | 23 Treat St, West Haven, CT
[18 empty] | TOTAL VOLUME | 645
PRIVATE LATERAL BYPASSES NOT CAUSED BY THE MUNICIPALITY'S SEWER MAIN ARE NOT REQUIRED TO BE REPORTED TO DEEP AND THUS ARE NOT COUNTED AS BYPASSES IN THE REPORT
They are included here to show that they were reported in good faith.
WEST HAVEN | Closed | Sewage Bypass | Dry | 2025-11-07 | 09:00 AM | Lateral - Private | Raw Sewage | Unknown | null | property owner called in a backup , but blockage is in the private system | 50 gallons | visual inspection | Yes | 10112 | cove river | 2025-11-07 | 11:00 AM | 50 to 60 gallons | 55 | null | property owner had plumber jet the blockage | West Haven | 125 Coleman St, West Haven, CT

## Windsor Locks
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WINDSOR LOCKS WPCF | Closed | Sewage Bypass | Dry | 2025-10-21 | 01:00 PM | Sewer Main | Raw Sewage | Sewage Line Blockage - Debris (bricks, etc) | null | Property owner where the Sewer main is located discovered a shifted manhole riser. | approx. 3600 | Volume of VAC Truck debris body. | No | 10049 | null | 2025-10-21 | 03:00 PM | Approx. 3600 gal | 3600 | null | Blockage clearedSSO cleaned by VAC truckMH/ riser repaired | Windsor Locks | 500 North St, Windsor Locks, CT
[18 empty] | TOTAL VOLUME | 3600

## Woodbury
Reporting Utility | Status | Incident Type | Weather Conditions | Date Bypass Began or was Discovered | Event Start Time | Location of Bypass | Type of Bypass | Cause of Bypass | Cause of Bypass Other Explanation | How was Incident Discovered | Estimated Quantity or Rate of Discharge | How was estimated Quantity or Rate Determined | Reach Waterbody | Request ID | Waterbody Name | Date Bypass Ended | Event End Time | Final Quantity | Final Volume Converted for counting | How was Final Volume Determined | How incident was resolved | Municipality | Address
WODDLAKE TAX DISTRICT | Closed | Sewage Bypass | Dry | 2025-03-21 | 09:30 AM | Sewer Main | Raw Sewage | Sewage Line Blockage - Roots |  | Treatment plant operator Joe Barrios arrived at the plant earlier than scheduled today at approximately 9:30am. He noticed wastewater flowing down the hill from behind the sewage treatment plant. He notified Woodlake Tax District maintenance office, and t | See below | See below | Yes | 9275 | Radey Pond | 2025-03-21 | 10:00 AM | 30000 | 30000 |  | The pipe clogged at the manhole invert at the final manhole before entering the sewage treatment plant occurred. Estimated as a 30,000 Gallon release that started approximately at noon on Thursday 03/20/25. During the clog over the past ~20 hours, a disch | Woodbury | 57 Clubhouse Dr, Woodbury, CT
[18 empty] | TOTAL VOLUME | 30000