CONNECTICUT DISTRIBUTED GENERATION TECHNICAL WORKING GROUP

Meeting Minutes

Tuesday, June 22, 2021

9:00 AM – 12:00 PM

9:00 AM – 9:05 AM		Introduction and Adoption of Meeting Minutes

Attendees:

- Andy Mayshar, Con Ed Clean Energy Business

- Jean-Paul LaMarche, Clean Focus (Greenskies)

- Carl Nowiszewski, Eversource

- David A Ferrante, Eversource

- Mark Kirschbaum, UI

- Joseph Folz, UI

- Joseph Marranca, UI

- Brad Marszalkowski, ISO NE

- Russell King, CIEC

- Joseph Debs, Eversource

- Elder Romero, UI

- Tim Young

- Erik Anderson

- Steve Broyer

- Michael DiPanfilo

- Rodney Galton

- Mike Trahan

- Chris Lobdell

- Ion Balan

- Brian Murtha

Facilitators:

- Zak Alexander, PURA, Zachary.Alexander@ct.gov

- Lauren Bergman, PURA, Lauren.Bergman@ct.gov

9:05 AM – 9:45 AM 	EDC Presentations on Screens

- Joint Eversource/UI Presentation

- First Screen – compare transformer rating to generating capacity

  - Fail if transformer cannot handle additional load

- Second Screen – shared secondary, not to exceed 20 kVA

  - Usually fail due to long distance

- Third Screen – not to exceed 4 kW for single phase inverter connection

- Fourth Screen – load flow analysis, not to exceed +/- 5% of voltage

  - Was changed from 3% to 5%

- For distance issue, Eversource and UI still working on screen

  - Depends on type of cable

  - Higher voltage needed for longer distances

  - Usually an issue in rural areas

  - Helpful to have information from developers on distance from DER to road

- Looking to simplify screens for DERs 25-200 kW

  - Using hosting capacity maps

- Hosting capacity based on load flow, does not include short circuit analysis

- For >200 kW, automation is more difficult, impact study required

- New Screen – time domain study

  - Flag risk of islanding and transient over voltage

- When screens fail, change inverter settings or use surge arrestor

- Many transformers are 25K

  - Seek to align DER with transformers

- Outstanding Questions

  - What to do if project fails screens? What upgrades are needed?

  - What are costs and needs for funding? Ratepayer dollars or application fees?

9:45 AM – 10:30 AM	Follow Up on IEEE-1547 2018 and MA Adoption

- MA report has 1547 interim guidelines, developed with ISO-NE

  - Contains ride through settings

- Need to specify types of inverters needed

  - Waiting on inverter manufacturers for certification

- Eversource ready to adopt MA document as is

- UI still reviewing document

- Once document is finalized, resume discussion and present to PURA

10:30 AM – 12:00 PM	Discussion of DER Location

- Issues:

  - Moving development closer to load

  - Affordable land vs distance to load centers

- SMART program in MA used to incentivize certain locations

  - Administered by third-party

  - Adders for different types of land uses

  - No geographic restrictions – incentivized by land use, did not push for projects in specific area

- Need buy-in from DEEP and PURA

- General process to explore:

  - Explore issues/reasons for disconnect between development and load

  - Identify best practices to incentivize development

  - Discuss technical solutions

- Also a policy discussion – need to identify policy reasons for disconnect

12:00 PM – 1:00 PM	Discuss Docket 17-12-03re06 requirement that applicants provide proof of lease/ownership contemporaneously with interconnection application.

- New Matters/Open Discussion

- Issue of agreements between land owner and developer

  - There is risk involved in leasing/owning without option to install DER

- Form considered for use with interconnection application to provide proof of lease/ownership

- UI sister utilities in NY use agreement

  - Not required for under 50 kW

  - Site control required over 50 kW

- All in agreement to require site control agreement form

  - to be submitted along with interconnection application

  - Not required for residential applications

- Next Steps:

  - Create draft form, based on NY Standard Site Control Form (Zak to draft)

  - Circulate, collect feedback, update draft form

  - Submit to Authority