| Docket 187A- Milford Power Company, LLC Certificate of Environmental Compatibility and Public Need for the Milford Power Project located off of Oronoque Road in Milford, Connecticut. Reopening of this docket pursuant to Connecticut General Statutes § 4-181a(b) to Modify the Decision and Order in Docket 187 to Allow Milford Power Company, LLC to Suspend its Backup Fuel System Based on Changed Conditions the attachment of conditions to the certificate consistent with the findings and recommendations contained in the Final Report issued by the Kleen Energy Plant Investigation Review Panel and the recommendations of the Thomas Commission. | } } } } | Connecticut Siting Council December 2, 2010 |
| --- | --- | --- |

Decision and Order

In response to a request to modify its Decision and Order submitted on July 29, 2010 by the Certificate Holder, Milford Power Company, LLC, the Connecticut Siting Council (Council) hereby modifies its Docket No. 187 Decision and Order of January 8, 1999 and its Docket No. 187 Decision and Order of April 7, 2009.  Condition (1e) of the Decision and Order is hereby modified and the following additional conditions are included, as follows:

1. Decision and Order 1(e) in Docket No. 187 is modified to now read as follows:

e)	The project shall operate on natural gas.  A backup distillate fuel oil system may be recommissioned if warranted by future conditions.

Additional Conditions to the Docket 187A Decision and Order as follows:

- The use of natural gas as a fuel pipeline/system cleaning media for any future facility modification shall be prohibited.

- Submit the following information to the Council 15-days prior to any future fuel pipeline/system cleaning operations related to any future facility modification:

  - Identification of the cleaning media to be used;

  - Identification of any known hazards through use of the cleaning media;

  - Description of how known hazards will be mitigated, including identification of any applicable state or federal regulations concerning hazard mitigation measures for such media;

  - Identification and description of accepted industry practices or relevant regulations concerning the proper use of such media;

  - Provide detailed specifications (narratives/drawings) indicating the location and procedures to be used during the pipe cleaning process, including any necessary worker safety exclusion zones;

  - Identification of the contractor or personnel performing the work, including a description of past project experience and the level of training and qualifications necessary for performance of the work;

  - Contact information for a special inspector hired by the Certificate Holder who is a Connecticut Registered Engineer with specific knowledge and experience regarding electric generating facilities or a National Board of Boiler and Pressure Vessel Inspector and written approval of such special inspector by the local fire marshal and building inspector; and

  - Certification of notice regarding pipe cleaning operations to all state agencies listed in General Statutes § 16-50j(h) and to the Department of Consumer Protection, Department of Labor, Department of Public Safety, Department of Public Works, and the Department of Emergency Management and Homeland Security.

- Submit a copy of an Emergency Response/Safety Plan within 90 days of the date of this decision that identifies any revisions since the initial filing of the Development and Management Plan, if applicable, and that includes, but is not limited to the following:

  - A description of the results of any simulated emergency response activities with any state and/or local emergency response officials; and

  - Details of the current construction site access system that accounts for all personnel entering and leaving facility.

    - Compliance with the following codes and standards, as adopted and amended by the Department of Public Safety and/or the Authority Having Jurisdiction, for any future fuel pipeline/system cleaning operations  related to any future facility modification:

  - NFPA 37 (2010 edition);

  - NFPA 54 (2009 edition);

  - NFPA 54 Temporary Interim Amendment 09-3 (August 25, 2010);

  - NFPA 850 (2010 edition);

  - ASME B31 (2007); and

  - ASME B31.1 Appendices IV and V (2007).

- The Certificate Holder shall remit timely payments associated with annual assessments and invoices submitted by the Council for expenses attributable to the facility under Conn. Gen. Stat. §16-50v.

- The Certificate may be transferred in accordance with Conn. Gen. Stat. §16-50k(b), provided both the Certificate Holder/transferor and the transferee are current with payments to the Council for their respective annual assessments and invoices under Conn. Gen. Stat. §16-50v. In addition, both the Certificate Holder/transferor and the transferee shall provide the Council a written agreement as to the entity responsible for any quarterly assessment charges under Conn. Gen. Stat. §16-50v(b)(2) that may be associated with this facility.

- If the Certificate Holder is a wholly owned subsidiary of a corporation or other entity and is sold/transferred to another corporation or other entity, the Council shall be notified of such sale and/or transfer and of any change in contact information for the individual or representative responsible for management and operations of the Certificate Holder within 30 days of the sale and/or transfer.

We hereby direct that a copy of the Findings of Fact, Opinion, and Decision and Order be served on each person listed below, and notice of issuance published in Milford Orange Bulletin and The New Haven Register.

By this Decision and Order, the Council disposes of the legal rights, duties, and privileges of each party named or admitted to the proceeding in accordance with Section 16-50j-17 of the Regulations of Connecticut State Agencies.

The parties and intervenors to this proceeding are:

Applicant		Its Representatives

Milford Power Company, LLC	Michael Cartney

Vice President and Plant Manager

Milford Power Company, LLC

55 Shelland Street

Milford, CT  06460

Tom Favinger

CPV Milford, LLC

c/o Competitive Power Ventures, Inc.

8403 Colesville Road, Suite 915

Silver Spring, MD  20910

Timothy P. Kober

Pillsbury Winthrop Shaw Pittman LLP

1540 Broadway

New York, NY  10036

James A. Hanley, CCTS

Assistant Vice President

Wilmington Trust Company

Rodney Square North

1100 North Market Street

Wilmington, DE  19890-1605

Franca L. DeRosa, Esq.

Philip M. Small, Esq.

Brown Rudnick LLP

CityPlace I, 185 Asylum Street

Hartford, CT  06103

Intervenor	Its Representative

The Connecticut Light and Power Company	John R. Morissette, Manager

Transmission Siting and Permitting

The Connecticut Light & Power Company

P.O. Box 270

Hartford, CT 06141-0270

Duncan R. Mackay, Esq.

Vincent P. Pace, Esq.

The Connecticut Light & Power Company

P.O. Box 270

Hartford, CT 06141-0270

Intervenor	Its Representative

Southern Connecticut Gas Company	Anne McCrory, Esq.

Southern Connecticut Gas Company

855 Main Street

Bridgeport, CT  06604

Intervenor		Its Representative

Iroquois Gas Transmission System, L.P.	Paul W. Diehl

Iroquois Gas Transmission System, L.P.

One Corporate Drive

Shelton, CT  06484